## Item
STEP.1(UUT Test seq.1) : Read UUT Total Number ---- (0'000) --------------- PASS | ElapsedTime: 0h3m36s
STEP.2(UUT Test seq.2) : PA 66202 Set_Multi ---- (0'078) ------------------ PASS
STEP.3(UUT Test seq.3) : 34970_Set ---- (0'000) --------------------------- PASS
STEP.4(UUT Test seq.4) : SUB20-Relay ---- (0'500) ------------------------- PASS
STEP.5(UUT Test seq.5) : Read UUT Total Number ---- (0'016) --------------- PASS
STEP.6(UUT Test seq.6) : 61512 Ac Source ACDC Mode_Multi_S2 ---- (0'171) -- PASS
STEP.7(UUT Test seq.7) : TTL & Relay Setup ---- (0'453) ------------------- PASS
STEP.8(UUT Test seq.8) : Turn On Timing Test_Multi or Single(264V_63Hz_HH) PASS | 264V_63Hz_HH
STEP.9(UUT Test seq.9) : SUB20-Relay ---- (0'515) ------------------------- PASS
STEP.10(UUT Test seq.10) : Pre I2C Multi Set ---- (0'000) ----------------- PASS
STEP.11(UUT Test seq.11) : I2C Read Status Multi_S6(264V_63Hz_HH) ---- (0'1 PASS | 264V_63Hz_HH
STEP.12(UUT Test seq.12) : FW Version Check Multi_S7 ---- (0'359) --------- FAIL
STEP.13(UUT Test seq.13) : Hold Up Timing Test_Multi or Single(264V_63Hz_70 PASS | 264V_63Hz_70%
STEP.14(UUT Test seq.14) : FAN Full Speed delay time Multi ---- (10'093) -- PASS
STEP.15(UUT Test seq.15) : FAN Speed Normal_Multi ---- (0'093) ------------ PASS
STEP.16(UUT Test seq.16) : Pause Message(Add Cap Laod) ---- (23'291) ------ PASS | Add Cap Laod
STEP.17(UUT Test seq.17) : TTL & Relay Setup(Add Cap Laod) ---- (0'702) --- PASS | Add Cap Laod
STEP.18(UUT Test seq.18) : Turn On Timing Test_Multi or Single(90V_47Hz_LL) PASS | 90V_47Hz_LL
STEP.19(UUT Test seq.19) : PS OFF Time 80611(90V_47Hz_LL) ---- (2'496) ---- PASS | 90V_47Hz_LL
STEP.20(UUT Test seq.20) : PS ON Delay time 80611(90V_47Hz_LL) ---- (0'889) PASS | 90V_47Hz_LL
STEP.21(UUT Test seq.21) : Turn On Timing Test_Multi or Single(90V_47Hz_LL_ PASS | 90V_47Hz_LL_Tac_12V_12Vsb_Rise
STEP.22(UUT Test seq.22) : TTL & Relay Setup ---- (0'000) ----------------- PASS
STEP.23(UUT Test seq.23) : PS ON Delay time 80611(90V_47Hz_LL_Tpson_12V_Ris PASS | 90V_47Hz_LL_Tpson_12V_Rise
STEP.24(UUT Test seq.24) : Hold Up Timing Test_Multi or Single(90V_47Hz_LL) PASS | 90V_47Hz_LL
STEP.25(UUT Test seq.25) : FAN Full Speed delay time Multi ---- (8'081) --- PASS
STEP.26(UUT Test seq.26) : FAN Speed Normal_Multi ---- (0'109) ------------ PASS
STEP.27(UUT Test seq.27) : Turn On Timing Test_Multi or Single(90V_47Hz_HH) PASS | 90V_47Hz_HH
STEP.28(UUT Test seq.28) : PS OFF Time 80611(90V_47Hz_HH) ---- (2'465) ---- PASS | 90V_47Hz_HH
STEP.29(UUT Test seq.29) : PS ON Delay time 80611(90V_47Hz_HH) ---- (0'889) PASS | 90V_47Hz_HH
STEP.30(UUT Test seq.30) : Turn On Timing Test_Multi or Single(90V_47Hz_HH_ PASS | 90V_47Hz_HH_Tac_12V_12Vsb_Rise
STEP.31(UUT Test seq.31) : TTL & Relay Setup ---- (0'000) ----------------- PASS
STEP.32(UUT Test seq.32) : PS ON Delay time 80611(90V_47Hz_HH_Tpson_12V_Ris PASS | 90V_47Hz_HH_Tpson_12V_Rise
STEP.33(UUT Test seq.33) : Hold Up Timing Test_Multi or Single(90V_47Hz_70% PASS | 90V_47Hz_70%
STEP.34(UUT Test seq.34) : FAN Full Speed delay time Multi ---- (8'112) --- PASS
STEP.35(UUT Test seq.35) : FAN Speed Normal_Multi ---- (0'093) ------------ PASS
STEP.36(UUT Test seq.36) : Turn On Timing Test_Multi or Single(100V_60Hz_HH PASS | 100V_60Hz_HH
STEP.37(UUT Test seq.37) : PS OFF Time 80611(100V_60Hz_HH) ---- (2'496) --- PASS | 100V_60Hz_HH
STEP.38(UUT Test seq.38) : PS ON Delay time 80611(100V_60Hz_HH) ---- (0'843 PASS | 100V_60Hz_HH
STEP.39(UUT Test seq.39) : Turn On Timing Test_Multi or Single(100V_60Hz_HH PASS | 100V_60Hz_HH_Tac_12V_12Vsb_Rise
STEP.40(UUT Test seq.40) : TTL & Relay Setup ---- (0'000) ----------------- PASS
STEP.41(UUT Test seq.41) : PS ON Delay time 80611(100V_60Hz_HH_Tpson_12V_Ri PASS | 100V_60Hz_HH_Tpson_12V_Rise
STEP.42(UUT Test seq.42) : Hold Up Timing Test_Multi or Single(100V_60Hz_70 PASS | 100V_60Hz_70%
STEP.43(UUT Test seq.43) : FAN Full Speed delay time Multi ---- (8'096) --- PASS
STEP.44(UUT Test seq.44) : FAN Speed Normal_Multi ---- (0'094) ------------ PASS
STEP.45(UUT Test seq.45) : Turn On Timing Test_Multi or Single(180V_47Hz_HH PASS | 180V_47Hz_HH
STEP.46(UUT Test seq.46) : PS OFF Time 80611(180V_47Hz_HH) ---- (2'450) --- PASS | 180V_47Hz_HH
STEP.47(UUT Test seq.47) : PS ON Delay time 80611(180V_47Hz_HH) ---- (0'983 PASS | 180V_47Hz_HH
STEP.48(UUT Test seq.48) : Turn On Timing Test_Multi or Single(180V_47Hz_HH PASS | 180V_47Hz_HH_Tac_12V_12Vsb_Rise
STEP.49(UUT Test seq.49) : TTL & Relay Setup ---- (0'000) ----------------- PASS
STEP.50(UUT Test seq.50) : PS ON Delay time 80611(180V_47Hz_HH_Tpson_12V_Ri PASS | 180V_47Hz_HH_Tpson_12V_Rise
STEP.51(UUT Test seq.51) : Hold Up Timing Test_Multi or Single(180V_47Hz_70 PASS | 180V_47Hz_70%
STEP.52(UUT Test seq.52) : FAN Full Speed delay time Multi ---- (8'112) --- PASS
STEP.53(UUT Test seq.53) : FAN Speed Normal_Multi ---- (0'078) ------------ PASS
STEP.54(UUT Test seq.54) : Turn On Timing Test_Multi or Single(200V_50Hz_HH PASS | 200V_50Hz_HH
STEP.55(UUT Test seq.55) : PS OFF Time 80611(200V_50Hz_HH) ---- (2'464) --- PASS | 200V_50Hz_HH
STEP.56(UUT Test seq.56) : PS ON Delay time 80611(200V_50Hz_HH) ---- (0'873 PASS | 200V_50Hz_HH
STEP.57(UUT Test seq.57) : Turn On Timing Test_Multi or Single(200V_50Hz_HH PASS | 200V_50Hz_HH_Tac_12V_12Vsb_Rise
STEP.58(UUT Test seq.58) : TTL & Relay Setup ---- (0'000) ----------------- PASS
STEP.59(UUT Test seq.59) : PS ON Delay time 80611(200V_50Hz_HH_Tpson_12V_Ri PASS | 200V_50Hz_HH_Tpson_12V_Rise
STEP.60(UUT Test seq.60) : Hold Up Timing Test_Multi or Single(200V_50Hz_70 PASS | 200V_50Hz_70%
STEP.61(UUT Test seq.61) : FAN Full Speed delay time Multi ---- (8'097) --- PASS
STEP.62(UUT Test seq.62) : FAN Speed Normal_Multi ---- (0'078) ------------ PASS
STEP.63(UUT Test seq.63) : Turn On Timing Test_Multi or Single(220V_50Hz_HH PASS | 220V_50Hz_HH
STEP.64(UUT Test seq.64) : PS OFF Time 80611(220V_50Hz_HH) ---- (2'511) --- PASS | 220V_50Hz_HH
STEP.65(UUT Test seq.65) : PS ON Delay time 80611(220V_50Hz_HH) ---- (0'873 PASS | 220V_50Hz_HH
STEP.66(UUT Test seq.66) : Turn On Timing Test_Multi or Single(220V_50Hz_HH PASS | 220V_50Hz_HH_Tac_12V_12Vsb_Rise
STEP.67(UUT Test seq.67) : TTL & Relay Setup ---- (0'016) ----------------- PASS
STEP.68(UUT Test seq.68) : PS ON Delay time 80611(220V_50Hz_HH_Tpson_12V_Ri PASS | 220V_50Hz_HH_Tpson_12V_Rise
STEP.69(UUT Test seq.69) : Hold Up Timing Test_Multi or Single(220V_50Hz_70 PASS | 220V_50Hz_70%
STEP.70(UUT Test seq.70) : FAN Full Speed delay time Multi ---- (8'097) --- PASS
STEP.71(UUT Test seq.71) : FAN Speed Normal_Multi ---- (0'109) ------------ PASS
STEP.72(UUT Test seq.72) : Turn On Timing Test_Multi or Single(264V_63Hz_LL PASS | 264V_63Hz_LL
STEP.73(UUT Test seq.73) : PS OFF Time 80611(264V_63Hz_LL) ---- (2'511) --- PASS | 264V_63Hz_LL
STEP.74(UUT Test seq.74) : PS ON Delay time 80611(264V_63Hz_LL) ---- (0'873 PASS | 264V_63Hz_LL
STEP.75(UUT Test seq.75) : Turn On Timing Test_Multi or Single(264V_63Hz_LL PASS | 264V_63Hz_LL_Tac_12V_12Vsb_Rise
STEP.76(UUT Test seq.76) : TTL & Relay Setup ---- (0'000) ----------------- PASS
STEP.77(UUT Test seq.77) : PS ON Delay time 80611(264V_63Hz_LL_Tpson_12V_Ri PASS | 264V_63Hz_LL_Tpson_12V_Rise
STEP.78(UUT Test seq.78) : Hold Up Timing Test_Multi or Single(264V_63Hz_LL PASS | 264V_63Hz_LL
STEP.79(UUT Test seq.79) : FAN Full Speed delay time Multi ---- (8'097) --- PASS
STEP.80(UUT Test seq.80) : FAN Speed Normal_Multi ---- (0'093) ------------ PASS
STEP.81(UUT Test seq.81) : Turn On Timing Test_Multi or Single(264V_63Hz_HH PASS | 264V_63Hz_HH
STEP.82(UUT Test seq.82) : PS OFF Time 80611(264V_63Hz_HH) ---- (2'496) --- PASS | 264V_63Hz_HH
STEP.83(UUT Test seq.83) : PS ON Delay time 80611(264V_63Hz_HH) ---- (0'890 PASS | 264V_63Hz_HH
STEP.84(UUT Test seq.84) : Turn On Timing Test_Multi or Single(264V_63Hz_HH PASS | 264V_63Hz_HH_Tac_12V_12Vsb_Rise
STEP.85(UUT Test seq.85) : TTL & Relay Setup ---- (0'016) ----------------- PASS
STEP.86(UUT Test seq.86) : PS ON Delay time 80611(264V_63Hz_HH_Tpson_12V_Ri PASS | 264V_63Hz_HH_Tpson_12V_Rise
STEP.87(UUT Test seq.87) : Hold Up Timing Test_Multi or Single(264V_63Hz_70 PASS | 264V_63Hz_70%
STEP.88(UUT Test seq.88) : FAN Full Speed delay time Multi ---- (8'096) --- PASS
STEP.89(UUT Test seq.89) : FAN Speed Normal_Multi ---- (0'094) ------------ PASS
STEP.90(UUT Test seq.90) : 61512 Ac Source ACDC Mode_Multi_S2 ---- (0'172) PASS
STEP.91(UUT Test seq.91) : Turn On Timing Test_Multi or Single(164VDC_LL) - PASS | 164VDC_LL
STEP.92(UUT Test seq.92) : PS OFF Time 80611(164VDC_LL) ---- (2'434) ------ PASS | 164VDC_LL
STEP.93(UUT Test seq.93) : PS ON Delay time 80611(164VDC_LL) ---- (0'842) - PASS | 164VDC_LL
STEP.94(UUT Test seq.94) : Turn On Timing Test_Multi or Single(164VDC_LL_Ta PASS | 164VDC_LL_Tac_12V_12Vsb_Rise
STEP.95(UUT Test seq.95) : TTL & Relay Setup ---- (0'000) ----------------- PASS
STEP.96(UUT Test seq.96) : PS ON Delay time 80611(164VDC_LL_Tpson_12V_Rise) PASS | 164VDC_LL_Tpson_12V_Rise
STEP.97(UUT Test seq.97) : Hold Up Timing Test_Multi or Single(164VDC_LL) - PASS | 164VDC_LL
STEP.98(UUT Test seq.98) : FAN Full Speed delay time Multi ---- (8'097) --- PASS
STEP.99(UUT Test seq.99) : FAN Speed Normal_Multi ---- (0'093) ------------ PASS
STEP.100(UUT Test seq.100) : Turn On Timing Test_Multi or Single(164VDC_HH) PASS | 164VDC_HH
STEP.101(UUT Test seq.101) : PS OFF Time 80611(164VDC_HH) ---- (2'543) ---- PASS | 164VDC_HH
STEP.102(UUT Test seq.102) : PS ON Delay time 80611(164VDC_HH) ---- (0'952) PASS | 164VDC_HH
STEP.103(UUT Test seq.103) : Turn On Timing Test_Multi or Single(164VDC_HH_ PASS | 164VDC_HH_Tac_12V_12Vsb_Rise
STEP.104(UUT Test seq.104) : TTL & Relay Setup ---- (0'000) --------------- PASS
STEP.105(UUT Test seq.105) : PS ON Delay time 80611(164VDC_HH_Tpson_12V_Ris PASS | 164VDC_HH_Tpson_12V_Rise
STEP.106(UUT Test seq.106) : Hold Up Timing Test_Multi or Single(164VDC_70% PASS | 164VDC_70%
STEP.107(UUT Test seq.107) : FAN Full Speed delay time Multi ---- (8'096) - PASS
STEP.108(UUT Test seq.108) : FAN Speed Normal_Multi ---- (0'109) ---------- PASS
STEP.109(UUT Test seq.109) : Turn On Timing Test_Multi or Single(200VDC_HH) PASS | 200VDC_HH
STEP.110(UUT Test seq.110) : PS OFF Time 80611(200VDC_HH) ---- (2'481) ---- PASS | 200VDC_HH
STEP.111(UUT Test seq.111) : PS ON Delay time 80611(200VDC_HH) ---- (0'874) PASS | 200VDC_HH
STEP.112(UUT Test seq.112) : Turn On Timing Test_Multi or Single(200VDC_HH_ PASS | 200VDC_HH_Tac_12V_12Vsb_Rise
STEP.113(UUT Test seq.113) : TTL & Relay Setup ---- (0'000) --------------- PASS
STEP.114(UUT Test seq.114) : PS ON Delay time 80611(200VDC_HH_Tpson_12V_Ris PASS | 200VDC_HH_Tpson_12V_Rise
STEP.115(UUT Test seq.115) : Hold Up Timing Test_Multi or Single(200VDC_70% PASS | 200VDC_70%
STEP.116(UUT Test seq.116) : FAN Full Speed delay time Multi ---- (8'096) - PASS
STEP.117(UUT Test seq.117) : Turn On Timing Test_Multi or Single(220VDC_HH) PASS | 220VDC_HH
STEP.118(UUT Test seq.118) : PS OFF Time 80611(220VDC_HH) ---- (2'512) ---- PASS | 220VDC_HH
STEP.119(UUT Test seq.119) : PS ON Delay time 80611(220VDC_HH) ---- (0'858) PASS | 220VDC_HH
STEP.120(UUT Test seq.120) : Turn On Timing Test_Multi or Single(220VDC_HH_ PASS | 220VDC_HH_Tac_12V_12Vsb_Rise
STEP.121(UUT Test seq.121) : TTL & Relay Setup ---- (0'000) --------------- PASS
STEP.122(UUT Test seq.122) : PS ON Delay time 80611(220VDC_HH_Tpson_12V_Ris PASS | 220VDC_HH_Tpson_12V_Rise
STEP.123(UUT Test seq.123) : Hold Up Timing Test_Multi or Single(220VDC_70% PASS | 220VDC_70%
STEP.124(UUT Test seq.124) : FAN Full Speed delay time Multi ---- (8'112) - PASS
STEP.125(UUT Test seq.125) : FAN Speed Normal_Multi ---- (0'093) ---------- PASS
STEP.126(UUT Test seq.126) : Turn On Timing Test_Multi or Single(300VDC_LL) PASS | 300VDC_LL
STEP.127(UUT Test seq.127) : PS OFF Time 80611(300VDC_LL) ---- (2'528) ---- PASS | 300VDC_LL
STEP.128(UUT Test seq.128) : PS ON Delay time 80611(300VDC_LL) ---- (0'952) PASS | 300VDC_LL
STEP.129(UUT Test seq.129) : Turn On Timing Test_Multi or Single(300VDC_LL_ PASS | 300VDC_LL_Tac_12V_12Vsb_Rise
STEP.130(UUT Test seq.130) : TTL & Relay Setup ---- (0'000) --------------- PASS
STEP.131(UUT Test seq.131) : PS ON Delay time 80611(300VDC_LL_Tpson_12V_Ris PASS | 300VDC_LL_Tpson_12V_Rise
STEP.132(UUT Test seq.132) : Hold Up Timing Test_Multi or Single(300VDC_LL) PASS | 300VDC_LL
STEP.133(UUT Test seq.133) : FAN Full Speed delay time Multi ---- (8'097) - PASS
STEP.134(UUT Test seq.134) : FAN Speed Normal_Multi ---- (0'094) ---------- PASS
STEP.135(UUT Test seq.135) : Turn On Timing Test_Multi or Single(300VDC_HH) PASS | 300VDC_HH
STEP.136(UUT Test seq.136) : PS OFF Time 80611(300VDC_HH) ---- (2'464) ---- PASS | 300VDC_HH
STEP.137(UUT Test seq.137) : PS ON Delay time 80611(300VDC_HH) ---- (0'858) PASS | 300VDC_HH
STEP.138(UUT Test seq.138) : Turn On Timing Test_Multi or Single(300VDC_HH_ PASS | 300VDC_HH_Tac_12V_12Vsb_Rise
STEP.139(UUT Test seq.139) : TTL & Relay Setup ---- (0'000) --------------- PASS
STEP.140(UUT Test seq.140) : PS ON Delay time 80611(300VDC_HH_Tpson_12V_Ris PASS | 300VDC_HH_Tpson_12V_Rise
STEP.141(UUT Test seq.141) : Hold Up Timing Test_Multi or Single(300VDC_70% PASS | 300VDC_70%
STEP.142(UUT Test seq.142) : FAN Full Speed delay time Multi ---- (8'097) - PASS
STEP.143(UUT Test seq.143) : FAN Speed Normal_Multi ---- (0'078) ---------- PASS
STEP.144(UUT Test seq.144) : Pause Message(Remove Cap Laod) ---- (14'680) - PASS | Remove Cap Laod
STEP.145(UUT Test seq.145) : TTL & Relay Setup ---- (0'202) --------------- PASS
STEP.146(UUT Test seq.146) : 61512 Ac Source ACDC Mode_Multi_S2 ---- (0'156 PASS
STEP.147(UUT Test seq.147) : Turn On Timing Test_Multi or Single(90V_47Hz_L PASS | 90V_47Hz_LL
STEP.148(UUT Test seq.148) : I2C Read Status Multi_S6(90V_47Hz_LL) ---- (0' PASS | 90V_47Hz_LL
STEP.149(UUT Test seq.149) : PS OFF Time 80611 ---- (1'576) --------------- PASS
STEP.150(UUT Test seq.150) : Input Output Eff Noise Multi or Single(90V_47H PASS | 90V_47Hz_No Load
STEP.151(UUT Test seq.151) : I2C Read Status Multi_S6(StandBy) ---- (0'109) PASS | StandBy
STEP.152(UUT Test seq.152) : Input Output Eff Noise Multi or Single(90V_47H PASS | 90V_47Hz_LH_Standby_2.5A
STEP.153(UUT Test seq.153) : Static ACDC 34970_or_Load_Multi or Single(12Vs PASS | 12Vsb_2.75A
STEP.154(UUT Test seq.154) : Static ACDC 34970_or_Load_Multi or Single(12Vs PASS | 12Vsb_OCP
STEP.155(UUT Test seq.155) : Static ACDC 34970_or_Load_Multi or Single(12Vs PASS | 12Vsb_2.75A
STEP.156(UUT Test seq.156) : Input Output Eff Noise Multi or Single(90V_47H PASS | 90V_47Hz_LL_Standby_0.1A
STEP.157(UUT Test seq.157) : PS ON Delay time 80611(90V_47Hz_LL) ---- (0'96 PASS | 90V_47Hz_LL
STEP.158(UUT Test seq.158) : Turn On Timing Test_Multi or Single(90V_47Hz_L PASS | 90V_47Hz_LL_Tac_12V_12Vsb_Rise
STEP.159(UUT Test seq.159) : TTL & Relay Setup ---- (0'016) --------------- PASS
STEP.160(UUT Test seq.160) : PS ON Delay time 80611(90V_47Hz_LL_Tpson_12V_R PASS | 90V_47Hz_LL_Tpson_12V_Rise
STEP.161(UUT Test seq.161) : Input Output Eff Noise Multi or Single(90V_47H PASS | 90V_47Hz_No Load
STEP.162(UUT Test seq.162) : I2C Read Status Multi_S6(90V_47Hz_No Load) --- PASS | 90V_47Hz_No Load
STEP.163(UUT Test seq.163) : Static ACDC 34970_or_Load_Multi or Single(12Vs PASS | 12Vsb_2.75A
STEP.164(UUT Test seq.164) : Static ACDC 34970_or_Load_Multi or Single(12Vs PASS | 12Vsb_OCP
STEP.165(UUT Test seq.165) : Static ACDC 34970_or_Load_Multi or Single(12Vs PASS | 12Vsb_2.75A
STEP.166(UUT Test seq.166) : Input Output Eff Noise Multi or Single(90V_47H PASS | 90V_47Hz_LL
STEP.167(UUT Test seq.167) : Input Output Eff Noise Multi or Single(90V_47H PASS | 90V_47Hz_LH
STEP.168(UUT Test seq.168) : Cold Redundant Master Multi _S2 ---- (0'094) - PASS
STEP.169(UUT Test seq.169) : Static ACDC 34970_or_Load_Multi or Single(90V_ PASS | 90V_47Hz_LL_Cheak CR
STEP.170(UUT Test seq.170) : Disable Cold Redundant Master Multi_S2 ---- (0 PASS
STEP.171(UUT Test seq.171) : Static ACDC 34970_or_Load_Multi or Single(90V_ PASS | 90V_47Hz_LL_Clear CR
STEP.172(UUT Test seq.172) : Hold Up Timing Test_Multi or Single(90V_47Hz_L PASS | 90V_47Hz_LL
STEP.173(UUT Test seq.173) : FAN Full Speed delay time Multi ---- (8'097) - PASS
STEP.174(UUT Test seq.174) : FAN Speed Normal_Multi ---- (0'078) ---------- PASS
STEP.175(UUT Test seq.175) : Turn On Timing Test_Multi or Single(90V_47Hz_H PASS | 90V_47Hz_HH
STEP.176(UUT Test seq.176) : I2C Read Status Multi_S6(90V_47Hz_HH) ---- (0' PASS | 90V_47Hz_HH
STEP.177(UUT Test seq.177) : 12V OVP I2C Multi(90V_47Hz_I2C_OVP) ---- (0'06 PASS | 90V_47Hz_I2C_OVP
STEP.178(UUT Test seq.178) : Static ACDC 34970_or_Load_Multi or Single(90V_ PASS | 90V_47Hz_HH_I2C_OVP
STEP.179(UUT Test seq.179) : I2C Read Status OR Multi_S6(90V_47Hz_HH_I2C_OV PASS | 90V_47Hz_HH_I2C_OVP
STEP.180(UUT Test seq.180) : 12V OVP Disable I2C Multi ---- (0'062) ------- PASS
STEP.181(UUT Test seq.181) : TTL & Relay Setup ---- (0'640) --------------- PASS
STEP.182(UUT Test seq.182) : PS OFF Time 80611(90V_47Hz_HH) ---- (1'591) -- PASS | 90V_47Hz_HH
STEP.183(UUT Test seq.183) : PS ON Delay time 80611(90V_47Hz_HH) ---- (0'96 PASS | 90V_47Hz_HH
STEP.184(UUT Test seq.184) : Turn On Timing Test_Multi or Single(90V_47Hz_H PASS | 90V_47Hz_HH_Tac_12V_12Vsb_Rise
STEP.185(UUT Test seq.185) : TTL & Relay Setup ---- (0'000) --------------- PASS
STEP.186(UUT Test seq.186) : PS ON Delay time 80611(90V_47Hz_HH_Tpson_12V_R PASS | 90V_47Hz_HH_Tpson_12V_Rise
STEP.187(UUT Test seq.187) : Input Output Eff Noise Multi or Single(90V_47H PASS | 90V_47Hz_HL
STEP.188(UUT Test seq.188) : Cold Redundant Master Multi _S2 ---- (0'109) - PASS
STEP.189(UUT Test seq.189) : Static ACDC 34970_or_Load_Multi or Single(90V_ PASS | 90V_47Hz_HH_Cheak CR
STEP.190(UUT Test seq.190) : Disable Cold Redundant Master Multi_S2 ---- (0 PASS
STEP.191(UUT Test seq.191) : Static ACDC 34970_or_Load_Multi or Single(90V_ PASS | 90V_47Hz_HH_Clear CR
STEP.192(UUT Test seq.192) : Input Output Eff Noise Multi or Single(90V_47H PASS | 90V_47Hz_HH
STEP.193(UUT Test seq.193) : Select OCP Mode(OCP Mode) ---- (0'000) ------- PASS | OCP Mode
STEP.194(UUT Test seq.194) : Over Load Protection 34970 or Load_Multi or Si PASS | 90V-OCP2
STEP.195(UUT Test seq.195) : I2C Read Status OR Multi_S6(90V-OCP2) ---- (0' PASS | 90V-OCP2
STEP.196(UUT Test seq.196) : Static ACDC 34970_or_Load_Multi or Single(90V- PASS | 90V-OCP2 Recover Set
STEP.197(UUT Test seq.197) : TTL & Relay Setup(PS OnOff) ---- (1'045) ----- PASS | PS OnOff
STEP.198(UUT Test seq.198) : Static ACDC 34970_or_Load_Multi or Single(90V- PASS | 90V-OCP2_Recover Check
STEP.199(UUT Test seq.199) : I2C Read Status Multi_S6(90V-OCP2_Recover Chec PASS | 90V-OCP2_Recover Check
STEP.200(UUT Test seq.200) : Hold Up Timing Test_Multi or Single(90V_47Hz_7 PASS | 90V_47Hz_70%
STEP.201(UUT Test seq.201) : FAN Full Speed delay time Multi ---- (8'096) - PASS
STEP.202(UUT Test seq.202) : FAN Speed Normal_Multi ---- (0'094) ---------- PASS
STEP.203(UUT Test seq.203) : Turn On Timing Test_Multi or Single(100V_60Hz_ PASS | 100V_60Hz_HH
STEP.204(UUT Test seq.204) : I2C Read Status Multi_S6(100V_60Hz_HH) ---- (0 PASS | 100V_60Hz_HH
STEP.205(UUT Test seq.205) : PS OFF Time 80611(100V_60Hz_HH) ---- (1'638) - PASS | 100V_60Hz_HH
STEP.206(UUT Test seq.206) : PS ON Delay time 80611(100V_60Hz_HH) ---- (0'9 PASS | 100V_60Hz_HH
STEP.207(UUT Test seq.207) : Turn On Timing Test_Multi or Single(100V_60Hz_ PASS | 100V_60Hz_HH_Tac_12V_12Vsb_Rise
STEP.208(UUT Test seq.208) : TTL & Relay Setup ---- (0'016) --------------- PASS
STEP.209(UUT Test seq.209) : PS ON Delay time 80611(100V_60Hz_HH_Tpson_12V_ PASS | 100V_60Hz_HH_Tpson_12V_Rise
STEP.210(UUT Test seq.210) : Input Output Eff Noise Multi or Single(100V_60 PASS | 100V_60Hz_HL
STEP.211(UUT Test seq.211) : Static ACDC 34970_or_Load_Multi or Single(100V PASS | 100V_60Hz_H_12Vsb_2.75A
STEP.212(UUT Test seq.212) : Static ACDC 34970_or_Load_Multi or Single(100V PASS | 100V_60Hz_H_12Vsb_OCP
STEP.213(UUT Test seq.213) : Static ACDC 34970_or_Load_Multi or Single(100V PASS | 100V_60Hz_H_12Vsb_2.75A
STEP.214(UUT Test seq.214) : Cold Redundant Master Multi _S2 ---- (0'094) - PASS
STEP.215(UUT Test seq.215) : Static ACDC 34970_or_Load_Multi or Single(100V PASS | 100V_60Hz_HH_Cheak CR
STEP.216(UUT Test seq.216) : Disable Cold Redundant Master Multi_S2 ---- (0 PASS
STEP.217(UUT Test seq.217) : Static ACDC 34970_or_Load_Multi or Single(100V PASS | 100V_60Hz_HH_Clear CR
STEP.218(UUT Test seq.218) : Input Output Eff Noise Multi or Single(HH) --- PASS | HH
STEP.219(UUT Test seq.219) : Static ACDC 34970_or_Load_Multi or Single(110V PASS | 110V-OCW
STEP.220(UUT Test seq.220) : TTL & Relay Setup(PS OnOff) ---- (1'030) ----- PASS | PS OnOff
STEP.221(UUT Test seq.221) : Peak_Load_S3_Multi_S(110V-OCP1_HL_Delay time 5 PASS | 110V-OCP1_HL_Delay time 50ms
STEP.222(UUT Test seq.222) : Peak_Load_S3_Multi_S(110V-OCP1_HH_Delay time 5 PASS | 110V-OCP1_HH_Delay time 50ms
STEP.223(UUT Test seq.223) : Peak_Load_S3_Multi_S(110V-OCP2_HL_Delay time 0 PASS | 110V-OCP2_HL_Delay time 0.1ms
STEP.224(UUT Test seq.224) : Peak_Load_S3_Multi_S(110V-OCP2_HH_Delay time 0 PASS | 110V-OCP2_HH_Delay time 0.1ms
STEP.225(UUT Test seq.225) : Set Input Condition Multi_S4_4(110V_60Hz) ---- PASS | 110V_60Hz
STEP.226(UUT Test seq.226) : Set Dynamic_Time ---- (0'000) ---------------- PASS
STEP.227(UUT Test seq.227) : SetAllLoad_SlewRate_S ---- (0'093) ----------- PASS
STEP.228(UUT Test seq.228) : Sync_Dynamic_80611_20200716_Multi_S(110V-OCP_1 PASS | 110V-OCP_12Vsb_LH_Delay time 50ms
STEP.229(UUT Test seq.229) : Sync_Dynamic_80611_20200716_Multi_S(110V-OCP_1 PASS | 110V-OCP_12Vsb_HH_Delay time 50ms
STEP.230(UUT Test seq.230) : Hold Up Timing Test_Multi or Single(100V_60Hz_ PASS | 100V_60Hz_70%
STEP.231(UUT Test seq.231) : FAN Full Speed delay time Multi ---- (8'096) - PASS
STEP.232(UUT Test seq.232) : FAN Speed Normal_Multi ---- (0'093) ---------- PASS
STEP.233(UUT Test seq.233) : Turn On Timing Test_Multi or Single(180V_47Hz_ PASS | 180V_47Hz_HH
STEP.234(UUT Test seq.234) : I2C Read Status Multi_S6(180V_47Hz_HH) ---- (0 PASS | 180V_47Hz_HH
STEP.235(UUT Test seq.235) : PS OFF Time 80611(180V_47Hz_HH) ---- (1'544) - PASS | 180V_47Hz_HH
STEP.236(UUT Test seq.236) : PS ON Delay time 80611(180V_47Hz_HH) ---- (0'8 PASS | 180V_47Hz_HH
STEP.237(UUT Test seq.237) : Turn On Timing Test_Multi or Single(180V_47Hz_ PASS | 180V_47Hz_HH_Tac_12V_12Vsb_Rise
STEP.238(UUT Test seq.238) : TTL & Relay Setup ---- (0'000) --------------- PASS
STEP.239(UUT Test seq.239) : PS ON Delay time 80611(180V_47Hz_HH_Tpson_12V_ PASS | 180V_47Hz_HH_Tpson_12V_Rise
STEP.240(UUT Test seq.240) : Input Output Eff Noise Multi or Single(180V_47 PASS | 180V_47Hz_HL
STEP.241(UUT Test seq.241) : Static ACDC 34970_or_Load_Multi or Single(180V PASS | 180V_47Hz_H_12Vsb_2.75A
STEP.242(UUT Test seq.242) : Static ACDC 34970_or_Load_Multi or Single(180V PASS | 180V_47Hz_H_12Vsb_OCP
STEP.243(UUT Test seq.243) : Static ACDC 34970_or_Load_Multi or Single(180V PASS | 180V_47Hz_H_12Vsb_2.75A
STEP.244(UUT Test seq.244) : Cold Redundant Master Multi _S2 ---- (0'094) - PASS
STEP.245(UUT Test seq.245) : Static ACDC 34970_or_Load_Multi or Single(180V PASS | 180V_47Hz_HH_Cheak CR
STEP.246(UUT Test seq.246) : Disable Cold Redundant Master Multi_S2 ---- (0 PASS
STEP.247(UUT Test seq.247) : Static ACDC 34970_or_Load_Multi or Single(180V PASS | 180V_47Hz_HH_Clear CR
STEP.248(UUT Test seq.248) : Input Output Eff Noise Multi or Single(180V_47 PASS | 180V_47Hz_HH
STEP.249(UUT Test seq.249) : Static ACDC 34970_or_Load_Multi or Single(180V PASS | 180V-OCW
STEP.250(UUT Test seq.250) : TTL & Relay Setup(PS OnOff) ---- (1'014) ----- PASS | PS OnOff
STEP.251(UUT Test seq.251) : Peak_Load_S3_Multi_S(180V-OCP1_HL_Delay time 5 PASS | 180V-OCP1_HL_Delay time 50ms
STEP.252(UUT Test seq.252) : Peak_Load_S3_Multi_S(180V-OCP1_HH_Delay time 5 PASS | 180V-OCP1_HH_Delay time 50ms
STEP.253(UUT Test seq.253) : Peak_Load_S3_Multi_S(180V-OCP2_HL_Delay time 0 PASS | 180V-OCP2_HL_Delay time 0.1ms
STEP.254(UUT Test seq.254) : Peak_Load_S3_Multi_S(180V-OCP2_HH_Delay time 0 PASS | 180V-OCP2_HH_Delay time 0.1ms
STEP.255(UUT Test seq.255) : Set Input Condition Multi_S4_4(180V_47Hz) ---- PASS | 180V_47Hz
STEP.256(UUT Test seq.256) : Set Dynamic_Time ---- (0'000) ---------------- PASS
STEP.257(UUT Test seq.257) : SetAllLoad_SlewRate_S ---- (0'140) ----------- PASS
STEP.258(UUT Test seq.258) : Sync_Dynamic_80611_20200716_Multi_S(180V-OCP_1 PASS | 180V-OCP_12Vsb_LH_Delay time 50ms
STEP.259(UUT Test seq.259) : Sync_Dynamic_80611_20200716_Multi_S(180V-OCP_1 PASS | 180V-OCP_12Vsb_HH_Delay time 50ms
STEP.260(UUT Test seq.260) : Hold Up Timing Test_Multi or Single(180V_47Hz_ PASS | 180V_47Hz_70%
STEP.261(UUT Test seq.261) : FAN Full Speed delay time Multi ---- (8'096) - PASS
STEP.262(UUT Test seq.262) : FAN Speed Normal_Multi ---- (0'094) ---------- PASS
STEP.263(UUT Test seq.263) : Turn On Timing Test_Multi or Single(200V_50Hz_ PASS | 200V_50Hz_HH
STEP.264(UUT Test seq.264) : I2C Read Status Multi_S6(200V_50Hz_HH) ---- (0 PASS | 200V_50Hz_HH
STEP.265(UUT Test seq.265) : PS OFF Time 80611(200V_50Hz_HH) ---- (1'560) - PASS | 200V_50Hz_HH
STEP.266(UUT Test seq.266) : PS ON Delay time 80611(200V_50Hz_HH) ---- (0'8 PASS | 200V_50Hz_HH
STEP.267(UUT Test seq.267) : Turn On Timing Test_Multi or Single(200V_50Hz_ PASS | 200V_50Hz_HH_Tac_12V_12Vsb_Rise
STEP.268(UUT Test seq.268) : TTL & Relay Setup ---- (0'000) --------------- PASS
STEP.269(UUT Test seq.269) : PS ON Delay time 80611(200V_50Hz_HH_Tpson_12V_ PASS | 200V_50Hz_HH_Tpson_12V_Rise
STEP.270(UUT Test seq.270) : Input Output Eff Noise Multi or Single(200V_50 PASS | 200V_50Hz_HL
STEP.271(UUT Test seq.271) : Static ACDC 34970_or_Load_Multi or Single(200V PASS | 200V_50Hz_H_12Vsb_2.75A
STEP.272(UUT Test seq.272) : Static ACDC 34970_or_Load_Multi or Single(200V PASS | 200V_50Hz_H_12Vsb_OCP
STEP.273(UUT Test seq.273) : Static ACDC 34970_or_Load_Multi or Single(200V PASS | 200V_50Hz_H_12Vsb_2.75A
STEP.274(UUT Test seq.274) : Cold Redundant Master Multi _S2 ---- (0'093) - PASS
STEP.275(UUT Test seq.275) : Static ACDC 34970_or_Load_Multi or Single(200V PASS | 200V_50Hz_HH_Cheak CR
STEP.276(UUT Test seq.276) : Disable Cold Redundant Master Multi_S2 ---- (0 PASS
STEP.277(UUT Test seq.277) : Static ACDC 34970_or_Load_Multi or Single(200V PASS | 200V_50Hz_HH_Clear CR
STEP.278(UUT Test seq.278) : Input Output Eff Noise Multi or Single(200V_50 PASS | 200V_50Hz_HH
STEP.279(UUT Test seq.279) : Static ACDC 34970_or_Load_Multi or Single(200V PASS | 200V-OCW
STEP.280(UUT Test seq.280) : TTL & Relay Setup(PS OnOff) ---- (1'029) ----- PASS | PS OnOff
STEP.281(UUT Test seq.281) : Peak_Load_S3_Multi_S(200V-OCP1_HL_Delay time 5 PASS | 200V-OCP1_HL_Delay time 50ms
STEP.282(UUT Test seq.282) : Peak_Load_S3_Multi_S(200V-OCP1_HH_Delay time 5 PASS | 200V-OCP1_HH_Delay time 50ms
STEP.283(UUT Test seq.283) : Peak_Load_S3_Multi_S(200V-OCP2_HL_Delay time 0 PASS | 200V-OCP2_HL_Delay time 0.1ms
STEP.284(UUT Test seq.284) : Peak_Load_S3_Multi_S(200V-OCP2_HH_Delay time 0 PASS | 200V-OCP2_HH_Delay time 0.1ms
STEP.285(UUT Test seq.285) : Set Input Condition Multi_S4_4(200V_50Hz) ---- PASS | 200V_50Hz
STEP.286(UUT Test seq.286) : Set Dynamic_Time ---- (0'016) ---------------- PASS
STEP.287(UUT Test seq.287) : SetAllLoad_SlewRate_S ---- (0'109) ----------- PASS
STEP.288(UUT Test seq.288) : Sync_Dynamic_80611_20200716_Multi_S(200V-OCP_1 PASS | 200V-OCP_12Vsb_LH_Delay time 50ms
STEP.289(UUT Test seq.289) : Sync_Dynamic_80611_20200716_Multi_S(200V-OCP_1 PASS | 200V-OCP_12Vsb_HH_Delay time 50ms
STEP.290(UUT Test seq.290) : Hold Up Timing Test_Multi or Single(200V_50Hz_ PASS | 200V_50Hz_70%
STEP.291(UUT Test seq.291) : FAN Full Speed delay time Multi ---- (8'097) - PASS
STEP.292(UUT Test seq.292) : FAN Speed Normal_Multi ---- (0'094) ---------- PASS
STEP.293(UUT Test seq.293) : Turn On Timing Test_Multi or Single(220V_50Hz_ PASS | 220V_50Hz_HH
STEP.294(UUT Test seq.294) : I2C Read Status Multi_S6(220V_50Hz_HH) ---- (0 PASS | 220V_50Hz_HH
STEP.295(UUT Test seq.295) : PS OFF Time 80611(220V_50Hz_HH) ---- (1'545) - PASS | 220V_50Hz_HH
STEP.296(UUT Test seq.296) : I2C Read Status Multi_S6(StandBy) ---- (0'125) PASS | StandBy
STEP.297(UUT Test seq.297) : PS ON Delay time 80611(220V_50Hz_HH) ---- (0'9 PASS | 220V_50Hz_HH
STEP.298(UUT Test seq.298) : Turn On Timing Test_Multi or Single(220V_50Hz_ PASS | 220V_50Hz_HH_Tac_12V_12Vsb_Rise
STEP.299(UUT Test seq.299) : TTL & Relay Setup ---- (0'000) --------------- PASS
STEP.300(UUT Test seq.300) : PS ON Delay time 80611(220V_50Hz_HH_Tpson_12V_ PASS | 220V_50Hz_HH_Tpson_12V_Rise
STEP.301(UUT Test seq.301) : Input Output Eff Noise Multi or Single(220V_50 PASS | 220V_50Hz_HL
STEP.302(UUT Test seq.302) : Static ACDC 34970_or_Load_Multi or Single(220V PASS | 220V_50Hz_H_12Vsb_2.75A
STEP.303(UUT Test seq.303) : Static ACDC 34970_or_Load_Multi or Single(220V PASS | 220V_50Hz_H_12Vsb_OCP
STEP.304(UUT Test seq.304) : Static ACDC 34970_or_Load_Multi or Single(220V PASS | 220V_50Hz_H_12Vsb_2.75A
STEP.305(UUT Test seq.305) : Cold Redundant Master Multi _S2 ---- (0'094) - PASS
STEP.306(UUT Test seq.306) : Static ACDC 34970_or_Load_Multi or Single(220V PASS | 220V_50Hz_HH_Cheak CR
STEP.307(UUT Test seq.307) : Disable Cold Redundant Master Multi_S2 ---- (0 PASS
STEP.308(UUT Test seq.308) : Static ACDC 34970_or_Load_Multi or Single(220V PASS | 220V_50Hz_HH_Clear CR
STEP.309(UUT Test seq.309) : Input Output Eff Noise Multi or Single(220V_50 PASS | 220V_50Hz_HH
STEP.310(UUT Test seq.310) : Static ACDC 34970_or_Load_Multi or Single(220V PASS | 220V-OCW
STEP.311(UUT Test seq.311) : TTL & Relay Setup(PS OnOff) ---- (1'029) ----- PASS | PS OnOff
STEP.312(UUT Test seq.312) : Peak_Load_S3_Multi_S(220V-OCP1_HL_Delay time 5 PASS | 220V-OCP1_HL_Delay time 50ms
STEP.313(UUT Test seq.313) : Peak_Load_S3_Multi_S(220V-OCP1_HH_Delay time 5 PASS | 220V-OCP1_HH_Delay time 50ms
STEP.314(UUT Test seq.314) : Peak_Load_S3_Multi_S(220V-OCP2_HL_Delay time 0 PASS | 220V-OCP2_HL_Delay time 0.1ms
STEP.315(UUT Test seq.315) : Peak_Load_S3_Multi_S(220V-OCP2_HH_Delay time 0 PASS | 220V-OCP2_HH_Delay time 0.1ms
STEP.316(UUT Test seq.316) : Set Input Condition Multi_S4_4(220V_50Hz) ---- PASS | 220V_50Hz
STEP.317(UUT Test seq.317) : Set Dynamic_Time ---- (0'000) ---------------- PASS
STEP.318(UUT Test seq.318) : SetAllLoad_SlewRate_S ---- (0'094) ----------- PASS
STEP.319(UUT Test seq.319) : Sync_Dynamic_80611_20200716_Multi_S(220V-OCP_1 PASS | 220V-OCP_12Vsb_LH_Delay time 50ms
STEP.320(UUT Test seq.320) : Sync_Dynamic_80611_20200716_Multi_S(220V-OCP_1 PASS | 220V-OCP_12Vsb_HH_Delay time 50ms
STEP.321(UUT Test seq.321) : Sync_Dynamic_80611_20200716_Multi_S(220V-Fast PASS | 220V-Fast OCW_SMBAlert
STEP.322(UUT Test seq.322) : PS ON Delay time 80611(220V-Fast OCW_SMBAlert) PASS | 220V-Fast OCW_SMBAlert
STEP.323(UUT Test seq.323) : Sync_Dynamic_80611_20200716_Multi_S(220V-Fast PASS | 220V-Fast OCW
STEP.324(UUT Test seq.324) : Hold Up Timing Test_Multi or Single(220V_50Hz_ PASS | 220V_50Hz_70%
STEP.325(UUT Test seq.325) : FAN Full Speed delay time Multi ---- (8'096) - PASS
STEP.326(UUT Test seq.326) : FAN Speed Normal_Multi ---- (0'109) ---------- PASS
STEP.327(UUT Test seq.327) : Turn On Timing Test_Multi or Single(264V_63Hz_ PASS | 264V_63Hz_LL
STEP.328(UUT Test seq.328) : PS OFF Time 80611(264V_63Hz_LL) ---- (1'591) - PASS | 264V_63Hz_LL
STEP.329(UUT Test seq.329) : I2C Read Status Multi_S6(StandBy) ---- (0'140) PASS | StandBy
STEP.330(UUT Test seq.330) : Input Output Eff Noise Multi or Single(264V_63 PASS | 264V_63Hz_No Load
STEP.331(UUT Test seq.331) : Input Output Eff Noise Multi or Single(264V_63 PASS | 264V_63Hz_Standby_2.5A
STEP.332(UUT Test seq.332) : Static ACDC 34970_or_Load_Multi or Single(12Vs PASS | 12Vsb_2.75A
STEP.333(UUT Test seq.333) : Static ACDC 34970_or_Load_Multi or Single(12Vs PASS | 12Vsb_OCP
STEP.334(UUT Test seq.334) : Static ACDC 34970_or_Load_Multi or Single(12Vs PASS | 12Vsb_2.75A
STEP.335(UUT Test seq.335) : Input Output Eff Noise Multi or Single(264V_63 PASS | 264V_63Hz_LL_Standby_0.1A
STEP.336(UUT Test seq.336) : PS ON Delay time 80611 ---- (0'874) ---------- PASS
STEP.337(UUT Test seq.337) : Turn On Timing Test_Multi or Single(264V_63Hz_ PASS | 264V_63Hz_LL_Tac_12V_12Vsb_Rise
STEP.338(UUT Test seq.338) : TTL & Relay Setup ---- (0'000) --------------- PASS
STEP.339(UUT Test seq.339) : PS ON Delay time 80611(264V_63Hz_LL_Tpson_12V_ PASS | 264V_63Hz_LL_Tpson_12V_Rise
STEP.340(UUT Test seq.340) : Input Output Eff Noise Multi or Single(No Load PASS | No Load
STEP.341(UUT Test seq.341) : Static ACDC 34970_or_Load_Multi or Single(12Vs PASS | 12Vsb_2.75A
STEP.342(UUT Test seq.342) : Static ACDC 34970_or_Load_Multi or Single(12Vs PASS | 12Vsb_OCP
STEP.343(UUT Test seq.343) : Static ACDC 34970_or_Load_Multi or Single(12Vs PASS | 12Vsb_2.75A
STEP.344(UUT Test seq.344) : Input Output Eff Noise Multi or Single(264V_63 PASS | 264V_63Hz_LL
STEP.345(UUT Test seq.345) : Input Output Eff Noise Multi or Single(264V_63 PASS | 264V_63Hz_LH
STEP.346(UUT Test seq.346) : Cold Redundant Master Multi _S2 ---- (0'094) - PASS
STEP.347(UUT Test seq.347) : Static ACDC 34970_or_Load_Multi or Single(264V PASS | 264V_63Hz_LL_Cheak CR
STEP.348(UUT Test seq.348) : Disable Cold Redundant Master Multi_S2 ---- (0 PASS
STEP.349(UUT Test seq.349) : Static ACDC 34970_or_Load_Multi or Single(264V PASS | 264V_63Hz_LL_Clear CR
STEP.350(UUT Test seq.350) : 12V OVP I2C Multi(12V_OVP_I2C) ---- (0'046) -- PASS | 12V_OVP_I2C
STEP.351(UUT Test seq.351) : Static ACDC 34970_or_Load_Multi or Single(264V PASS | 264V_63Hz_LL
STEP.352(UUT Test seq.352) : I2C Read Status OR Multi_S6(12V_OV) ---- (0'10 PASS | 12V_OV
STEP.353(UUT Test seq.353) : 12V OVP Disable I2C Multi ---- (0'062) ------- PASS
STEP.354(UUT Test seq.354) : TTL & Relay Setup ---- (0'624) --------------- PASS
STEP.355(UUT Test seq.355) : Hold Up Timing Test_Multi or Single(264V_63Hz_ PASS | 264V_63Hz_LL
STEP.356(UUT Test seq.356) : FAN Full Speed delay time Multi ---- (8'097) - PASS
STEP.357(UUT Test seq.357) : FAN Speed Normal_Multi ---- (0'110) ---------- PASS
STEP.358(UUT Test seq.358) : Turn On Timing Test_Multi or Single(264V_63Hz_ PASS | 264V_63Hz_HH
STEP.359(UUT Test seq.359) : I2C Read Status Multi_S6(264V_63Hz_HH) ---- (0 PASS | 264V_63Hz_HH
STEP.360(UUT Test seq.360) : PS OFF Time 80611(264V_63Hz_HH) ---- (1'591) - PASS | 264V_63Hz_HH
STEP.361(UUT Test seq.361) : I2C Read Status Multi_S6(StandBy) ---- (0'140) PASS | StandBy
STEP.362(UUT Test seq.362) : PS ON Delay time 80611(264V_63Hz_HH) ---- (0'8 PASS | 264V_63Hz_HH
STEP.363(UUT Test seq.363) : Turn On Timing Test_Multi or Single(264V_63Hz_ PASS | 264V_63Hz_HH_Tac_12V_12Vsb_Rise
STEP.364(UUT Test seq.364) : TTL & Relay Setup ---- (0'000) --------------- PASS
STEP.365(UUT Test seq.365) : PS ON Delay time 80611(264V_63Hz_HH_Tpson_12V_ PASS | 264V_63Hz_HH_Tpson_12V_Rise
STEP.366(UUT Test seq.366) : Input Output Eff Noise Multi or Single(264V_63 PASS | 264V_63Hz_HL
STEP.367(UUT Test seq.367) : Static ACDC 34970_or_Load_Multi or Single(264V PASS | 264V_63Hz_H_12Vsb_2.75A
STEP.368(UUT Test seq.368) : Static ACDC 34970_or_Load_Multi or Single(264V PASS | 264V_63Hz_H_12Vsb_OCP
STEP.369(UUT Test seq.369) : Static ACDC 34970_or_Load_Multi or Single(264V PASS | 264V_63Hz_H_12Vsb_2.75A
STEP.370(UUT Test seq.370) : Cold Redundant Master Multi _S2 ---- (0'093) - PASS
STEP.371(UUT Test seq.371) : Static ACDC 34970_or_Load_Multi or Single(264V PASS | 264V_63Hz_HH_Cheak CR
STEP.372(UUT Test seq.372) : Disable Cold Redundant Master Multi_S2 ---- (0 PASS
STEP.373(UUT Test seq.373) : Static ACDC 34970_or_Load_Multi or Single(264V PASS | 264V_63Hz_HH_Clear CR
STEP.374(UUT Test seq.374) : Input Output Eff Noise Multi or Single(HH) --- PASS | HH
STEP.375(UUT Test seq.375) : Static ACDC 34970_or_Load_Multi or Single(264V PASS | 264V-OCW
STEP.376(UUT Test seq.376) : TTL & Relay Setup(PS OnOff) ---- (1'014) ----- PASS | PS OnOff
STEP.377(UUT Test seq.377) : Peak_Load_S3_Multi_S(264V-OCP1_HL_Delay time 5 PASS | 264V-OCP1_HL_Delay time 50ms
STEP.378(UUT Test seq.378) : Peak_Load_S3_Multi_S(264V-OCP1_HH_Delay time 5 PASS | 264V-OCP1_HH_Delay time 50ms
STEP.379(UUT Test seq.379) : Peak_Load_S3_Multi_S(264V-OCP2_HL_Delay time 0 PASS | 264V-OCP2_HL_Delay time 0.1ms
STEP.380(UUT Test seq.380) : Peak_Load_S3_Multi_S(264V-OCP2_HH_Delay time 0 PASS | 264V-OCP2_HH_Delay time 0.1ms
STEP.381(UUT Test seq.381) : Set Input Condition Multi_S4_4(264V_63Hz) ---- PASS | 264V_63Hz
STEP.382(UUT Test seq.382) : Set Dynamic_Time ---- (0'016) ---------------- PASS
STEP.383(UUT Test seq.383) : SetAllLoad_SlewRate_S ---- (0'109) ----------- PASS
STEP.384(UUT Test seq.384) : Sync_Dynamic_80611_20200716_Multi_S(264V-OCP_1 PASS | 264V-OCP_12Vsb_LH_Delay time 50ms
STEP.385(UUT Test seq.385) : Sync_Dynamic_80611_20200716_Multi_S(264V-OCP_1 PASS | 264V-OCP_12Vsb_HH_Delay time 50ms
STEP.386(UUT Test seq.386) : Sync_Dynamic_80611_20200716_Multi_S(264V-Fast PASS | 264V-Fast OCW_SMBAlert
STEP.387(UUT Test seq.387) : PS ON Delay time 80611(264V-Fast OCW_SMBAlert) PASS | 264V-Fast OCW_SMBAlert
STEP.388(UUT Test seq.388) : Sync_Dynamic_80611_20200716_Multi_S(264V-Fast PASS | 264V-Fast OCW
STEP.389(UUT Test seq.389) : Hold Up Timing Test_Multi or Single(264V_63Hz_ PASS | 264V_63Hz_70%
STEP.390(UUT Test seq.390) : FAN Full Speed delay time Multi ---- (8'096) - PASS
STEP.391(UUT Test seq.391) : FAN Speed Normal_Multi ---- (0'078) ---------- PASS
STEP.392(UUT Test seq.392) : 61512 Ac Source ACDC Mode_Multi_S2(VDC) ---- ( PASS | VDC
STEP.393(UUT Test seq.393) : Turn On Timing Test_Multi or Single(164VDC_LL) PASS | 164VDC_LL
STEP.394(UUT Test seq.394) : I2C Read Status Multi_S6(164VDC_LL) ---- (0'12 PASS | 164VDC_LL
STEP.395(UUT Test seq.395) : PS OFF Time 80611(164VDC_LL) ---- (1'591) ---- PASS | 164VDC_LL
STEP.396(UUT Test seq.396) : I2C Read Status Multi_S6(StandBy) ---- (0'125) PASS | StandBy
STEP.397(UUT Test seq.397) : Check VinDC_Posi_Nega Status ---- (0'094) ---- PASS
STEP.398(UUT Test seq.398) : Input Output Eff Noise Multi or Single(164VDC_ PASS | 164VDC_No Load
STEP.399(UUT Test seq.399) : Input Output Eff Noise Multi or Single(164Vdc_ PASS | 164Vdc_Standby_2.5A
STEP.400(UUT Test seq.400) : Static ACDC 34970_or_Load_Multi or Single(12Vs PASS | 12Vsb_2.75A
STEP.401(UUT Test seq.401) : Static ACDC 34970_or_Load_Multi or Single(12Vs PASS | 12Vsb_OCP
STEP.402(UUT Test seq.402) : Static ACDC 34970_or_Load_Multi or Single(12Vs PASS | 12Vsb_2.75A
STEP.403(UUT Test seq.403) : Input Output Eff Noise Multi or Single(164VDC_ PASS | 164VDC_LL_Standby_0.1A
STEP.404(UUT Test seq.404) : PS ON Delay time 80611(164VDC_LL) ---- (0'874) PASS | 164VDC_LL
STEP.405(UUT Test seq.405) : Turn On Timing Test_Multi or Single(164VDC_LL_ PASS | 164VDC_LL_Tac_12V_12Vsb_Rise
STEP.406(UUT Test seq.406) : TTL & Relay Setup ---- (0'000) --------------- PASS
STEP.407(UUT Test seq.407) : PS ON Delay time 80611(164VDC_LL_Tpson_12V_Ris PASS | 164VDC_LL_Tpson_12V_Rise
STEP.408(UUT Test seq.408) : 12V OVP I2C Multi(OVP_I2C) ---- (0'062) ------ PASS | OVP_I2C
STEP.409(UUT Test seq.409) : Static ACDC 34970_or_Load_Multi or Single(164V PASS | 164VDC_LL
STEP.410(UUT Test seq.410) : I2C Read Status OR Multi_S6(12V_OV) ---- (0'10 PASS | 12V_OV
STEP.411(UUT Test seq.411) : 12V OVP Disable I2C Multi ---- (0'062) ------- PASS
STEP.412(UUT Test seq.412) : TTL & Relay Setup ---- (0'624) --------------- PASS
STEP.413(UUT Test seq.413) : Input Output Eff Noise Multi or Single(No Load PASS | No Load
STEP.414(UUT Test seq.414) : Static ACDC 34970_or_Load_Multi or Single(12Vs PASS | 12Vsb_2.75A
STEP.415(UUT Test seq.415) : Static ACDC 34970_or_Load_Multi or Single(12Vs PASS | 12Vsb_OCP
STEP.416(UUT Test seq.416) : Static ACDC 34970_or_Load_Multi or Single(12Vs PASS | 12Vsb_2.75A
STEP.417(UUT Test seq.417) : Input Output Eff Noise Multi or Single(164VDC_ PASS | 164VDC_LL
STEP.418(UUT Test seq.418) : Input Output Eff Noise Multi or Single(164VDC_ PASS | 164VDC_LH
STEP.419(UUT Test seq.419) : Cold Redundant Master Multi _S2 ---- (0'093) - PASS
STEP.420(UUT Test seq.420) : Static ACDC 34970_or_Load_Multi or Single(164V PASS | 164VDC_LL_Cheak CR
STEP.421(UUT Test seq.421) : Disable Cold Redundant Master Multi_S2 ---- (0 PASS
STEP.422(UUT Test seq.422) : Static ACDC 34970_or_Load_Multi or Single(164V PASS | 164VDC_LL_Clear CR
STEP.423(UUT Test seq.423) : Hold Up Timing Test_Multi or Single(164VDC_LL) PASS | 164VDC_LL
STEP.424(UUT Test seq.424) : FAN Full Speed delay time Multi ---- (8'096) - PASS
STEP.425(UUT Test seq.425) : FAN Speed Normal_Multi ---- (0'094) ---------- PASS
STEP.426(UUT Test seq.426) : Turn On Timing Test_Multi or Single(164VDC_HH) PASS | 164VDC_HH
STEP.427(UUT Test seq.427) : I2C Read Status Multi_S6(164VDC_HH) ---- (0'14 PASS | 164VDC_HH
STEP.428(UUT Test seq.428) : PS OFF Time 80611(164VDC_HH) ---- (1'560) ---- PASS | 164VDC_HH
STEP.429(UUT Test seq.429) : I2C Read Status Multi_S6(StandBy) ---- (0'125) PASS | StandBy
STEP.430(UUT Test seq.430) : PS ON Delay time 80611(164VDC_HH) ---- (0'858) PASS | 164VDC_HH
STEP.431(UUT Test seq.431) : Turn On Timing Test_Multi or Single(164VDC_HH_ PASS | 164VDC_HH_Tac_12V_12Vsb_Rise
STEP.432(UUT Test seq.432) : TTL & Relay Setup ---- (0'000) --------------- PASS
STEP.433(UUT Test seq.433) : PS ON Delay time 80611(164VDC_HH_Tpson_12V_Ris PASS | 164VDC_HH_Tpson_12V_Rise
STEP.434(UUT Test seq.434) : Input Output Eff Noise Multi or Single(164VDC_ PASS | 164VDC_50%_L
STEP.435(UUT Test seq.435) : Input Output Eff Noise Multi or Single(164VDC_ PASS | 164VDC_HH
STEP.436(UUT Test seq.436) : Static ACDC 34970_or_Load_Multi or Single(164V PASS | 164VDC_H_12Vsb_2.75A
STEP.437(UUT Test seq.437) : Static ACDC 34970_or_Load_Multi or Single(164V PASS | 164VDC_H_12Vsb_OCP
STEP.438(UUT Test seq.438) : Static ACDC 34970_or_Load_Multi or Single(164V PASS | 164VDC_H_12Vsb_2.75A
STEP.439(UUT Test seq.439) : Cold Redundant Master Multi _S2 ---- (0'093) - PASS
STEP.440(UUT Test seq.440) : Static ACDC 34970_or_Load_Multi or Single(164V PASS | 164VDC_HH_Cheak CR
STEP.441(UUT Test seq.441) : Disable Cold Redundant Master Multi_S2 ---- (0 PASS
STEP.442(UUT Test seq.442) : Static ACDC 34970_or_Load_Multi or Single(164V PASS | 164VDC_HH_Clear CR
STEP.443(UUT Test seq.443) : Input Output Eff Noise Multi or Single(164VDC_ PASS | 164VDC_HL
STEP.444(UUT Test seq.444) : Hold Up Timing Test_Multi or Single(164VDC_70% PASS | 164VDC_70%
STEP.445(UUT Test seq.445) : FAN Full Speed delay time Multi ---- (8'096) - PASS
STEP.446(UUT Test seq.446) : FAN Speed Normal_Multi ---- (0'093) ---------- PASS
STEP.447(UUT Test seq.447) : Turn On Timing Test_Multi or Single(200Vdc_HH) PASS | 200Vdc_HH
STEP.448(UUT Test seq.448) : I2C Read Status Multi_S6(200Vdc_HH) ---- (0'10 PASS | 200Vdc_HH
STEP.449(UUT Test seq.449) : PS OFF Time 80611(200Vdc_HH) ---- (1'544) ---- PASS | 200Vdc_HH
STEP.450(UUT Test seq.450) : PS ON Delay time 80611(200Vdc_HH) ---- (0'873) PASS | 200Vdc_HH
STEP.451(UUT Test seq.451) : Turn On Timing Test_Multi or Single(200Vdc_HH_ PASS | 200Vdc_HH_Tac_12V_12Vsb_Rise
STEP.452(UUT Test seq.452) : TTL & Relay Setup ---- (0'000) --------------- PASS
STEP.453(UUT Test seq.453) : PS ON Delay time 80611(200Vdc_HH_Tpson_12V_Ris PASS | 200Vdc_HH_Tpson_12V_Rise
STEP.454(UUT Test seq.454) : Input Output Eff Noise Multi or Single(200Vdc_ PASS | 200Vdc_HL
STEP.455(UUT Test seq.455) : Static ACDC 34970_or_Load_Multi or Single(200V PASS | 200Vdc_H_12Vsb_2.75A
STEP.456(UUT Test seq.456) : Static ACDC 34970_or_Load_Multi or Single(200V PASS | 200Vdc_H_12Vsb_OCP
STEP.457(UUT Test seq.457) : Static ACDC 34970_or_Load_Multi or Single(200V PASS | 200Vdc_H_12Vsb_2.75A
STEP.458(UUT Test seq.458) : Cold Redundant Master Multi _S2 ---- (0'093) - PASS
STEP.459(UUT Test seq.459) : Static ACDC 34970_or_Load_Multi or Single(200V PASS | 200Vdc_HH_Cheak CR
STEP.460(UUT Test seq.460) : Disable Cold Redundant Master Multi_S2 ---- (0 PASS
STEP.461(UUT Test seq.461) : Static ACDC 34970_or_Load_Multi or Single(200V PASS | 200Vdc_HH_Clear CR
STEP.462(UUT Test seq.462) : Input Output Eff Noise Multi or Single(200Vdc_ PASS | 200Vdc_HH
STEP.463(UUT Test seq.463) : Hold Up Timing Test_Multi or Single(200Vdc_70% PASS | 200Vdc_70%
STEP.464(UUT Test seq.464) : FAN Full Speed delay time Multi ---- (8'190) - PASS
STEP.465(UUT Test seq.465) : FAN Speed Normal_Multi ---- (0'093) ---------- PASS
STEP.466(UUT Test seq.466) : Turn On Timing Test_Multi or Single(220VDC_HH) PASS | 220VDC_HH
STEP.467(UUT Test seq.467) : I2C Read Status Multi_S6(220VDC_HH) ---- (0'10 PASS | 220VDC_HH
STEP.468(UUT Test seq.468) : PS OFF Time 80611(220VDC_HH) ---- (1'575) ---- PASS | 220VDC_HH
STEP.469(UUT Test seq.469) : I2C Read Status Multi_S6(StandBy) ---- (0'124) PASS | StandBy
STEP.470(UUT Test seq.470) : PS ON Delay time 80611(220VDC_HH) ---- (0'858) PASS | 220VDC_HH
STEP.471(UUT Test seq.471) : Turn On Timing Test_Multi or Single(220VDC_HH_ PASS | 220VDC_HH_Tac_12V_12Vsb_Rise
STEP.472(UUT Test seq.472) : TTL & Relay Setup ---- (0'000) --------------- PASS
STEP.473(UUT Test seq.473) : PS ON Delay time 80611(220VDC_HH_Tpson_12V_Ris PASS | 220VDC_HH_Tpson_12V_Rise
STEP.474(UUT Test seq.474) : Input Output Eff Noise Multi or Single(220VDC_ PASS | 220VDC_HL
STEP.475(UUT Test seq.475) : Static ACDC 34970_or_Load_Multi or Single(220V PASS | 220Vdc_H_12Vsb_2.75A
STEP.476(UUT Test seq.476) : Static ACDC 34970_or_Load_Multi or Single(220V PASS | 220Vdc_H_12Vsb_OCP
STEP.477(UUT Test seq.477) : Static ACDC 34970_or_Load_Multi or Single(220V PASS | 220Vdc_H_12Vsb_2.75A
STEP.478(UUT Test seq.478) : Cold Redundant Master Multi _S2 ---- (0'094) - PASS
STEP.479(UUT Test seq.479) : Static ACDC 34970_or_Load_Multi or Single(220V PASS | 220VDC_HH_Cheak CR
STEP.480(UUT Test seq.480) : Disable Cold Redundant Master Multi_S2 ---- (0 PASS
STEP.481(UUT Test seq.481) : Static ACDC 34970_or_Load_Multi or Single(220V PASS | 220VDC_HH_Clear CR
STEP.482(UUT Test seq.482) : Input Output Eff Noise Multi or Single(220VDC_ PASS | 220VDC_HH
STEP.483(UUT Test seq.483) : Hold Up Timing Test_Multi or Single(220VDC_70% PASS | 220VDC_70%
STEP.484(UUT Test seq.484) : FAN Full Speed delay time Multi ---- (8'096) - PASS
STEP.485(UUT Test seq.485) : FAN Speed Normal_Multi ---- (0'093) ---------- PASS
STEP.486(UUT Test seq.486) : Turn On Timing Test_Multi or Single(300VDC_LL) PASS | 300VDC_LL
STEP.487(UUT Test seq.487) : I2C Read Status Multi_S6(300VDC_LL) ---- (0'10 PASS | 300VDC_LL
STEP.488(UUT Test seq.488) : PS OFF Time 80611(300VDC_LL) ---- (1'544) ---- PASS | 300VDC_LL
STEP.489(UUT Test seq.489) : I2C Read Status Multi_S6(StandBy) ---- (0'125) PASS | StandBy
STEP.490(UUT Test seq.490) : Input Output Eff Noise Multi or Single(No Load PASS | No Load
STEP.491(UUT Test seq.491) : Input Output Eff Noise Multi or Single(300Vdc_ PASS | 300Vdc_Standby_2.5A
STEP.492(UUT Test seq.492) : Static ACDC 34970_or_Load_Multi or Single(12Vs PASS | 12Vsb_2.75A
STEP.493(UUT Test seq.493) : Static ACDC 34970_or_Load_Multi or Single(12Vs PASS | 12Vsb_OCP
STEP.494(UUT Test seq.494) : Static ACDC 34970_or_Load_Multi or Single(12Vs PASS | 12Vsb_2.75A
STEP.495(UUT Test seq.495) : Input Output Eff Noise Multi or Single(300Vdc_ PASS | 300Vdc_Standby_0.1A
STEP.496(UUT Test seq.496) : PS ON Delay time 80611(300VDC_LL) ---- (0'983) PASS | 300VDC_LL
STEP.497(UUT Test seq.497) : Turn On Timing Test_Multi or Single(300VDC_LL_ PASS | 300VDC_LL_Tac_12V_12Vsb_Rise
STEP.498(UUT Test seq.498) : TTL & Relay Setup ---- (0'016) --------------- PASS
STEP.499(UUT Test seq.499) : PS ON Delay time 80611(300VDC_LL_Tpson_12V_Ris PASS | 300VDC_LL_Tpson_12V_Rise
STEP.500(UUT Test seq.500) : 12V OVP I2C Multi(OVP_I2C) ---- (0'063) ------ PASS | OVP_I2C
STEP.501(UUT Test seq.501) : Static ACDC 34970_or_Load_Multi or Single(300V PASS | 300VDC_LL
STEP.502(UUT Test seq.502) : I2C Read Status OR Multi_S6(12V_OV) ---- (0'10 PASS | 12V_OV
STEP.503(UUT Test seq.503) : 12V OVP Disable I2C Multi ---- (0'063) ------- PASS
STEP.504(UUT Test seq.504) : TTL & Relay Setup ---- (0'405) --------------- PASS
STEP.505(UUT Test seq.505) : Input Output Eff Noise Multi or Single(No Load PASS | No Load
STEP.506(UUT Test seq.506) : Static ACDC 34970_or_Load_Multi or Single(12Vs PASS | 12Vsb_2.75A
STEP.507(UUT Test seq.507) : Static ACDC 34970_or_Load_Multi or Single(12Vs PASS | 12Vsb_OCP
STEP.508(UUT Test seq.508) : Static ACDC 34970_or_Load_Multi or Single(12Vs PASS | 12Vsb_2.75A
STEP.509(UUT Test seq.509) : Input Output Eff Noise Multi or Single(300VDC_ PASS | 300VDC_LL
STEP.510(UUT Test seq.510) : Input Output Eff Noise Multi or Single(300VDC_ PASS | 300VDC_LH
STEP.511(UUT Test seq.511) : Cold Redundant Master Multi _S2 ---- (0'110) - PASS
STEP.512(UUT Test seq.512) : Static ACDC 34970_or_Load_Multi or Single(300V PASS | 300VDC_LL_Cheak CR
STEP.513(UUT Test seq.513) : Disable Cold Redundant Master Multi_S2 ---- (0 PASS
STEP.514(UUT Test seq.514) : Static ACDC 34970_or_Load_Multi or Single(300V PASS | 300VDC_LL_Clear CR
STEP.515(UUT Test seq.515) : Hold Up Timing Test_Multi or Single(300VDC_LL) PASS | 300VDC_LL
STEP.516(UUT Test seq.516) : FAN Full Speed delay time Multi ---- (8'096) - PASS
STEP.517(UUT Test seq.517) : FAN Speed Normal_Multi ---- (0'078) ---------- PASS
STEP.518(UUT Test seq.518) : 61512 Ac Source ACDC Mode_Multi_S2(300VDC_HH) PASS | 300VDC_HH
STEP.519(UUT Test seq.519) : Turn On Timing Test_Multi or Single(300VDC_HH) PASS | 300VDC_HH
STEP.520(UUT Test seq.520) : I2C Read Status Multi_S6(300VDC_HH) ---- (0'12 PASS | 300VDC_HH
STEP.521(UUT Test seq.521) : PS OFF Time 80611(300VDC_HH) ---- (1'653) ---- PASS | 300VDC_HH
STEP.522(UUT Test seq.522) : I2C Read Status Multi_S6(StandBy) ---- (0'109) PASS | StandBy
STEP.523(UUT Test seq.523) : PS ON Delay time 80611(300VDC_HH) ---- (0'982) PASS | 300VDC_HH
STEP.524(UUT Test seq.524) : Turn On Timing Test_Multi or Single(300VDC_HH_ PASS | 300VDC_HH_Tac_12V_12Vsb_Rise
STEP.525(UUT Test seq.525) : TTL & Relay Setup ---- (0'000) --------------- PASS
STEP.526(UUT Test seq.526) : PS ON Delay time 80611(300VDC_HH_Tpson_12V_Ris PASS | 300VDC_HH_Tpson_12V_Rise
STEP.527(UUT Test seq.527) : Input Output Eff Noise Multi or Single(300VDC_ PASS | 300VDC_50%_L
STEP.528(UUT Test seq.528) : Input Output Eff Noise Multi or Single(300VDC_ PASS | 300VDC_HL
STEP.529(UUT Test seq.529) : Cold Redundant Master Multi _S2 ---- (0'094) - PASS
STEP.530(UUT Test seq.530) : Static ACDC 34970_or_Load_Multi or Single(300V PASS | 300VDC_HH_Cheak CR
STEP.531(UUT Test seq.531) : Disable Cold Redundant Master Multi_S2 ---- (0 PASS
STEP.532(UUT Test seq.532) : Static ACDC 34970_or_Load_Multi or Single(300V PASS | 300VDC_HH_Clear CR
STEP.533(UUT Test seq.533) : Input Output Eff Noise Multi or Single(300VDC_ PASS | 300VDC_HH
STEP.534(UUT Test seq.534) : Static ACDC 34970_or_Load_Multi or Single(300V PASS | 300Vdc_H_12Vsb_2.75A
STEP.535(UUT Test seq.535) : Static ACDC 34970_or_Load_Multi or Single(300V PASS | 300Vdc_H_12Vsb_OCP
STEP.536(UUT Test seq.536) : Static ACDC 34970_or_Load_Multi or Single(300V PASS | 300Vdc_H_12Vsb_2.75A
STEP.537(UUT Test seq.537) : Hold Up Timing Test_Multi or Single(300VDC_70% PASS | 300VDC_70%
STEP.538(UUT Test seq.538) : FAN Full Speed delay time Multi ---- (5'101) - PASS
STEP.539(UUT Test seq.539) : FAN Speed Normal_Multi ---- (0'094) ---------- PASS
STEP.540(UUT Test seq.540) : 61512 Ac Source ACDC Mode_Multi_S2 ---- (0'172 PASS
STEP.541(UUT Test seq.541) : Input Source Distortion_Multi or Single ---- ( PASS
STEP.542(UUT Test seq.542) : Static ACDC 34970_or_Load_Multi or Single(---- PASS | --------100Vac Distortion_H
STEP.543(UUT Test seq.543) : Input Source Distortion_Multi or Single ---- ( PASS
STEP.544(UUT Test seq.544) : Static ACDC 34970_or_Load_Multi or Single(---- PASS | --------100Vac Distortion_L
STEP.545(UUT Test seq.545) : Input Source Distortion_Multi or Single ---- ( PASS
STEP.546(UUT Test seq.546) : Static ACDC 34970_or_Load_Multi or Single(---- PASS | --------200Vac Distortion_L
STEP.547(UUT Test seq.547) : Input Source Distortion_Multi or Single ---- ( PASS
STEP.548(UUT Test seq.548) : Static ACDC 34970_or_Load_Multi or Single(---- PASS | --------200Vac Distortion_H
STEP.549(UUT Test seq.549) : Input Source Set SinWaveform_Multi or Single - PASS
STEP.550(UUT Test seq.550) : Static ACDC 34970_or_Load_Multi or Single(89.5 PASS | 89.5Vac_ON
STEP.551(UUT Test seq.551) : Static ACDC 34970_or_Load_Multi or Single(80Va PASS | 80Vac_ON
STEP.552(UUT Test seq.552) : Static ACDC 34970_or_Load_Multi or Single(70.5 PASS | 70.5Vac_OFF
STEP.553(UUT Test seq.553) : Static ACDC 34970_or_Load_Multi or Single(79.8 PASS | 79.8Vac_OFF
STEP.554(UUT Test seq.554) : I2C Read Status Multi_S6(Vin_UV) ---- (0'125) PASS | Vin_UV
STEP.555(UUT Test seq.555) : Static ACDC 34970_or_Load_Multi or Single(89.5 PASS | 89.5Vac_ON
STEP.556(UUT Test seq.556) : Static ACDC 34970_or_Load_Multi or Single(80Va PASS | 80Vac_ON
STEP.557(UUT Test seq.557) : Static ACDC 34970_or_Load_Multi or Single(70.5 PASS | 70.5Vac_OFF
STEP.558(UUT Test seq.558) : Static ACDC 34970_or_Load_Multi or Single(79.8 PASS | 79.8Vac_OFF
STEP.559(UUT Test seq.559) : AC Line Sag Surge 80611N-2_Multi_S5(90V-5S) -- PASS | 90V-5S
STEP.560(UUT Test seq.560) : Static ACDC 34970_or_Load_Multi or Single ---- PASS
STEP.561(UUT Test seq.561) : AC Source ON/OFF(input source)_Multi_S2 ---- ( PASS
STEP.562(UUT Test seq.562) : AC Line Sag Surge 80611N-2_Multi_S5(264V-5S) - PASS | 264V-5S
STEP.563(UUT Test seq.563) : Static ACDC 34970_or_Load_Multi or Single ---- PASS
STEP.564(UUT Test seq.564) : AC Source ON/OFF(input source)_Multi_S2 ---- ( PASS
STEP.565(UUT Test seq.565) : AC Line Sag Surge 80611N-2_Multi_S5(115V-->97. PASS | 115V-->97.75V -15S
STEP.566(UUT Test seq.566) : I2C Read Status Multi_S6 ---- (0'125) -------- PASS
STEP.567(UUT Test seq.567) : AC Line Sag Surge 80611N-2_Multi_S5(115V-->132 PASS | 115V-->132.25V -15S
STEP.568(UUT Test seq.568) : I2C Read Status Multi_S6 ---- (0'109) -------- PASS
STEP.569(UUT Test seq.569) : AC Source ON/OFF(input source)_Multi_S2 ---- ( PASS
STEP.570(UUT Test seq.570) : Set Input Condition_Load_S4 ---- (0'016) ----- PASS
STEP.571(UUT Test seq.571) : Set Drop Time ---- (0'000) ------------------- PASS
STEP.572(UUT Test seq.572) : AC_DC Line Sag Surge 80611N-2_Multi_S2(90Vac - PASS | 90Vac -->0Vac -10ms-0
STEP.573(UUT Test seq.573) : I2C Read Status Multi_S6(90Vac -->0Vac - 10ms- PASS | 90Vac -->0Vac - 10ms-0
STEP.574(UUT Test seq.574) : AC_DC Line Sag Surge 80611N-2_Multi_S2(90Vac - PASS | 90Vac -->0Vac - 10ms-45
STEP.575(UUT Test seq.575) : I2C Read Status Multi_S6(90Vac -->0Vac - 10ms- PASS | 90Vac -->0Vac - 10ms-45
STEP.576(UUT Test seq.576) : AC_DC Line Sag Surge 80611N-2_Multi_S2(90Vac - PASS | 90Vac -->0Vac - 10ms-90
STEP.577(UUT Test seq.577) : I2C Read Status Multi_S6(90Vac -->0Vac - 10ms- PASS | 90Vac -->0Vac - 10ms-90
STEP.578(UUT Test seq.578) : AC_DC Line Sag Surge 80611N-2_Multi_S2(90Vac - PASS | 90Vac -->0Vac - 10ms-135
STEP.579(UUT Test seq.579) : I2C Read Status Multi_S6(90Vac -->0Vac - 10ms- PASS | 90Vac -->0Vac - 10ms-135
STEP.580(UUT Test seq.580) : AC_DC Line Sag Surge 80611N-2_Multi_S2(90Vac - PASS | 90Vac -->0Vac - 10ms-225
STEP.581(UUT Test seq.581) : I2C Read Status Multi_S6(90Vac -->0Vac - 10ms- PASS | 90Vac -->0Vac - 10ms-225
STEP.582(UUT Test seq.582) : AC_DC Line Sag Surge 80611N-2_Multi_S2(90Vac - PASS | 90Vac -->0Vac - 10ms-270
STEP.583(UUT Test seq.583) : I2C Read Status Multi_S6(90Vac -->0Vac - 10ms- PASS | 90Vac -->0Vac - 10ms-270
STEP.584(UUT Test seq.584) : AC_DC Line Sag Surge 80611N-2_Multi_S2(90Vac - PASS | 90Vac -->0Vac - 10ms-315
STEP.585(UUT Test seq.585) : I2C Read Status Multi_S6(90Vac -->0Vac - 10ms- PASS | 90Vac -->0Vac - 10ms-315
STEP.586(UUT Test seq.586) : AC Source ON/OFF(input source)_Multi_S2 ---- ( PASS
STEP.587(UUT Test seq.587) : Set Input Condition_Load_S4 ---- (0'000) ----- PASS
STEP.588(UUT Test seq.588) : Set Drop Time ---- (0'000) ------------------- PASS
STEP.589(UUT Test seq.589) : AC_DC Line Sag Surge 80611N-2_Multi_S2(100Vac PASS | 100Vac -->0Vac -10ms-0
STEP.590(UUT Test seq.590) : I2C Read Status Multi_S6(100Vac -->0Vac - 10ms PASS | 100Vac -->0Vac - 10ms-0
STEP.591(UUT Test seq.591) : AC_DC Line Sag Surge 80611N-2_Multi_S2(100Vac PASS | 100Vac -->0Vac - 10ms-45
STEP.592(UUT Test seq.592) : I2C Read Status Multi_S6(100Vac -->0Vac - 10ms PASS | 100Vac -->0Vac - 10ms-45
STEP.593(UUT Test seq.593) : AC_DC Line Sag Surge 80611N-2_Multi_S2(100Vac PASS | 100Vac -->0Vac - 10ms-90
STEP.594(UUT Test seq.594) : I2C Read Status Multi_S6(100Vac -->0Vac - 10ms PASS | 100Vac -->0Vac - 10ms-90
STEP.595(UUT Test seq.595) : AC_DC Line Sag Surge 80611N-2_Multi_S2(100Vac PASS | 100Vac -->0Vac - 10ms-135
STEP.596(UUT Test seq.596) : I2C Read Status Multi_S6(100Vac -->0Vac - 10ms PASS | 100Vac -->0Vac - 10ms-135
STEP.597(UUT Test seq.597) : AC_DC Line Sag Surge 80611N-2_Multi_S2(100Vac PASS | 100Vac -->0Vac - 10ms-225
STEP.598(UUT Test seq.598) : I2C Read Status Multi_S6(100Vac -->0Vac - 10ms PASS | 100Vac -->0Vac - 10ms-225
STEP.599(UUT Test seq.599) : AC_DC Line Sag Surge 80611N-2_Multi_S2(100Vac PASS | 100Vac -->0Vac - 10ms-270
STEP.600(UUT Test seq.600) : I2C Read Status Multi_S6(100Vac -->0Vac - 10ms PASS | 100Vac -->0Vac - 10ms-270
STEP.601(UUT Test seq.601) : AC_DC Line Sag Surge 80611N-2_Multi_S2(100Vac PASS | 100Vac -->0Vac - 10ms-315
STEP.602(UUT Test seq.602) : I2C Read Status Multi_S6(100Vac -->0Vac - 10ms PASS | 100Vac -->0Vac - 10ms-315
STEP.603(UUT Test seq.603) : AC Source ON/OFF(input source)_Multi_S2 ---- ( PASS
STEP.604(UUT Test seq.604) : Set Input Condition_Load_S4 ---- (0'000) ----- PASS
STEP.605(UUT Test seq.605) : Set Drop Time ---- (0'000) ------------------- PASS
STEP.606(UUT Test seq.606) : AC_DC Line Sag Surge 80611N-2_Multi_S2(180Vac PASS | 180Vac -->0Vac -10ms-0
STEP.607(UUT Test seq.607) : I2C Read Status Multi_S6(180Vac -->0Vac - 10ms PASS | 180Vac -->0Vac - 10ms-0
STEP.608(UUT Test seq.608) : AC_DC Line Sag Surge 80611N-2_Multi_S2(180Vac PASS | 180Vac -->0Vac - 10ms-45
STEP.609(UUT Test seq.609) : I2C Read Status Multi_S6(180Vac -->0Vac - 10ms PASS | 180Vac -->0Vac - 10ms-45
STEP.610(UUT Test seq.610) : AC_DC Line Sag Surge 80611N-2_Multi_S2(180Vac PASS | 180Vac -->0Vac - 10ms-90
STEP.611(UUT Test seq.611) : I2C Read Status Multi_S6(180Vac -->0Vac - 10ms PASS | 180Vac -->0Vac - 10ms-90
STEP.612(UUT Test seq.612) : AC_DC Line Sag Surge 80611N-2_Multi_S2(180Vac PASS | 180Vac -->0Vac - 10ms-135
STEP.613(UUT Test seq.613) : I2C Read Status Multi_S6(180Vac -->0Vac - 10ms PASS | 180Vac -->0Vac - 10ms-135
STEP.614(UUT Test seq.614) : AC_DC Line Sag Surge 80611N-2_Multi_S2(180Vac PASS | 180Vac -->0Vac - 10ms-225
STEP.615(UUT Test seq.615) : I2C Read Status Multi_S6(180Vac -->0Vac - 10ms PASS | 180Vac -->0Vac - 10ms-225
STEP.616(UUT Test seq.616) : AC_DC Line Sag Surge 80611N-2_Multi_S2(180Vac PASS | 180Vac -->0Vac - 10ms-270
STEP.617(UUT Test seq.617) : I2C Read Status Multi_S6(180Vac -->0Vac - 10ms PASS | 180Vac -->0Vac - 10ms-270
STEP.618(UUT Test seq.618) : AC_DC Line Sag Surge 80611N-2_Multi_S2(180Vac PASS | 180Vac -->0Vac - 10ms-315
STEP.619(UUT Test seq.619) : I2C Read Status Multi_S6(180Vac -->0Vac - 10ms PASS | 180Vac -->0Vac - 10ms-315
STEP.620(UUT Test seq.620) : AC Source ON/OFF(input source)_Multi_S2 ---- ( PASS
STEP.621(UUT Test seq.621) : Set Input Condition_Load_S4 ---- (0'016) ----- PASS
STEP.622(UUT Test seq.622) : Set Drop Time ---- (0'000) ------------------- PASS
STEP.623(UUT Test seq.623) : AC_DC Line Sag Surge 80611N-2_Multi_S2(200Vac PASS | 200Vac -->0Vac -10ms-0
STEP.624(UUT Test seq.624) : I2C Read Status Multi_S6(200Vac -->0Vac - 10ms PASS | 200Vac -->0Vac - 10ms-0
STEP.625(UUT Test seq.625) : AC_DC Line Sag Surge 80611N-2_Multi_S2(200Vac PASS | 200Vac -->0Vac - 10ms-45
STEP.626(UUT Test seq.626) : I2C Read Status Multi_S6(200Vac -->0Vac - 10ms PASS | 200Vac -->0Vac - 10ms-45
STEP.627(UUT Test seq.627) : AC_DC Line Sag Surge 80611N-2_Multi_S2(200Vac PASS | 200Vac -->0Vac - 10ms-90
STEP.628(UUT Test seq.628) : I2C Read Status Multi_S6(200Vac -->0Vac - 10ms PASS | 200Vac -->0Vac - 10ms-90
STEP.629(UUT Test seq.629) : AC_DC Line Sag Surge 80611N-2_Multi_S2(200Vac PASS | 200Vac -->0Vac - 10ms-135
STEP.630(UUT Test seq.630) : I2C Read Status Multi_S6(200Vac -->0Vac - 10ms PASS | 200Vac -->0Vac - 10ms-135
STEP.631(UUT Test seq.631) : AC_DC Line Sag Surge 80611N-2_Multi_S2(200Vac PASS | 200Vac -->0Vac - 10ms-225
STEP.632(UUT Test seq.632) : I2C Read Status Multi_S6(200Vac -->0Vac - 10ms PASS | 200Vac -->0Vac - 10ms-225
STEP.633(UUT Test seq.633) : AC_DC Line Sag Surge 80611N-2_Multi_S2(200Vac PASS | 200Vac -->0Vac - 10ms-270
STEP.634(UUT Test seq.634) : I2C Read Status Multi_S6(200Vac -->0Vac - 10ms PASS | 200Vac -->0Vac - 10ms-270
STEP.635(UUT Test seq.635) : AC_DC Line Sag Surge 80611N-2_Multi_S2(200Vac PASS | 200Vac -->0Vac - 10ms-315
STEP.636(UUT Test seq.636) : I2C Read Status Multi_S6(200Vac -->0Vac - 10ms PASS | 200Vac -->0Vac - 10ms-315
STEP.637(UUT Test seq.637) : AC Source ON/OFF(input source)_Multi_S2 ---- ( PASS
STEP.638(UUT Test seq.638) : Set Input Condition_Load_S4 ---- (0'015) ----- PASS
STEP.639(UUT Test seq.639) : Set Drop Time ---- (0'000) ------------------- PASS
STEP.640(UUT Test seq.640) : AC_DC Line Sag Surge 80611N-2_Multi_S2(220Vac PASS | 220Vac -->0Vac -10ms-0
STEP.641(UUT Test seq.641) : I2C Read Status Multi_S6(220Vac -->0Vac - 10ms PASS | 220Vac -->0Vac - 10ms-0
STEP.642(UUT Test seq.642) : AC_DC Line Sag Surge 80611N-2_Multi_S2(220Vac PASS | 220Vac -->0Vac - 10ms-45
STEP.643(UUT Test seq.643) : I2C Read Status Multi_S6(220Vac -->0Vac - 10ms PASS | 220Vac -->0Vac - 10ms-45
STEP.644(UUT Test seq.644) : AC_DC Line Sag Surge 80611N-2_Multi_S2(220Vac PASS | 220Vac -->0Vac - 10ms-90
STEP.645(UUT Test seq.645) : I2C Read Status Multi_S6(220Vac -->0Vac - 10ms PASS | 220Vac -->0Vac - 10ms-90
STEP.646(UUT Test seq.646) : AC_DC Line Sag Surge 80611N-2_Multi_S2(220Vac PASS | 220Vac -->0Vac - 10ms-135
STEP.647(UUT Test seq.647) : I2C Read Status Multi_S6(220Vac -->0Vac - 10ms PASS | 220Vac -->0Vac - 10ms-135
STEP.648(UUT Test seq.648) : AC_DC Line Sag Surge 80611N-2_Multi_S2(220Vac PASS | 220Vac -->0Vac - 10ms-225
STEP.649(UUT Test seq.649) : I2C Read Status Multi_S6(220Vac -->0Vac - 10ms PASS | 220Vac -->0Vac - 10ms-225
STEP.650(UUT Test seq.650) : AC_DC Line Sag Surge 80611N-2_Multi_S2(220Vac PASS | 220Vac -->0Vac - 10ms-270
STEP.651(UUT Test seq.651) : I2C Read Status Multi_S6(220Vac -->0Vac - 10ms PASS | 220Vac -->0Vac - 10ms-270
STEP.652(UUT Test seq.652) : AC_DC Line Sag Surge 80611N-2_Multi_S2(220Vac PASS | 220Vac -->0Vac - 10ms-315
STEP.653(UUT Test seq.653) : I2C Read Status Multi_S6(220Vac -->0Vac - 10ms PASS | 220Vac -->0Vac - 10ms-315
STEP.654(UUT Test seq.654) : AC Source ON/OFF(input source)_Multi_S2 ---- ( PASS
STEP.655(UUT Test seq.655) : Set Input Condition_Load_S4 ---- (0'000) ----- PASS
STEP.656(UUT Test seq.656) : Set Drop Time ---- (0'000) ------------------- PASS
STEP.657(UUT Test seq.657) : AC_DC Line Sag Surge 80611N-2_Multi_S2(264Vac PASS | 264Vac -->0Vac -10ms-0
STEP.658(UUT Test seq.658) : I2C Read Status Multi_S6(264Vac -->0Vac - 10ms PASS | 264Vac -->0Vac - 10ms-0
STEP.659(UUT Test seq.659) : AC_DC Line Sag Surge 80611N-2_Multi_S2(264Vac PASS | 264Vac -->0Vac - 10ms-45
STEP.660(UUT Test seq.660) : I2C Read Status Multi_S6(264Vac -->0Vac - 10ms PASS | 264Vac -->0Vac - 10ms-45
STEP.661(UUT Test seq.661) : AC_DC Line Sag Surge 80611N-2_Multi_S2(264Vac PASS | 264Vac -->0Vac - 10ms-90
STEP.662(UUT Test seq.662) : I2C Read Status Multi_S6(264Vac -->0Vac - 10ms PASS | 264Vac -->0Vac - 10ms-90
STEP.663(UUT Test seq.663) : AC_DC Line Sag Surge 80611N-2_Multi_S2(264Vac PASS | 264Vac -->0Vac - 10ms-135
STEP.664(UUT Test seq.664) : I2C Read Status Multi_S6(264Vac -->0Vac - 10ms PASS | 264Vac -->0Vac - 10ms-135
STEP.665(UUT Test seq.665) : AC_DC Line Sag Surge 80611N-2_Multi_S2(264Vac PASS | 264Vac -->0Vac - 10ms-225
STEP.666(UUT Test seq.666) : I2C Read Status Multi_S6(264Vac -->0Vac - 10ms PASS | 264Vac -->0Vac - 10ms-225
STEP.667(UUT Test seq.667) : AC_DC Line Sag Surge 80611N-2_Multi_S2(264Vac PASS | 264Vac -->0Vac - 10ms-270
STEP.668(UUT Test seq.668) : I2C Read Status Multi_S6(264Vac -->0Vac - 10ms PASS | 264Vac -->0Vac - 10ms-270
STEP.669(UUT Test seq.669) : AC_DC Line Sag Surge 80611N-2_Multi_S2(264Vac PASS | 264Vac -->0Vac - 10ms-315
STEP.670(UUT Test seq.670) : I2C Read Status Multi_S6(264Vac -->0Vac - 10ms PASS | 264Vac -->0Vac - 10ms-315
STEP.671(UUT Test seq.671) : AC Source ON/OFF(input source)_Multi_S2 ---- ( PASS
STEP.672(UUT Test seq.672) : AC Line Sag Surge 80611N-2_Multi_S5(115Vac --> PASS | 115Vac -->80.5Vac - 0.5 cycle
STEP.673(UUT Test seq.673) : I2C Read Status Multi_S6(115Vac -->80.5Vac - 0 PASS | 115Vac -->80.5Vac - 0.5 cycle
STEP.674(UUT Test seq.674) : AC Line Sag Surge 80611N-2_Multi_S5(115Vac --> PASS | 115Vac -->149.5Vac - 0.5 cycle
STEP.675(UUT Test seq.675) : I2C Read Status Multi_S6(115Vac -->149.5Vac - PASS | 115Vac -->149.5Vac - 0.5 cycle
STEP.676(UUT Test seq.676) : AC Source ON/OFF(input source)_Multi_S2 ---- ( PASS
STEP.677(UUT Test seq.677) : AC Line Sag Surge 80611N-2_Multi_S5(220Vac --> PASS | 220Vac -->253Vac - 100ms Max
STEP.678(UUT Test seq.678) : I2C Read Status Multi_S6(220Vac -->253Vac - 10 PASS | 220Vac -->253Vac - 100ms Max
STEP.679(UUT Test seq.679) : AC Line Sag Surge 80611N-2_Multi_S5(220Vac --> PASS | 220Vac -->286Vac - 0.5 Cycle Max
STEP.680(UUT Test seq.680) : I2C Read Status Multi_S6(220Vac -->286Vac - 0. PASS | 220Vac -->286Vac - 0.5 Cycle Max
STEP.681(UUT Test seq.681) : AC Line Sag Surge 80611N-2_Multi_S5(220Vac --> PASS | 220Vac -->253Vac - 100ms Min
STEP.682(UUT Test seq.682) : I2C Read Status Multi_S6(220Vac -->253Vac - 10 PASS | 220Vac -->253Vac - 100ms Min
STEP.683(UUT Test seq.683) : AC Line Sag Surge 80611N-2_Multi_S5(220Vac --> PASS | 220Vac -->286Vac - 0.5 Cycle Min
STEP.684(UUT Test seq.684) : I2C Read Status Multi_S6(220Vac -->286Vac - 0. PASS | 220Vac -->286Vac - 0.5 Cycle Min
STEP.685(UUT Test seq.685) : UUT Off_Multi_S2 ---- (1'108) ---------------- PASS
STEP.686(UUT Test seq.686) : FAN Full Speed delay time Multi ---- (10'093) PASS
STEP.687(UUT Test seq.687) : FAN Speed Normal_Multi ---- (0'109) ---------- PASS
STEP.688(UUT Test seq.688) : 61512 Ac Source ACDC Mode_Multi_S2 ---- (0'156 PASS
STEP.689(UUT Test seq.689) : TTL & Relay Setup ---- (0'219) --------------- PASS
STEP.690(UUT Test seq.690) : Input Output Accuracy Multi or Single_S3(230Va PASS | 230Vac-50Hz-100%
STEP.691(UUT Test seq.691) : Harmonic Multi UUT_Test_S2 ---- (2'122) ------ PASS
STEP.692(UUT Test seq.692) : Input Output Accuracy Multi or Single_S3(230Va PASS | 230Vac-50Hz-90%
STEP.693(UUT Test seq.693) : Harmonic Multi UUT_Test_S2 ---- (2'122) ------ PASS
STEP.694(UUT Test seq.694) : Input Output Accuracy Multi or Single_S3(230Va PASS | 230Vac-50Hz-80%
STEP.695(UUT Test seq.695) : Harmonic Multi UUT_Test_S2 ---- (2'153) ------ PASS
STEP.696(UUT Test seq.696) : Input Output Accuracy Multi or Single_S3(230Va PASS | 230Vac-50Hz-70%
STEP.697(UUT Test seq.697) : Harmonic Multi UUT_Test_S2 ---- (2'122) ------ PASS
STEP.698(UUT Test seq.698) : Input Output Accuracy Multi or Single_S3(230Va PASS | 230Vac-50Hz-60%
STEP.699(UUT Test seq.699) : Harmonic Multi UUT_Test_S2 ---- (2'121) ------ PASS
STEP.700(UUT Test seq.700) : Input Output Accuracy Multi or Single_S3(230Va PASS | 230Vac-50Hz-50%
STEP.701(UUT Test seq.701) : Harmonic Multi UUT_Test_S2 ---- (2'122) ------ PASS
STEP.702(UUT Test seq.702) : Input Output Accuracy Multi or Single_S3(230Va PASS | 230Vac-50Hz-40%
STEP.703(UUT Test seq.703) : Harmonic Multi UUT_Test_S2 ---- (2'138) ------ PASS
STEP.704(UUT Test seq.704) : Input Output Accuracy Multi or Single_S3(230Va PASS | 230Vac-50Hz-30%
STEP.705(UUT Test seq.705) : Harmonic Multi UUT_Test_S2 ---- (2'106) ------ PASS
STEP.706(UUT Test seq.706) : Input Output Accuracy Multi or Single_S3(230Va PASS | 230Vac-50Hz-20%
STEP.707(UUT Test seq.707) : Harmonic Multi UUT_Test_S2 ---- (2'122) ------ PASS
STEP.708(UUT Test seq.708) : Input Output Accuracy Multi or Single_S3(230Va PASS | 230Vac-50Hz-10%
STEP.709(UUT Test seq.709) : Harmonic Multi UUT_Test_S2 ---- (2'122) ------ PASS
STEP.710(UUT Test seq.710) : Input Output Accuracy Multi or Single_S3(230Va PASS | 230Vac-60Hz-100%
STEP.711(UUT Test seq.711) : Input Output Accuracy Multi or Single_S3(230Va PASS | 230Vac-60Hz-90%
STEP.712(UUT Test seq.712) : Input Output Accuracy Multi or Single_S3(230Va PASS | 230Vac-60Hz-80%
STEP.713(UUT Test seq.713) : Input Output Accuracy Multi or Single_S3(230Va PASS | 230Vac-60Hz-70%
STEP.714(UUT Test seq.714) : Input Output Accuracy Multi or Single_S3(230Va PASS | 230Vac-60Hz-60%
STEP.715(UUT Test seq.715) : Input Output Accuracy Multi or Single_S3(230Va PASS | 230Vac-60Hz-50%
STEP.716(UUT Test seq.716) : Input Output Accuracy Multi or Single_S3(230Va PASS | 230Vac-60Hz-40%
STEP.717(UUT Test seq.717) : Input Output Accuracy Multi or Single_S3(230Va PASS | 230Vac-60Hz-30%
STEP.718(UUT Test seq.718) : Input Output Accuracy Multi or Single_S3(230Va PASS | 230Vac-60Hz-20%
STEP.719(UUT Test seq.719) : Input Output Accuracy Multi or Single_S3(230Va PASS | 230Vac-60Hz-10%
STEP.720(UUT Test seq.720) : Input Output Accuracy Multi or Single_S3(240Va PASS | 240Vac-60Hz-100%
STEP.721(UUT Test seq.721) : Input Output Accuracy Multi or Single_S3(240Va PASS | 240Vac-60Hz-90%
STEP.722(UUT Test seq.722) : Input Output Accuracy Multi or Single_S3(240Va PASS | 240Vac-60Hz-80%
STEP.723(UUT Test seq.723) : Input Output Accuracy Multi or Single_S3(240Va PASS | 240Vac-60Hz-70%
STEP.724(UUT Test seq.724) : Input Output Accuracy Multi or Single_S3(240Va PASS | 240Vac-60Hz-60%
STEP.725(UUT Test seq.725) : Input Output Accuracy Multi or Single_S3(240Va PASS | 240Vac-60Hz-50%
STEP.726(UUT Test seq.726) : Input Output Accuracy Multi or Single_S3(240Va PASS | 240Vac-60Hz-40%
STEP.727(UUT Test seq.727) : Input Output Accuracy Multi or Single_S3(240Va PASS | 240Vac-60Hz-30%
STEP.728(UUT Test seq.728) : Input Output Accuracy Multi or Single_S3(240Va PASS | 240Vac-60Hz-20%
STEP.729(UUT Test seq.729) : Input Output Accuracy Multi or Single_S3(240Va PASS | 240Vac-60Hz-10%
STEP.730(UUT Test seq.730) : Input Output Accuracy Multi or Single_S3(100Va PASS | 100Vac-60Hz-100%
STEP.731(UUT Test seq.731) : Harmonic Multi UUT_Test_S2 ---- (2'137) ------ PASS
STEP.732(UUT Test seq.732) : Input Output Accuracy Multi or Single_S3(100Va PASS | 100Vac-60Hz-90%
STEP.733(UUT Test seq.733) : Harmonic Multi UUT_Test_S2 ---- (2'122) ------ PASS
STEP.734(UUT Test seq.734) : Input Output Accuracy Multi or Single_S3(100Va PASS | 100Vac-60Hz-80%
STEP.735(UUT Test seq.735) : Harmonic Multi UUT_Test_S2 ---- (2'122) ------ PASS
STEP.736(UUT Test seq.736) : Input Output Accuracy Multi or Single_S3(100Va PASS | 100Vac-60Hz-70%
STEP.737(UUT Test seq.737) : Harmonic Multi UUT_Test_S2 ---- (2'137) ------ PASS
STEP.738(UUT Test seq.738) : Input Output Accuracy Multi or Single_S3(100Va PASS | 100Vac-60Hz-60%
STEP.739(UUT Test seq.739) : Harmonic Multi UUT_Test_S2 ---- (2'138) ------ PASS
STEP.740(UUT Test seq.740) : Input Output Accuracy Multi or Single_S3(100Va PASS | 100Vac-60Hz-50%
STEP.741(UUT Test seq.741) : Harmonic Multi UUT_Test_S2 ---- (2'137) ------ PASS
STEP.742(UUT Test seq.742) : Input Output Accuracy Multi or Single_S3(100Va PASS | 100Vac-60Hz-40%
STEP.743(UUT Test seq.743) : Harmonic Multi UUT_Test_S2 ---- (2'138) ------ PASS
STEP.744(UUT Test seq.744) : Input Output Accuracy Multi or Single_S3(100Va PASS | 100Vac-60Hz-30%
STEP.745(UUT Test seq.745) : Harmonic Multi UUT_Test_S2 ---- (2'277) ------ PASS
STEP.746(UUT Test seq.746) : Input Output Accuracy Multi or Single_S3(100Va PASS | 100Vac-60Hz-20%
STEP.747(UUT Test seq.747) : Harmonic Multi UUT_Test_S2 ---- (2'168) ------ PASS
STEP.748(UUT Test seq.748) : Input Output Accuracy Multi or Single_S3(100Va PASS | 100Vac-60Hz-10%
STEP.749(UUT Test seq.749) : Harmonic Multi UUT_Test_S2 ---- (2'137) ------ PASS
STEP.750(UUT Test seq.750) : 61512 Ac Source ACDC Mode_Multi_S2 ---- (0'219 PASS
STEP.751(UUT Test seq.751) : AC Source ON/OFF(input source)_Multi_S2 ---- ( PASS
STEP.752(UUT Test seq.752) : Set Input Condition_Load_S4 ---- (0'016) ----- PASS
STEP.753(UUT Test seq.753) : Set Drop Time ---- (0'000) ------------------- PASS
STEP.754(UUT Test seq.754) : AC_DC Line Sag Surge 80611N-2_Multi_S2(DropOut PASS | DropOut H_164Vdc - 10ms
STEP.755(UUT Test seq.755) : I2C Read Status Multi_S6(DropOut H_164Vdc - 10 PASS | DropOut H_164Vdc - 10ms
STEP.756(UUT Test seq.756) : AC_DC Line Sag Surge 80611N-2_Multi_S2(DropOut PASS | DropOut H_164Vdc - 10ms
STEP.757(UUT Test seq.757) : I2C Read Status Multi_S6(DropOut H_164Vdc - 10 PASS | DropOut H_164Vdc - 10ms
STEP.758(UUT Test seq.758) : AC_DC Line Sag Surge 80611N-2_Multi_S2(DropOut PASS | DropOut H_164Vdc - 10ms
STEP.759(UUT Test seq.759) : I2C Read Status Multi_S6(DropOut H_164Vdc - 10 PASS | DropOut H_164Vdc - 10ms
STEP.760(UUT Test seq.760) : AC_DC Line Sag Surge 80611N-2_Multi_S2(DropOut PASS | DropOut H_164Vdc - 10ms
STEP.761(UUT Test seq.761) : I2C Read Status Multi_S6(DropOut H_164Vdc - 10 PASS | DropOut H_164Vdc - 10ms
STEP.762(UUT Test seq.762) : AC_DC Line Sag Surge 80611N-2_Multi_S2(DropOut PASS | DropOut H_164Vdc - 10ms
STEP.763(UUT Test seq.763) : I2C Read Status Multi_S6(DropOut H_164Vdc - 10 PASS | DropOut H_164Vdc - 10ms
STEP.764(UUT Test seq.764) : AC_DC Line Sag Surge 80611N-2_Multi_S2(DropOut PASS | DropOut H_164Vdc - 10ms
STEP.765(UUT Test seq.765) : I2C Read Status Multi_S6(DropOut H_164Vdc - 10 PASS | DropOut H_164Vdc - 10ms
STEP.766(UUT Test seq.766) : AC_DC Line Sag Surge 80611N-2_Multi_S2(DropOut PASS | DropOut H_164Vdc - 10ms
STEP.767(UUT Test seq.767) : I2C Read Status Multi_S6(DropOut H_164Vdc - 10 PASS | DropOut H_164Vdc - 10ms
STEP.768(UUT Test seq.768) : AC_DC Line Sag Surge 80611N-2_Multi_S2(DropOut PASS | DropOut H_164Vdc - 10ms
STEP.769(UUT Test seq.769) : I2C Read Status Multi_S6(DropOut H_164Vdc - 10 PASS | DropOut H_164Vdc - 10ms
STEP.770(UUT Test seq.770) : AC_DC Line Sag Surge 80611N-2_Multi_S2(DropOut PASS | DropOut H_164Vdc - 10ms
STEP.771(UUT Test seq.771) : I2C Read Status Multi_S6(DropOut H_164Vdc - 10 PASS | DropOut H_164Vdc - 10ms
STEP.772(UUT Test seq.772) : AC_DC Line Sag Surge 80611N-2_Multi_S2(DropOut PASS | DropOut H_164Vdc - 10ms
STEP.773(UUT Test seq.773) : I2C Read Status Multi_S6(DropOut H_164Vdc - 10 PASS | DropOut H_164Vdc - 10ms
STEP.774(UUT Test seq.774) : AC Source ON/OFF(input source)_Multi_S2 ---- ( PASS
STEP.775(UUT Test seq.775) : Input Output Accuracy Multi or Single_S3(240Vd PASS | 240Vdc-100%
STEP.776(UUT Test seq.776) : Input Output Accuracy Multi or Single_S3(240Vd PASS | 240Vdc-50%
STEP.777(UUT Test seq.777) : Input Output Accuracy Multi or Single_S3(240Vd FAIL | 240Vdc-20%
STEP.778(UUT Test seq.778) : Input Output Accuracy Multi or Single_S3(240Vd PASS | 240Vdc-10%
STEP.779(UUT Test seq.779) : AC Source ON/OFF(input source)_Multi_S2 ---- ( PASS
STEP.780(UUT Test seq.780) : Set Input Condition_Load_S4 ---- (0'015) ----- PASS
STEP.781(UUT Test seq.781) : Set Drop Time ---- (0'000) ------------------- PASS
STEP.782(UUT Test seq.782) : AC_DC Line Sag Surge 80611N-2_Multi_S2(DropOut PASS | DropOut H_200Vdc - 10ms
STEP.783(UUT Test seq.783) : I2C Read Status Multi_S6(DropOut H_200Vdc - 10 PASS | DropOut H_200Vdc - 10ms
STEP.784(UUT Test seq.784) : AC_DC Line Sag Surge 80611N-2_Multi_S2(DropOut PASS | DropOut H_200Vdc - 10ms
STEP.785(UUT Test seq.785) : I2C Read Status Multi_S6(DropOut H_200Vdc - 10 PASS | DropOut H_200Vdc - 10ms
STEP.786(UUT Test seq.786) : AC_DC Line Sag Surge 80611N-2_Multi_S2(DropOut PASS | DropOut H_200Vdc - 10ms
STEP.787(UUT Test seq.787) : I2C Read Status Multi_S6(DropOut H_200Vdc - 10 PASS | DropOut H_200Vdc - 10ms
STEP.788(UUT Test seq.788) : AC_DC Line Sag Surge 80611N-2_Multi_S2(DropOut PASS | DropOut H_200Vdc - 10ms
STEP.789(UUT Test seq.789) : I2C Read Status Multi_S6(DropOut H_200Vdc - 10 PASS | DropOut H_200Vdc - 10ms
STEP.790(UUT Test seq.790) : AC_DC Line Sag Surge 80611N-2_Multi_S2(DropOut PASS | DropOut H_200Vdc - 10ms
STEP.791(UUT Test seq.791) : I2C Read Status Multi_S6(DropOut H_200Vdc - 10 PASS | DropOut H_200Vdc - 10ms
STEP.792(UUT Test seq.792) : AC_DC Line Sag Surge 80611N-2_Multi_S2(DropOut PASS | DropOut H_200Vdc - 10ms
STEP.793(UUT Test seq.793) : I2C Read Status Multi_S6(DropOut H_200Vdc - 10 PASS | DropOut H_200Vdc - 10ms
STEP.794(UUT Test seq.794) : AC_DC Line Sag Surge 80611N-2_Multi_S2(DropOut PASS | DropOut H_200Vdc - 10ms
STEP.795(UUT Test seq.795) : I2C Read Status Multi_S6(DropOut H_200Vdc - 10 PASS | DropOut H_200Vdc - 10ms
STEP.796(UUT Test seq.796) : AC_DC Line Sag Surge 80611N-2_Multi_S2(DropOut PASS | DropOut H_200Vdc - 10ms
STEP.797(UUT Test seq.797) : I2C Read Status Multi_S6(DropOut H_200Vdc - 10 PASS | DropOut H_200Vdc - 10ms
STEP.798(UUT Test seq.798) : AC_DC Line Sag Surge 80611N-2_Multi_S2(DropOut PASS | DropOut H_200Vdc - 10ms
STEP.799(UUT Test seq.799) : I2C Read Status Multi_S6(DropOut H_200Vdc - 10 PASS | DropOut H_200Vdc - 10ms
STEP.800(UUT Test seq.800) : AC_DC Line Sag Surge 80611N-2_Multi_S2(DropOut PASS | DropOut H_200Vdc - 10ms
STEP.801(UUT Test seq.801) : I2C Read Status Multi_S6(DropOut H_200Vdc - 10 PASS | DropOut H_200Vdc - 10ms
STEP.802(UUT Test seq.802) : AC Source ON/OFF(input source)_Multi_S2 ---- ( PASS
STEP.803(UUT Test seq.803) : Set Input Condition_Load_S4 ---- (0'016) ----- PASS
STEP.804(UUT Test seq.804) : Set Drop Time ---- (0'000) ------------------- PASS
STEP.805(UUT Test seq.805) : AC_DC Line Sag Surge 80611N-2_Multi_S2(DropOut PASS | DropOut H_220Vdc - 10ms
STEP.806(UUT Test seq.806) : I2C Read Status Multi_S6(DropOut H_220Vdc - 10 PASS | DropOut H_220Vdc - 10ms
STEP.807(UUT Test seq.807) : AC_DC Line Sag Surge 80611N-2_Multi_S2(DropOut PASS | DropOut H_220Vdc - 10ms
STEP.808(UUT Test seq.808) : I2C Read Status Multi_S6(DropOut H_220Vdc - 10 PASS | DropOut H_220Vdc - 10ms
STEP.809(UUT Test seq.809) : AC_DC Line Sag Surge 80611N-2_Multi_S2(DropOut PASS | DropOut H_220Vdc - 10ms
STEP.810(UUT Test seq.810) : I2C Read Status Multi_S6(DropOut H_220Vdc - 10 PASS | DropOut H_220Vdc - 10ms
STEP.811(UUT Test seq.811) : AC_DC Line Sag Surge 80611N-2_Multi_S2(DropOut PASS | DropOut H_220Vdc - 10ms
STEP.812(UUT Test seq.812) : I2C Read Status Multi_S6(DropOut H_220Vdc - 10 PASS | DropOut H_220Vdc - 10ms
STEP.813(UUT Test seq.813) : AC_DC Line Sag Surge 80611N-2_Multi_S2(DropOut PASS | DropOut H_220Vdc - 10ms
STEP.814(UUT Test seq.814) : I2C Read Status Multi_S6(DropOut H_220Vdc - 10 PASS | DropOut H_220Vdc - 10ms
STEP.815(UUT Test seq.815) : AC_DC Line Sag Surge 80611N-2_Multi_S2(DropOut PASS | DropOut H_220Vdc - 10ms
STEP.816(UUT Test seq.816) : I2C Read Status Multi_S6(DropOut H_220Vdc - 10 PASS | DropOut H_220Vdc - 10ms
STEP.817(UUT Test seq.817) : AC_DC Line Sag Surge 80611N-2_Multi_S2(DropOut PASS | DropOut H_220Vdc - 10ms
STEP.818(UUT Test seq.818) : I2C Read Status Multi_S6(DropOut H_220Vdc - 10 PASS | DropOut H_220Vdc - 10ms
STEP.819(UUT Test seq.819) : AC_DC Line Sag Surge 80611N-2_Multi_S2(DropOut PASS | DropOut H_220Vdc - 10ms
STEP.820(UUT Test seq.820) : I2C Read Status Multi_S6(DropOut H_220Vdc - 10 PASS | DropOut H_220Vdc - 10ms
STEP.821(UUT Test seq.821) : AC_DC Line Sag Surge 80611N-2_Multi_S2(DropOut PASS | DropOut H_220Vdc - 10ms
STEP.822(UUT Test seq.822) : I2C Read Status Multi_S6(DropOut H_220Vdc - 10 PASS | DropOut H_220Vdc - 10ms
STEP.823(UUT Test seq.823) : AC_DC Line Sag Surge 80611N-2_Multi_S2(DropOut PASS | DropOut H_220Vdc - 10ms
STEP.824(UUT Test seq.824) : I2C Read Status Multi_S6(DropOut H_220Vdc - 10 PASS | DropOut H_220Vdc - 10ms
STEP.825(UUT Test seq.825) : AC Source ON/OFF(input source)_Multi_S2 ---- ( PASS
STEP.826(UUT Test seq.826) : Set Input Condition_Load_S4 ---- (0'015) ----- PASS
STEP.827(UUT Test seq.827) : Set Drop Time ---- (0'000) ------------------- PASS
STEP.828(UUT Test seq.828) : AC_DC Line Sag Surge 80611N-2_Multi_S2(DropOut PASS | DropOut H_300Vdc - 10ms
STEP.829(UUT Test seq.829) : I2C Read Status Multi_S6(DropOut H_300Vdc - 10 PASS | DropOut H_300Vdc - 10ms
STEP.830(UUT Test seq.830) : AC_DC Line Sag Surge 80611N-2_Multi_S2(DropOut PASS | DropOut H_300Vdc - 10ms
STEP.831(UUT Test seq.831) : I2C Read Status Multi_S6(DropOut H_300Vdc - 10 PASS | DropOut H_300Vdc - 10ms
STEP.832(UUT Test seq.832) : AC_DC Line Sag Surge 80611N-2_Multi_S2(DropOut PASS | DropOut H_300Vdc - 10ms
STEP.833(UUT Test seq.833) : I2C Read Status Multi_S6(DropOut H_300Vdc - 10 PASS | DropOut H_300Vdc - 10ms
STEP.834(UUT Test seq.834) : AC_DC Line Sag Surge 80611N-2_Multi_S2(DropOut PASS | DropOut H_300Vdc - 10ms
STEP.835(UUT Test seq.835) : I2C Read Status Multi_S6(DropOut H_300Vdc - 10 PASS | DropOut H_300Vdc - 10ms
STEP.836(UUT Test seq.836) : AC_DC Line Sag Surge 80611N-2_Multi_S2(DropOut PASS | DropOut H_300Vdc - 10ms
STEP.837(UUT Test seq.837) : I2C Read Status Multi_S6(DropOut H_300Vdc - 10 PASS | DropOut H_300Vdc - 10ms
STEP.838(UUT Test seq.838) : AC_DC Line Sag Surge 80611N-2_Multi_S2(DropOut PASS | DropOut H_300Vdc - 10ms
STEP.839(UUT Test seq.839) : I2C Read Status Multi_S6(DropOut H_300Vdc - 10 PASS | DropOut H_300Vdc - 10ms
STEP.840(UUT Test seq.840) : AC_DC Line Sag Surge 80611N-2_Multi_S2(DropOut PASS | DropOut H_300Vdc - 10ms
STEP.841(UUT Test seq.841) : I2C Read Status Multi_S6(DropOut H_300Vdc - 10 PASS | DropOut H_300Vdc - 10ms
STEP.842(UUT Test seq.842) : AC_DC Line Sag Surge 80611N-2_Multi_S2(DropOut PASS | DropOut H_300Vdc - 10ms
STEP.843(UUT Test seq.843) : I2C Read Status Multi_S6(DropOut H_300Vdc - 10 PASS | DropOut H_300Vdc - 10ms
STEP.844(UUT Test seq.844) : AC_DC Line Sag Surge 80611N-2_Multi_S2(DropOut PASS | DropOut H_300Vdc - 10ms
STEP.845(UUT Test seq.845) : I2C Read Status Multi_S6(DropOut H_300Vdc - 10 PASS | DropOut H_300Vdc - 10ms
STEP.846(UUT Test seq.846) : AC_DC Line Sag Surge 80611N-2_Multi_S2(DropOut PASS | DropOut H_300Vdc - 10ms
STEP.847(UUT Test seq.847) : I2C Read Status Multi_S6(DropOut H_300Vdc - 10 PASS | DropOut H_300Vdc - 10ms
STEP.848(UUT Test seq.848) : SUB20-Relay ---- (0'514) --------------------- PASS
STEP.849(UUT Test seq.849) : UUT Off_Multi_S2 ---- (1'076) ---------------- PASS
STEP.850(UUT Test seq.850) : 61512 Ac Source ACDC Mode_Multi_S2 ---- (0'171 PASS

## All
Switch Mode Power Supply
Testing Report
Test Program Name : R2k0AX17p-IV01-ATS5_Multi_Single_20230503_1
Serial No : 0505C55T01S68 System Time : 2023/05/05 11:00:57 AM
Model Name : 2000W Elapsed Time : 00:29:43
LOT Number : Environment :
Order Number : Inspector : root
Customer : Test Result : FAIL
(Pre Test seq.1) : Set Pre Load_or_UUT ---- (0'000)
(The Report Format of this Sequence was not found)
STEP.1(UUT Test seq.1) : Read UUT Total Number ---- (0'000) --------------- PASS
STEP.2(UUT Test seq.2) : PA 66202 Set_Multi ---- (0'078) ------------------ PASS
(The Report Format of this Sequence was not found)
STEP.3(UUT Test seq.3) : 34970_Set ---- (0'000) --------------------------- PASS
STEP.4(UUT Test seq.4) : SUB20-Relay ---- (0'500) ------------------------- PASS
Relay State 1: 05
Relay State 2: 05
Relay Change State Delay Time(ms): 500
STEP.5(UUT Test seq.5) : Read UUT Total Number ---- (0'016) --------------- PASS
STEP.6(UUT Test seq.6) : 61512 Ac Source ACDC Mode_Multi_S2 ---- (0'171) -- PASS
(The Report Format of this Sequence was not found)
STEP.7(UUT Test seq.7) : TTL & Relay Setup ---- (0'453) ------------------- PASS
(The Report Format of this Sequence was not found)
STEP.8(UUT Test seq.8) : Turn On Timing Test_Multi or Single(264V_63Hz_HH) PASS
ElaspedTime (S)= 2'028
Vin (V)= 264.00
Fin (Hz)= 63.00
On Phase Delay(ms)= 90.00
UUT Off Time (s)= 0.00
Trigger: 1:TTL1R, 2:TTL2R, 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:TTL1F, 9:TTL2F,10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1.00
2 1.00
3 1.00
4 1.00
Load Loading Start End VcmpA VcmpB
Name (A/Ohm/V) Trigger Trigger (V) (V)
------------- ---------- ------- ------- ------- -------
12V 161.500 8 5 11.590 12.810
12Vsb 2.500 8 5 11.400 12.600
PWOK 0.000 8 5 2.600 3.460
Vin_Good 0.000 8 1 2.600 3.460
SMBAlert 0.000 8 1 2.600 3.460
Load Ton Ton Ton
Name Max Min (ms)
------------- -------- -------- ---------
12V 3000.00 1.00 1047.66
12Vsb 1500.00 1.00 802.18
PWOK ******** ******** 1253.40
Vin_Good ******** ******** 0.06
SMBAlert ******** ******** 0.06
Load Ref Load Td Td Td
Name No. Max Min (ms)
------------- ------------- -------- -------- ---------
12V 3 -500.00 -100.00 -205.74
12Vsb 1 -1500.00 -50.00 -245.48
PWOK 1 500.00 100.00 205.74
Vin_Good 0 ******** ******** 0.06
SMBAlert 0 ******** ******** 0.06
STEP.9(UUT Test seq.9) : SUB20-Relay ---- (0'515) ------------------------- PASS
Relay State 1: 45
Relay State 2: 45
Relay Change State Delay Time(ms): 500
STEP.10(UUT Test seq.10) : Pre I2C Multi Set ---- (0'000) ----------------- PASS
(The Report Format of this Sequence was not found)
STEP.11(UUT Test seq.11) : I2C Read Status Multi_S6(264V_63Hz_HH) ---- (0'1 PASS
Adderss :B0
Command Page00 :060200
Command Page01 :060201
Status Word :79
Status Byte :78
Status VOUT :7A
Status IOUT :7B
Status INPUT :7C
Status TEMPERATURE :7D
Status CML :7E
Status FANS :81
---------------------------------
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
----------------------------------
Word_Page_00 : 0
Word_Page_01 : 0
Status_Byte_P00 : 0
Status_Byte_P01 : 0
Status_VOUT_P00 : 0
Status_VOUT_P01 : 0
Status_IOUT_P00 : 0
Status_IOUT_P01 : 0
Status_INPUT_P00 : 0
Status_INPUT_P01 : 0
Status_TEM_P00 : 0
Status_TEM_P01 : 0
Status_CML_P00 : 0
Status_CML_P01 : 0
Status_FANS_P00 : 0
Status_FANS_P01 : 0
STEP.12(UUT Test seq.12) : FW Version Check Multi_S7 ---- (0'359) --------- FAIL
Cheak Primary FW Version: 23954
Cheak Primary FW Version: *******
Cheak Primary FW Version: *******
Cheak Primary FW Version: *******
Cheak Primary FW Version: *******
Cheak Primary FW Version: *******
Cheak Primary FW Version: *******
Cheak Primary FW Version: *******
Cheak Second FW Version: 61039
Cheak Second FW Version: *******
Cheak Second FW Version: *******
Cheak Second FW Version: *******
Cheak Second FW Version: *******
Cheak Second FW Version: *******
Cheak Second FW Version: *******
Cheak Second FW Version: *******
--------------------------------------
Pri FW Version: 9377
Sec FW Version: 10032
STEP.13(UUT Test seq.13) : Hold Up Timing Test_Multi or Single(264V_63Hz_70 PASS
ElapsedTime (S)= 0'748
Vin (V)= 264.00
Fin (Hz)= 63.00
Delay Time (ms)= 0.00
On Phase Delay(ms)= 90.00
UUT Off Time (s)= 0.00
Trigger: 1:Trig1R(AC), 2:Trig2R(PS on), 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:Trig1F(AC), 9:Trig2F(PS on),10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1
2 1
3 1
4 1
Load Loading Start End VcmpA VcmpB
Name (A/Ohm/V) Trigger Trigger (V) (V)
------------- ---------- ------- ------- ------- -------
12V 113.050 8 12 11.590 12.810
12Vsb 1.750 8 12 11.400 12.600
PWOK 0.000 8 12 2.600 3.460
Vin_Good 0.000 8 12 2.600 3.460
SMBAlert 0.000 8 1 2.600 3.460
Load Tholdup Tholdup Tholdup
Name Max Min (ms)
------------- -------- -------- ---------
12V 1000.00 10.00 21.96
12Vsb 1000.00 70.00 78.99
PWOK 300.00 9.00 20.35
Vin_Good 4.00 0.01 2.78
SMBAlert ******** ******** 0.06
Load Ref Load Tholdup Tholdup Tholdup
Name No. Max Min (ms)
------------- ---------- -------- -------- ---------
12V 3 100.00 1.00 1.62
12Vsb 0 ******** ******** 78.99
PWOK 1 -100.00 -1.00 -1.62
Vin_Good 0 ******** ******** 2.78
SMBAlert 0 ******** ******** 0.06
STEP.14(UUT Test seq.14) : FAN Full Speed delay time Multi ---- (10'093) -- PASS
STEP.15(UUT Test seq.15) : FAN Speed Normal_Multi ---- (0'093) ------------ PASS
(The Report Format of this Sequence was not found)
STEP.16(UUT Test seq.16) : Pause Message(Add Cap Laod) ---- (23'291) ------ PASS
STEP.17(UUT Test seq.17) : TTL & Relay Setup(Add Cap Laod) ---- (0'702) --- PASS
(The Report Format of this Sequence was not found)
STEP.18(UUT Test seq.18) : Turn On Timing Test_Multi or Single(90V_47Hz_LL) PASS
ElaspedTime (S)= 2'215
Vin (V)= 90.00
Fin (Hz)= 47.00
On Phase Delay(ms)= 90.00
UUT Off Time (s)= 0.00
Trigger: 1:TTL1R, 2:TTL2R, 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:TTL1F, 9:TTL2F,10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1.00
2 1.00
3 1.00
4 1.00
Load Loading Start End VcmpA VcmpB
Name (A/Ohm/V) Trigger Trigger (V) (V)
------------- ---------- ------- ------- ------- -------
12V 1.000 8 5 11.590 12.810
12Vsb 0.100 8 5 11.400 12.600
PWOK 0.000 8 5 2.600 3.460
Vin_Good 0.000 8 1 2.600 3.460
SMBAlert 0.000 8 1 2.600 3.460
Load Ton Ton Ton
Name Max Min (ms)
------------- -------- -------- ---------
12V 3000.00 1.00 1480.94
12Vsb 1500.00 1.00 1236.31
PWOK ******** ******** 1686.96
Vin_Good ******** ******** 0.06
SMBAlert ******** ******** 0.06
Load Ref Load Td Td Td
Name No. Max Min (ms)
------------- ------------- -------- -------- ---------
12V 3 -500.00 -100.00 -206.02
12Vsb 1 -1500.00 -50.00 -244.63
PWOK 1 500.00 100.00 206.02
Vin_Good 0 ******** ******** 0.06
SMBAlert 0 ******** ******** 0.06
STEP.19(UUT Test seq.19) : PS OFF Time 80611(90V_47Hz_LL) ---- (2'496) ---- PASS
Vin (V)= Refer to the previous item
Fin (Hz)= Refer to the previous item
On Phase Delay(ms)= Refer to the previous item
UUT Off Time (s)= Refer to the previous item
Loading (A/Ohm/V)= Refer to the previous item
Trigger: 1:Trig1R(AC), 2:Trig2R(PS on), 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:Trig1F(AC), 9:Trig2F(PS on),10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1
2 1
3 1
4 1
Load Start End VcmpA VcmpB
Name Trigger Trigger (V) (V)
------------- ------- ------- ------- -------
12V 2 12 11.590 12.810
12Vsb 2 2 11.400 12.600
PWOK 2 12 2.600 2.600
Vin_Good 2 2 2.600 2.600
SMBAlert 2 2 2.600 2.600
Load Ton Ton Ton
Name Max Min (ms)
------------- -------- -------- ---------
12V ******** ******** 21.91
12Vsb ******** ******** --------
PWOK 50.00 0.01 0.72
Vin_Good ******** ******** --------
SMBAlert ******** ******** --------
Load Ref Load Td Td Td
Name No. Max Min (ms)
------------- ---------- -------- -------- ---------
12V 3 100.00 1.00 21.19
12Vsb 0 ******** ******** --------
PWOK 1 -100.00 -1.00 -21.19
Vin_Good 0 ******** ******** --------
SMBAlert 0 ******** ******** --------
STEP.20(UUT Test seq.20) : PS ON Delay time 80611(90V_47Hz_LL) ---- (0'889) PASS
Vin (V)= Refer to the previous item
Fin (Hz)= Refer to the previous item
On Phase Delay(ms)= Refer to the previous item
UUT Off Time (s)= Refer to the previous item
Loading (A/Ohm/V)= Refer to the previous item
Trigger: 1:Trig1R(AC), 2:Trig2R(PS on), 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:Trig1F(AC), 9:Trig2F(PS on),10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1
2 1
3 1
4 1
Load Start End VcmpA VcmpB
Name Trigger Trigger (V) (V)
------------- ------- ------- ------- -------
12V 9 5 11.590 12.810
12Vsb 9 9 11.400 12.600
PWOK 9 5 2.600 2.600
Vin_Good 9 9 2.600 2.600
SMBAlert 9 9 2.600 2.600
Load Ton Ton Ton
Name Max Min (ms)
------------- -------- -------- ---------
12V 400.00 5.00 62.14
12Vsb ******** ******** 0.12
PWOK ******** ******** 268.19
Vin_Good ******** ******** 0.12
SMBAlert ******** ******** 0.12
Load Ref Load Td Td Td
Name No. Max Min (ms)
------------- ---------- -------- -------- ---------
12V 3 -500.000 -100.000 -206.051
12Vsb 0 ********* ********* 0.123
PWOK 1 500.000 100.000 206.051
Vin_Good 0 ********* ********* 0.123
SMBAlert 0 ********* ********* 0.122
STEP.21(UUT Test seq.21) : Turn On Timing Test_Multi or Single(90V_47Hz_LL_ PASS
ElaspedTime (S)= 1'982
Vin (V)= 90.00
Fin (Hz)= 47.00
On Phase Delay(ms)= 90.00
UUT Off Time (s)= 0.50
Trigger: 1:TTL1R, 2:TTL2R, 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:TTL1F, 9:TTL2F,10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1.00
2 1.00
3 1.00
4 1.00
Load Loading Start End VcmpA VcmpB
Name (A/Ohm/V) Trigger Trigger (V) (V)
------------- ---------- ------- ------- ------- -------
12V 1.000 5 6 1.220 11.590
12Vsb 0.100 5 6 1.200 10.800
PWOK 0.000 8 1 2.600 3.460
Vin_Good 0.000 8 1 2.600 3.460
SMBAlert 0.000 8 1 2.600 3.460
Load Ton Ton Ton
Name Max Min (ms)
------------- -------- -------- ---------
12V 70.00 5.00 51.27
12Vsb 70.00 1.00 12.90
PWOK ******** ******** 0.06
Vin_Good ******** ******** 0.06
SMBAlert ******** ******** 0.06
Load Ref Load Td Td Td
Name No. Max Min (ms)
------------- ------------- -------- -------- ---------
12V 0 ******** ******** 51.27
12Vsb 0 ******** ******** 12.90
PWOK 0 ******** ******** 0.06
Vin_Good 0 ******** ******** 0.06
SMBAlert 0 ******** ******** 0.06
STEP.22(UUT Test seq.22) : TTL & Relay Setup ---- (0'000) ----------------- PASS
(The Report Format of this Sequence was not found)
STEP.23(UUT Test seq.23) : PS ON Delay time 80611(90V_47Hz_LL_Tpson_12V_Ris PASS
Vin (V)= Refer to the previous item
Fin (Hz)= Refer to the previous item
On Phase Delay(ms)= Refer to the previous item
UUT Off Time (s)= Refer to the previous item
Loading (A/Ohm/V)= Refer to the previous item
Trigger: 1:Trig1R(AC), 2:Trig2R(PS on), 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:Trig1F(AC), 9:Trig2F(PS on),10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1
2 1
3 1
4 1
Load Start End VcmpA VcmpB
Name Trigger Trigger (V) (V)
------------- ------- ------- ------- -------
12V 5 6 1.220 11.590
12Vsb 9 9 1.200 10.800
PWOK 9 9 2.600 2.600
Vin_Good 9 9 2.600 2.600
SMBAlert 9 9 2.600 2.600
Load Ton Ton Ton
Name Max Min (ms)
------------- -------- -------- ---------
12V 70.00 5.00 51.30
12Vsb ******** ******** 0.12
PWOK ******** ******** 0.12
Vin_Good ******** ******** 0.12
SMBAlert ******** ******** 0.12
Load Ref Load Td Td Td
Name No. Max Min (ms)
------------- ---------- -------- -------- ---------
12V 0 ********* ********* 51.300
12Vsb 0 ********* ********* 0.120
PWOK 0 ********* ********* 0.120
Vin_Good 0 ********* ********* 0.120
SMBAlert 0 ********* ********* 0.120
STEP.24(UUT Test seq.24) : Hold Up Timing Test_Multi or Single(90V_47Hz_LL) PASS
ElapsedTime (S)= 0'702
Vin (V)= 90.00
Fin (Hz)= 47.00
Delay Time (ms)= 0.00
On Phase Delay(ms)= 90.00
UUT Off Time (s)= 0.00
Trigger: 1:Trig1R(AC), 2:Trig2R(PS on), 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:Trig1F(AC), 9:Trig2F(PS on),10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1
2 1
3 1
4 1
Load Loading Start End VcmpA VcmpB
Name (A/Ohm/V) Trigger Trigger (V) (V)
------------- ---------- ------- ------- ------- -------
12V 1.000 8 12 11.590 12.810
12Vsb 0.100 8 12 11.400 12.600
PWOK 0.000 8 12 2.600 3.460
Vin_Good 0.000 8 12 2.600 3.460
SMBAlert 0.000 8 1 2.600 3.460
Load Tholdup Tholdup Tholdup
Name Max Min (ms)
------------- -------- -------- ---------
12V 1000.00 10.00 64.00
12Vsb 1000.00 70.00 91.77
PWOK 300.00 9.00 42.87
Vin_Good 4.00 0.01 2.57
SMBAlert ******** ******** 0.06
Load Ref Load Tholdup Tholdup Tholdup
Name No. Max Min (ms)
------------- ---------- -------- -------- ---------
12V 3 100.00 1.00 21.13
12Vsb 0 ******** ******** 91.77
PWOK 1 -100.00 -1.00 -21.13
Vin_Good 0 ******** ******** 2.57
SMBAlert 0 ******** ******** 0.06
STEP.25(UUT Test seq.25) : FAN Full Speed delay time Multi ---- (8'081) --- PASS
STEP.26(UUT Test seq.26) : FAN Speed Normal_Multi ---- (0'109) ------------ PASS
(The Report Format of this Sequence was not found)
STEP.27(UUT Test seq.27) : Turn On Timing Test_Multi or Single(90V_47Hz_HH) PASS
ElaspedTime (S)= 2'199
Vin (V)= 90.00
Fin (Hz)= 47.00
On Phase Delay(ms)= 90.00
UUT Off Time (s)= 0.00
Trigger: 1:TTL1R, 2:TTL2R, 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:TTL1F, 9:TTL2F,10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1.00
2 1.00
3 1.00
4 1.00
Load Loading Start End VcmpA VcmpB
Name (A/Ohm/V) Trigger Trigger (V) (V)
------------- ---------- ------- ------- ------- -------
12V 71.300 8 5 11.590 12.810
12Vsb 2.500 8 5 11.400 12.600
PWOK 0.000 8 5 2.600 3.460
Vin_Good 0.000 8 1 2.600 3.460
SMBAlert 0.000 8 1 2.600 3.460
Load Ton Ton Ton
Name Max Min (ms)
------------- -------- -------- ---------
12V 3000.00 1.00 1374.46
12Vsb 1500.00 1.00 1129.26
PWOK ******** ******** 1580.22
Vin_Good ******** ******** 0.06
SMBAlert ******** ******** 0.06
Load Ref Load Td Td Td
Name No. Max Min (ms)
------------- ------------- -------- -------- ---------
12V 3 -500.00 -100.00 -205.76
12Vsb 1 -1500.00 -50.00 -245.20
PWOK 1 500.00 100.00 205.76
Vin_Good 0 ******** ******** 0.06
SMBAlert 0 ******** ******** 0.06
STEP.28(UUT Test seq.28) : PS OFF Time 80611(90V_47Hz_HH) ---- (2'465) ---- PASS
Vin (V)= Refer to the previous item
Fin (Hz)= Refer to the previous item
On Phase Delay(ms)= Refer to the previous item
UUT Off Time (s)= Refer to the previous item
Loading (A/Ohm/V)= Refer to the previous item
Trigger: 1:Trig1R(AC), 2:Trig2R(PS on), 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:Trig1F(AC), 9:Trig2F(PS on),10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1
2 1
3 1
4 1
Load Start End VcmpA VcmpB
Name Trigger Trigger (V) (V)
------------- ------- ------- ------- -------
12V 2 12 11.590 12.810
12Vsb 2 2 11.400 12.600
PWOK 2 12 2.600 2.600
Vin_Good 2 2 2.600 2.600
SMBAlert 2 2 2.600 2.600
Load Ton Ton Ton
Name Max Min (ms)
------------- -------- -------- ---------
12V ******** ******** 2.63
12Vsb ******** ******** --------
PWOK 50.00 0.01 0.78
Vin_Good ******** ******** --------
SMBAlert ******** ******** --------
Load Ref Load Td Td Td
Name No. Max Min (ms)
------------- ---------- -------- -------- ---------
12V 3 100.00 1.00 1.85
12Vsb 0 ******** ******** --------
PWOK 1 -100.00 -1.00 -1.85
Vin_Good 0 ******** ******** --------
SMBAlert 0 ******** ******** --------
STEP.29(UUT Test seq.29) : PS ON Delay time 80611(90V_47Hz_HH) ---- (0'889) PASS
Vin (V)= Refer to the previous item
Fin (Hz)= Refer to the previous item
On Phase Delay(ms)= Refer to the previous item
UUT Off Time (s)= Refer to the previous item
Loading (A/Ohm/V)= Refer to the previous item
Trigger: 1:Trig1R(AC), 2:Trig2R(PS on), 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:Trig1F(AC), 9:Trig2F(PS on),10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1
2 1
3 1
4 1
Load Start End VcmpA VcmpB
Name Trigger Trigger (V) (V)
------------- ------- ------- ------- -------
12V 9 5 11.590 12.810
12Vsb 9 9 11.400 12.600
PWOK 9 5 2.600 2.600
Vin_Good 9 9 2.600 2.600
SMBAlert 9 9 2.600 2.600
Load Ton Ton Ton
Name Max Min (ms)
------------- -------- -------- ---------
12V 400.00 5.00 62.33
12Vsb ******** ******** 0.12
PWOK ******** ******** 268.00
Vin_Good ******** ******** 0.12
SMBAlert ******** ******** 0.12
Load Ref Load Td Td Td
Name No. Max Min (ms)
------------- ---------- -------- -------- ---------
12V 3 -500.000 -100.000 -205.676
12Vsb 0 ********* ********* 0.123
PWOK 1 500.000 100.000 205.676
Vin_Good 0 ********* ********* 0.123
SMBAlert 0 ********* ********* 0.123
STEP.30(UUT Test seq.30) : Turn On Timing Test_Multi or Single(90V_47Hz_HH_ PASS
ElaspedTime (S)= 2'043
Vin (V)= 90.00
Fin (Hz)= 47.00
On Phase Delay(ms)= 90.00
UUT Off Time (s)= 0.50
Trigger: 1:TTL1R, 2:TTL2R, 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:TTL1F, 9:TTL2F,10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1.00
2 1.00
3 1.00
4 1.00
Load Loading Start End VcmpA VcmpB
Name (A/Ohm/V) Trigger Trigger (V) (V)
------------- ---------- ------- ------- ------- -------
12V 71.300 5 6 1.220 11.590
12Vsb 2.500 5 6 1.200 10.800
PWOK 0.000 8 1 2.600 3.460
Vin_Good 0.000 8 1 2.600 3.460
SMBAlert 0.000 8 1 2.600 3.460
Load Ton Ton Ton
Name Max Min (ms)
------------- -------- -------- ---------
12V 70.00 5.00 51.30
12Vsb 70.00 1.00 11.97
PWOK ******** ******** 0.06
Vin_Good ******** ******** 0.06
SMBAlert ******** ******** 0.06
Load Ref Load Td Td Td
Name No. Max Min (ms)
------------- ------------- -------- -------- ---------
12V 0 ******** ******** 51.30
12Vsb 0 ******** ******** 11.97
PWOK 0 ******** ******** 0.06
Vin_Good 0 ******** ******** 0.06
SMBAlert 0 ******** ******** 0.06
STEP.31(UUT Test seq.31) : TTL & Relay Setup ---- (0'000) ----------------- PASS
(The Report Format of this Sequence was not found)
STEP.32(UUT Test seq.32) : PS ON Delay time 80611(90V_47Hz_HH_Tpson_12V_Ris PASS
Vin (V)= Refer to the previous item
Fin (Hz)= Refer to the previous item
On Phase Delay(ms)= Refer to the previous item
UUT Off Time (s)= Refer to the previous item
Loading (A/Ohm/V)= Refer to the previous item
Trigger: 1:Trig1R(AC), 2:Trig2R(PS on), 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:Trig1F(AC), 9:Trig2F(PS on),10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1
2 1
3 1
4 1
Load Start End VcmpA VcmpB
Name Trigger Trigger (V) (V)
------------- ------- ------- ------- -------
12V 5 6 1.220 11.590
12Vsb 9 9 1.200 10.800
PWOK 9 9 2.600 2.600
Vin_Good 9 9 2.600 2.600
SMBAlert 9 9 2.600 2.600
Load Ton Ton Ton
Name Max Min (ms)
------------- -------- -------- ---------
12V 70.00 5.00 51.29
12Vsb ******** ******** 0.11
PWOK ******** ******** 0.11
Vin_Good ******** ******** 0.11
SMBAlert ******** ******** 0.11
Load Ref Load Td Td Td
Name No. Max Min (ms)
------------- ---------- -------- -------- ---------
12V 0 ********* ********* 51.293
12Vsb 0 ********* ********* 0.110
PWOK 0 ********* ********* 0.109
Vin_Good 0 ********* ********* 0.109
SMBAlert 0 ********* ********* 0.110
STEP.33(UUT Test seq.33) : Hold Up Timing Test_Multi or Single(90V_47Hz_70% PASS
ElapsedTime (S)= 0'718
Vin (V)= 90.00
Fin (Hz)= 47.00
Delay Time (ms)= 0.00
On Phase Delay(ms)= 90.00
UUT Off Time (s)= 0.00
Trigger: 1:Trig1R(AC), 2:Trig2R(PS on), 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:Trig1F(AC), 9:Trig2F(PS on),10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1
2 1
3 1
4 1
Load Loading Start End VcmpA VcmpB
Name (A/Ohm/V) Trigger Trigger (V) (V)
------------- ---------- ------- ------- ------- -------
12V 49.910 8 12 11.590 12.810
12Vsb 1.750 8 12 11.400 12.600
PWOK 0.000 8 12 2.600 3.460
Vin_Good 0.000 8 12 2.600 3.460
SMBAlert 0.000 8 1 2.600 3.460
Load Tholdup Tholdup Tholdup
Name Max Min (ms)
------------- -------- -------- ---------
12V 1000.00 10.00 36.76
12Vsb 1000.00 70.00 78.90
PWOK 300.00 9.00 34.85
Vin_Good 4.00 0.01 2.74
SMBAlert ******** ******** 0.06
Load Ref Load Tholdup Tholdup Tholdup
Name No. Max Min (ms)
------------- ---------- -------- -------- ---------
12V 3 100.00 1.00 1.91
12Vsb 0 ******** ******** 78.90
PWOK 1 -100.00 -1.00 -1.91
Vin_Good 0 ******** ******** 2.74
SMBAlert 0 ******** ******** 0.06
STEP.34(UUT Test seq.34) : FAN Full Speed delay time Multi ---- (8'112) --- PASS
STEP.35(UUT Test seq.35) : FAN Speed Normal_Multi ---- (0'093) ------------ PASS
(The Report Format of this Sequence was not found)
STEP.36(UUT Test seq.36) : Turn On Timing Test_Multi or Single(100V_60Hz_HH PASS
ElaspedTime (S)= 2'028
Vin (V)= 100.00
Fin (Hz)= 60.00
On Phase Delay(ms)= 90.00
UUT Off Time (s)= 0.00
Trigger: 1:TTL1R, 2:TTL2R, 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:TTL1F, 9:TTL2F,10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1.00
2 1.00
3 1.00
4 1.00
Load Loading Start End VcmpA VcmpB
Name (A/Ohm/V) Trigger Trigger (V) (V)
------------- ---------- ------- ------- ------- -------
12V 79.500 8 5 11.590 12.810
12Vsb 2.500 8 5 11.400 12.600
PWOK 0.000 8 5 2.600 3.460
Vin_Good 0.000 8 1 2.600 3.460
SMBAlert 0.000 8 1 2.600 3.460
Load Ton Ton Ton
Name Max Min (ms)
------------- -------- -------- ---------
12V 3000.00 1.00 1281.22
12Vsb 1500.00 1.00 1036.03
PWOK ******** ******** 1486.93
Vin_Good ******** ******** 0.06
SMBAlert ******** ******** 0.06
Load Ref Load Td Td Td
Name No. Max Min (ms)
------------- ------------- -------- -------- ---------
12V 3 -500.00 -100.00 -205.71
12Vsb 1 -1500.00 -50.00 -245.19
PWOK 1 500.00 100.00 205.71
Vin_Good 0 ******** ******** 0.06
SMBAlert 0 ******** ******** 0.06
STEP.37(UUT Test seq.37) : PS OFF Time 80611(100V_60Hz_HH) ---- (2'496) --- PASS
Vin (V)= Refer to the previous item
Fin (Hz)= Refer to the previous item
On Phase Delay(ms)= Refer to the previous item
UUT Off Time (s)= Refer to the previous item
Loading (A/Ohm/V)= Refer to the previous item
Trigger: 1:Trig1R(AC), 2:Trig2R(PS on), 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:Trig1F(AC), 9:Trig2F(PS on),10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1
2 1
3 1
4 1
Load Start End VcmpA VcmpB
Name Trigger Trigger (V) (V)
------------- ------- ------- ------- -------
12V 2 12 11.590 12.810
12Vsb 2 2 11.400 12.600
PWOK 2 12 2.600 2.600
Vin_Good 2 2 2.600 2.600
SMBAlert 2 2 2.600 2.600
Load Ton Ton Ton
Name Max Min (ms)
------------- -------- -------- ---------
12V ******** ******** 2.48
12Vsb ******** ******** --------
PWOK 50.00 0.01 0.66
Vin_Good ******** ******** --------
SMBAlert ******** ******** --------
Load Ref Load Td Td Td
Name No. Max Min (ms)
------------- ---------- -------- -------- ---------
12V 3 100.00 1.00 1.82
12Vsb 0 ******** ******** --------
PWOK 1 -100.00 -1.00 -1.82
Vin_Good 0 ******** ******** --------
SMBAlert 0 ******** ******** --------
STEP.38(UUT Test seq.38) : PS ON Delay time 80611(100V_60Hz_HH) ---- (0'843 PASS
Vin (V)= Refer to the previous item
Fin (Hz)= Refer to the previous item
On Phase Delay(ms)= Refer to the previous item
UUT Off Time (s)= Refer to the previous item
Loading (A/Ohm/V)= Refer to the previous item
Trigger: 1:Trig1R(AC), 2:Trig2R(PS on), 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:Trig1F(AC), 9:Trig2F(PS on),10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1
2 1
3 1
4 1
Load Start End VcmpA VcmpB
Name Trigger Trigger (V) (V)
------------- ------- ------- ------- -------
12V 9 5 11.590 12.810
12Vsb 9 9 11.400 12.600
PWOK 9 5 2.600 2.600
Vin_Good 9 9 2.600 2.600
SMBAlert 9 9 2.600 2.600
Load Ton Ton Ton
Name Max Min (ms)
------------- -------- -------- ---------
12V 400.00 5.00 62.41
12Vsb ******** ******** 0.12
PWOK ******** ******** 268.16
Vin_Good ******** ******** 0.12
SMBAlert ******** ******** 0.12
Load Ref Load Td Td Td
Name No. Max Min (ms)
------------- ---------- -------- -------- ---------
12V 3 -500.000 -100.000 -205.750
12Vsb 0 ********* ********* 0.116
PWOK 1 500.000 100.000 205.750
Vin_Good 0 ********* ********* 0.115
SMBAlert 0 ********* ********* 0.116
STEP.39(UUT Test seq.39) : Turn On Timing Test_Multi or Single(100V_60Hz_HH PASS
ElaspedTime (S)= 2'012
Vin (V)= 100.00
Fin (Hz)= 60.00
On Phase Delay(ms)= 90.00
UUT Off Time (s)= 0.50
Trigger: 1:TTL1R, 2:TTL2R, 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:TTL1F, 9:TTL2F,10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1.00
2 1.00
3 1.00
4 1.00
Load Loading Start End VcmpA VcmpB
Name (A/Ohm/V) Trigger Trigger (V) (V)
------------- ---------- ------- ------- ------- -------
12V 79.500 5 6 1.220 11.590
12Vsb 2.500 5 6 1.200 10.800
PWOK 0.000 8 1 2.600 3.460
Vin_Good 0.000 8 1 2.600 3.460
SMBAlert 0.000 8 1 2.600 3.460
Load Ton Ton Ton
Name Max Min (ms)
------------- -------- -------- ---------
12V 70.00 5.00 51.27
12Vsb 70.00 1.00 11.97
PWOK ******** ******** 0.06
Vin_Good ******** ******** 0.06
SMBAlert ******** ******** 0.06
Load Ref Load Td Td Td
Name No. Max Min (ms)
------------- ------------- -------- -------- ---------
12V 0 ******** ******** 51.27
12Vsb 0 ******** ******** 11.97
PWOK 0 ******** ******** 0.06
Vin_Good 0 ******** ******** 0.06
SMBAlert 0 ******** ******** 0.06
STEP.40(UUT Test seq.40) : TTL & Relay Setup ---- (0'000) ----------------- PASS
(The Report Format of this Sequence was not found)
STEP.41(UUT Test seq.41) : PS ON Delay time 80611(100V_60Hz_HH_Tpson_12V_Ri PASS
Vin (V)= Refer to the previous item
Fin (Hz)= Refer to the previous item
On Phase Delay(ms)= Refer to the previous item
UUT Off Time (s)= Refer to the previous item
Loading (A/Ohm/V)= Refer to the previous item
Trigger: 1:Trig1R(AC), 2:Trig2R(PS on), 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:Trig1F(AC), 9:Trig2F(PS on),10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1
2 1
3 1
4 1
Load Start End VcmpA VcmpB
Name Trigger Trigger (V) (V)
------------- ------- ------- ------- -------
12V 5 6 1.220 11.590
12Vsb 9 9 1.200 10.800
PWOK 9 9 2.600 2.600
Vin_Good 9 9 2.600 2.600
SMBAlert 9 9 2.600 2.600
Load Ton Ton Ton
Name Max Min (ms)
------------- -------- -------- ---------
12V 70.00 5.00 51.25
12Vsb ******** ******** 0.12
PWOK ******** ******** 0.12
Vin_Good ******** ******** 0.12
SMBAlert ******** ******** 0.12
Load Ref Load Td Td Td
Name No. Max Min (ms)
------------- ---------- -------- -------- ---------
12V 0 ********* ********* 51.254
12Vsb 0 ********* ********* 0.124
PWOK 0 ********* ********* 0.124
Vin_Good 0 ********* ********* 0.124
SMBAlert 0 ********* ********* 0.124
STEP.42(UUT Test seq.42) : Hold Up Timing Test_Multi or Single(100V_60Hz_70 PASS
ElapsedTime (S)= 0'717
Vin (V)= 100.00
Fin (Hz)= 60.00
Delay Time (ms)= 0.00
On Phase Delay(ms)= 90.00
UUT Off Time (s)= 0.00
Trigger: 1:Trig1R(AC), 2:Trig2R(PS on), 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:Trig1F(AC), 9:Trig2F(PS on),10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1
2 1
3 1
4 1
Load Loading Start End VcmpA VcmpB
Name (A/Ohm/V) Trigger Trigger (V) (V)
------------- ---------- ------- ------- ------- -------
12V 55.650 8 12 11.590 12.810
12Vsb 1.750 8 12 11.400 12.600
PWOK 0.000 8 12 2.600 3.460
Vin_Good 0.000 8 12 2.600 3.460
SMBAlert 0.000 8 1 2.600 3.460
Load Tholdup Tholdup Tholdup
Name Max Min (ms)
------------- -------- -------- ---------
12V 1000.00 10.00 33.43
12Vsb 1000.00 70.00 78.98
PWOK 300.00 9.00 31.53
Vin_Good 4.00 0.01 2.60
SMBAlert ******** ******** 0.06
Load Ref Load Tholdup Tholdup Tholdup
Name No. Max Min (ms)
------------- ---------- -------- -------- ---------
12V 3 100.00 1.00 1.90
12Vsb 0 ******** ******** 78.98
PWOK 1 -100.00 -1.00 -1.90
Vin_Good 0 ******** ******** 2.60
SMBAlert 0 ******** ******** 0.06
STEP.43(UUT Test seq.43) : FAN Full Speed delay time Multi ---- (8'096) --- PASS
STEP.44(UUT Test seq.44) : FAN Speed Normal_Multi ---- (0'094) ------------ PASS
(The Report Format of this Sequence was not found)
STEP.45(UUT Test seq.45) : Turn On Timing Test_Multi or Single(180V_47Hz_HH PASS
ElaspedTime (S)= 1'934
Vin (V)= 180.00
Fin (Hz)= 47.00
On Phase Delay(ms)= 90.00
UUT Off Time (s)= 0.00
Trigger: 1:TTL1R, 2:TTL2R, 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:TTL1F, 9:TTL2F,10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1.00
2 1.00
3 1.00
4 1.00
Load Loading Start End VcmpA VcmpB
Name (A/Ohm/V) Trigger Trigger (V) (V)
------------- ---------- ------- ------- ------- -------
12V 128.700 8 5 11.590 12.810
12Vsb 2.500 8 5 11.400 12.600
PWOK 0.000 8 5 2.600 3.460
Vin_Good 0.000 8 1 2.600 3.460
SMBAlert 0.000 8 1 2.600 3.460
Load Ton Ton Ton
Name Max Min (ms)
------------- -------- -------- ---------
12V 3000.00 1.00 1118.21
12Vsb 1500.00 1.00 872.88
PWOK ******** ******** 1323.76
Vin_Good ******** ******** 0.06
SMBAlert ******** ******** 0.06
Load Ref Load Td Td Td
Name No. Max Min (ms)
------------- ------------- -------- -------- ---------
12V 3 -500.00 -100.00 -205.55
12Vsb 1 -1500.00 -50.00 -245.33
PWOK 1 500.00 100.00 205.55
Vin_Good 0 ******** ******** 0.06
SMBAlert 0 ******** ******** 0.06
STEP.46(UUT Test seq.46) : PS OFF Time 80611(180V_47Hz_HH) ---- (2'450) --- PASS
Vin (V)= Refer to the previous item
Fin (Hz)= Refer to the previous item
On Phase Delay(ms)= Refer to the previous item
UUT Off Time (s)= Refer to the previous item
Loading (A/Ohm/V)= Refer to the previous item
Trigger: 1:Trig1R(AC), 2:Trig2R(PS on), 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:Trig1F(AC), 9:Trig2F(PS on),10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1
2 1
3 1
4 1
Load Start End VcmpA VcmpB
Name Trigger Trigger (V) (V)
------------- ------- ------- ------- -------
12V 2 12 11.590 12.810
12Vsb 2 2 11.400 12.600
PWOK 2 12 2.600 2.600
Vin_Good 2 2 2.600 2.600
SMBAlert 2 2 2.600 2.600
Load Ton Ton Ton
Name Max Min (ms)
------------- -------- -------- ---------
12V ******** ******** 2.50
12Vsb ******** ******** --------
PWOK 50.00 0.01 0.77
Vin_Good ******** ******** --------
SMBAlert ******** ******** --------
Load Ref Load Td Td Td
Name No. Max Min (ms)
------------- ---------- -------- -------- ---------
12V 3 100.00 1.00 1.73
12Vsb 0 ******** ******** --------
PWOK 1 -100.00 -1.00 -1.73
Vin_Good 0 ******** ******** --------
SMBAlert 0 ******** ******** --------
STEP.47(UUT Test seq.47) : PS ON Delay time 80611(180V_47Hz_HH) ---- (0'983 PASS
Vin (V)= Refer to the previous item
Fin (Hz)= Refer to the previous item
On Phase Delay(ms)= Refer to the previous item
UUT Off Time (s)= Refer to the previous item
Loading (A/Ohm/V)= Refer to the previous item
Trigger: 1:Trig1R(AC), 2:Trig2R(PS on), 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:Trig1F(AC), 9:Trig2F(PS on),10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1
2 1
3 1
4 1
Load Start End VcmpA VcmpB
Name Trigger Trigger (V) (V)
------------- ------- ------- ------- -------
12V 9 5 11.590 12.810
12Vsb 9 9 11.400 12.600
PWOK 9 5 2.600 2.600
Vin_Good 9 9 2.600 2.600
SMBAlert 9 9 2.600 2.600
Load Ton Ton Ton
Name Max Min (ms)
------------- -------- -------- ---------
12V 400.00 5.00 62.64
12Vsb ******** ******** 0.13
PWOK ******** ******** 268.34
Vin_Good ******** ******** 0.13
SMBAlert ******** ******** 0.13
Load Ref Load Td Td Td
Name No. Max Min (ms)
------------- ---------- -------- -------- ---------
12V 3 -500.000 -100.000 -205.695
12Vsb 0 ********* ********* 0.132
PWOK 1 500.000 100.000 205.695
Vin_Good 0 ********* ********* 0.132
SMBAlert 0 ********* ********* 0.132
STEP.48(UUT Test seq.48) : Turn On Timing Test_Multi or Single(180V_47Hz_HH PASS
ElaspedTime (S)= 2'231
Vin (V)= 180.00
Fin (Hz)= 47.00
On Phase Delay(ms)= 90.00
UUT Off Time (s)= 0.50
Trigger: 1:TTL1R, 2:TTL2R, 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:TTL1F, 9:TTL2F,10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1.00
2 1.00
3 1.00
4 1.00
Load Loading Start End VcmpA VcmpB
Name (A/Ohm/V) Trigger Trigger (V) (V)
------------- ---------- ------- ------- ------- -------
12V 128.700 5 6 1.220 11.590
12Vsb 2.500 5 6 1.200 10.800
PWOK 0.000 8 1 2.600 3.460
Vin_Good 0.000 8 1 2.600 3.460
SMBAlert 0.000 8 1 2.600 3.460
Load Ton Ton Ton
Name Max Min (ms)
------------- -------- -------- ---------
12V 70.00 5.00 51.28
12Vsb 70.00 1.00 11.94
PWOK ******** ******** 0.06
Vin_Good ******** ******** 0.06
SMBAlert ******** ******** 0.06
Load Ref Load Td Td Td
Name No. Max Min (ms)
------------- ------------- -------- -------- ---------
12V 0 ******** ******** 51.28
12Vsb 0 ******** ******** 11.94
PWOK 0 ******** ******** 0.06
Vin_Good 0 ******** ******** 0.06
SMBAlert 0 ******** ******** 0.06
STEP.49(UUT Test seq.49) : TTL & Relay Setup ---- (0'000) ----------------- PASS
(The Report Format of this Sequence was not found)
STEP.50(UUT Test seq.50) : PS ON Delay time 80611(180V_47Hz_HH_Tpson_12V_Ri PASS
Vin (V)= Refer to the previous item
Fin (Hz)= Refer to the previous item
On Phase Delay(ms)= Refer to the previous item
UUT Off Time (s)= Refer to the previous item
Loading (A/Ohm/V)= Refer to the previous item
Trigger: 1:Trig1R(AC), 2:Trig2R(PS on), 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:Trig1F(AC), 9:Trig2F(PS on),10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1
2 1
3 1
4 1
Load Start End VcmpA VcmpB
Name Trigger Trigger (V) (V)
------------- ------- ------- ------- -------
12V 5 6 1.220 11.590
12Vsb 9 9 1.200 10.800
PWOK 9 9 2.600 2.600
Vin_Good 9 9 2.600 2.600
SMBAlert 9 9 2.600 2.600
Load Ton Ton Ton
Name Max Min (ms)
------------- -------- -------- ---------
12V 70.00 5.00 51.27
12Vsb ******** ******** 0.13
PWOK ******** ******** 0.13
Vin_Good ******** ******** 0.13
SMBAlert ******** ******** 0.13
Load Ref Load Td Td Td
Name No. Max Min (ms)
------------- ---------- -------- -------- ---------
12V 0 ********* ********* 51.271
12Vsb 0 ********* ********* 0.128
PWOK 0 ********* ********* 0.128
Vin_Good 0 ********* ********* 0.128
SMBAlert 0 ********* ********* 0.128
STEP.51(UUT Test seq.51) : Hold Up Timing Test_Multi or Single(180V_47Hz_70 PASS
ElapsedTime (S)= 0'687
Vin (V)= 180.00
Fin (Hz)= 47.00
Delay Time (ms)= 0.00
On Phase Delay(ms)= 90.00
UUT Off Time (s)= 0.00
Trigger: 1:Trig1R(AC), 2:Trig2R(PS on), 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:Trig1F(AC), 9:Trig2F(PS on),10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1
2 1
3 1
4 1
Load Loading Start End VcmpA VcmpB
Name (A/Ohm/V) Trigger Trigger (V) (V)
------------- ---------- ------- ------- ------- -------
12V 90.090 8 12 11.590 12.810
12Vsb 1.750 8 12 11.400 12.600
PWOK 0.000 8 12 2.600 3.460
Vin_Good 0.000 8 12 2.600 3.460
SMBAlert 0.000 8 1 2.600 3.460
Load Tholdup Tholdup Tholdup
Name Max Min (ms)
------------- -------- -------- ---------
12V 1000.00 10.00 26.83
12Vsb 1000.00 70.00 79.08
PWOK 300.00 9.00 25.04
Vin_Good 4.00 0.01 2.89
SMBAlert ******** ******** 0.06
Load Ref Load Tholdup Tholdup Tholdup
Name No. Max Min (ms)
------------- ---------- -------- -------- ---------
12V 3 100.00 1.00 1.79
12Vsb 0 ******** ******** 79.08
PWOK 1 -100.00 -1.00 -1.79
Vin_Good 0 ******** ******** 2.89
SMBAlert 0 ******** ******** 0.06
STEP.52(UUT Test seq.52) : FAN Full Speed delay time Multi ---- (8'112) --- PASS
STEP.53(UUT Test seq.53) : FAN Speed Normal_Multi ---- (0'078) ------------ PASS
(The Report Format of this Sequence was not found)
STEP.54(UUT Test seq.54) : Turn On Timing Test_Multi or Single(200V_50Hz_HH PASS
ElaspedTime (S)= 1'810
Vin (V)= 200.00
Fin (Hz)= 50.00
On Phase Delay(ms)= 90.00
UUT Off Time (s)= 0.00
Trigger: 1:TTL1R, 2:TTL2R, 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:TTL1F, 9:TTL2F,10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1.00
2 1.00
3 1.00
4 1.00
Load Loading Start End VcmpA VcmpB
Name (A/Ohm/V) Trigger Trigger (V) (V)
------------- ---------- ------- ------- ------- -------
12V 145.100 8 5 11.590 12.810
12Vsb 2.500 8 5 11.400 12.600
PWOK 0.000 8 5 2.600 3.460
Vin_Good 0.000 8 1 2.600 3.460
SMBAlert 0.000 8 1 2.600 3.460
Load Ton Ton Ton
Name Max Min (ms)
------------- -------- -------- ---------
12V 3000.00 1.00 1064.22
12Vsb 1500.00 1.00 818.65
PWOK ******** ******** 1269.78
Vin_Good ******** ******** 0.06
SMBAlert ******** ******** 0.06
Load Ref Load Td Td Td
Name No. Max Min (ms)
------------- ------------- -------- -------- ---------
12V 3 -500.00 -100.00 -205.56
12Vsb 1 -1500.00 -50.00 -245.57
PWOK 1 500.00 100.00 205.56
Vin_Good 0 ******** ******** 0.06
SMBAlert 0 ******** ******** 0.06
STEP.55(UUT Test seq.55) : PS OFF Time 80611(200V_50Hz_HH) ---- (2'464) --- PASS
Vin (V)= Refer to the previous item
Fin (Hz)= Refer to the previous item
On Phase Delay(ms)= Refer to the previous item
UUT Off Time (s)= Refer to the previous item
Loading (A/Ohm/V)= Refer to the previous item
Trigger: 1:Trig1R(AC), 2:Trig2R(PS on), 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:Trig1F(AC), 9:Trig2F(PS on),10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1
2 1
3 1
4 1
Load Start End VcmpA VcmpB
Name Trigger Trigger (V) (V)
------------- ------- ------- ------- -------
12V 2 12 11.590 12.810
12Vsb 2 2 11.400 12.600
PWOK 2 12 2.600 2.600
Vin_Good 2 2 2.600 2.600
SMBAlert 2 2 2.600 2.600
Load Ton Ton Ton
Name Max Min (ms)
------------- -------- -------- ---------
12V ******** ******** 2.38
12Vsb ******** ******** --------
PWOK 50.00 0.01 0.67
Vin_Good ******** ******** --------
SMBAlert ******** ******** --------
Load Ref Load Td Td Td
Name No. Max Min (ms)
------------- ---------- -------- -------- ---------
12V 3 100.00 1.00 1.71
12Vsb 0 ******** ******** --------
PWOK 1 -100.00 -1.00 -1.71
Vin_Good 0 ******** ******** --------
SMBAlert 0 ******** ******** --------
STEP.56(UUT Test seq.56) : PS ON Delay time 80611(200V_50Hz_HH) ---- (0'873 PASS
Vin (V)= Refer to the previous item
Fin (Hz)= Refer to the previous item
On Phase Delay(ms)= Refer to the previous item
UUT Off Time (s)= Refer to the previous item
Loading (A/Ohm/V)= Refer to the previous item
Trigger: 1:Trig1R(AC), 2:Trig2R(PS on), 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:Trig1F(AC), 9:Trig2F(PS on),10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1
2 1
3 1
4 1
Load Start End VcmpA VcmpB
Name Trigger Trigger (V) (V)
------------- ------- ------- ------- -------
12V 9 5 11.590 12.810
12Vsb 9 9 11.400 12.600
PWOK 9 5 2.600 2.600
Vin_Good 9 9 2.600 2.600
SMBAlert 9 9 2.600 2.600
Load Ton Ton Ton
Name Max Min (ms)
------------- -------- -------- ---------
12V 400.00 5.00 62.58
12Vsb ******** ******** 0.13
PWOK ******** ******** 268.14
Vin_Good ******** ******** 0.13
SMBAlert ******** ******** 0.13
Load Ref Load Td Td Td
Name No. Max Min (ms)
------------- ---------- -------- -------- ---------
12V 3 -500.000 -100.000 -205.561
12Vsb 0 ********* ********* 0.130
PWOK 1 500.000 100.000 205.561
Vin_Good 0 ********* ********* 0.130
SMBAlert 0 ********* ********* 0.130
STEP.57(UUT Test seq.57) : Turn On Timing Test_Multi or Single(200V_50Hz_HH PASS
ElaspedTime (S)= 2'012
Vin (V)= 200.00
Fin (Hz)= 50.00
On Phase Delay(ms)= 90.00
UUT Off Time (s)= 0.50
Trigger: 1:TTL1R, 2:TTL2R, 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:TTL1F, 9:TTL2F,10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1.00
2 1.00
3 1.00
4 1.00
Load Loading Start End VcmpA VcmpB
Name (A/Ohm/V) Trigger Trigger (V) (V)
------------- ---------- ------- ------- ------- -------
12V 145.100 5 6 1.220 11.590
12Vsb 2.500 5 6 1.200 10.800
PWOK 0.000 8 1 2.600 3.460
Vin_Good 0.000 8 1 2.600 3.460
SMBAlert 0.000 8 1 2.600 3.460
Load Ton Ton Ton
Name Max Min (ms)
------------- -------- -------- ---------
12V 70.00 5.00 51.29
12Vsb 70.00 1.00 11.92
PWOK ******** ******** 0.06
Vin_Good ******** ******** 0.06
SMBAlert ******** ******** 0.06
Load Ref Load Td Td Td
Name No. Max Min (ms)
------------- ------------- -------- -------- ---------
12V 0 ******** ******** 51.29
12Vsb 0 ******** ******** 11.92
PWOK 0 ******** ******** 0.06
Vin_Good 0 ******** ******** 0.06
SMBAlert 0 ******** ******** 0.06
STEP.58(UUT Test seq.58) : TTL & Relay Setup ---- (0'000) ----------------- PASS
(The Report Format of this Sequence was not found)
STEP.59(UUT Test seq.59) : PS ON Delay time 80611(200V_50Hz_HH_Tpson_12V_Ri PASS
Vin (V)= Refer to the previous item
Fin (Hz)= Refer to the previous item
On Phase Delay(ms)= Refer to the previous item
UUT Off Time (s)= Refer to the previous item
Loading (A/Ohm/V)= Refer to the previous item
Trigger: 1:Trig1R(AC), 2:Trig2R(PS on), 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:Trig1F(AC), 9:Trig2F(PS on),10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1
2 1
3 1
4 1
Load Start End VcmpA VcmpB
Name Trigger Trigger (V) (V)
------------- ------- ------- ------- -------
12V 5 6 1.220 11.590
12Vsb 9 9 1.200 10.800
PWOK 9 9 2.600 2.600
Vin_Good 9 9 2.600 2.600
SMBAlert 9 9 2.600 2.600
Load Ton Ton Ton
Name Max Min (ms)
------------- -------- -------- ---------
12V 70.00 5.00 51.32
12Vsb ******** ******** 0.13
PWOK ******** ******** 0.13
Vin_Good ******** ******** 0.13
SMBAlert ******** ******** 0.13
Load Ref Load Td Td Td
Name No. Max Min (ms)
------------- ---------- -------- -------- ---------
12V 0 ********* ********* 51.318
12Vsb 0 ********* ********* 0.130
PWOK 0 ********* ********* 0.130
Vin_Good 0 ********* ********* 0.130
SMBAlert 0 ********* ********* 0.130
STEP.60(UUT Test seq.60) : Hold Up Timing Test_Multi or Single(200V_50Hz_70 PASS
ElapsedTime (S)= 0'702
Vin (V)= 200.00
Fin (Hz)= 50.00
Delay Time (ms)= 0.00
On Phase Delay(ms)= 90.00
UUT Off Time (s)= 0.00
Trigger: 1:Trig1R(AC), 2:Trig2R(PS on), 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:Trig1F(AC), 9:Trig2F(PS on),10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1
2 1
3 1
4 1
Load Loading Start End VcmpA VcmpB
Name (A/Ohm/V) Trigger Trigger (V) (V)
------------- ---------- ------- ------- ------- -------
12V 101.570 8 12 11.590 12.810
12Vsb 1.750 8 12 11.400 12.600
PWOK 0.000 8 12 2.600 3.460
Vin_Good 0.000 8 12 2.600 3.460
SMBAlert 0.000 8 1 2.600 3.460
Load Tholdup Tholdup Tholdup
Name Max Min (ms)
------------- -------- -------- ---------
12V 1000.00 10.00 24.15
12Vsb 1000.00 70.00 78.45
PWOK 300.00 9.00 22.43
Vin_Good 4.00 0.01 2.68
SMBAlert ******** ******** 0.06
Load Ref Load Tholdup Tholdup Tholdup
Name No. Max Min (ms)
------------- ---------- -------- -------- ---------
12V 3 100.00 1.00 1.72
12Vsb 0 ******** ******** 78.45
PWOK 1 -100.00 -1.00 -1.72
Vin_Good 0 ******** ******** 2.68
SMBAlert 0 ******** ******** 0.06
STEP.61(UUT Test seq.61) : FAN Full Speed delay time Multi ---- (8'097) --- PASS
STEP.62(UUT Test seq.62) : FAN Speed Normal_Multi ---- (0'078) ------------ PASS
(The Report Format of this Sequence was not found)
STEP.63(UUT Test seq.63) : Turn On Timing Test_Multi or Single(220V_50Hz_HH PASS
ElaspedTime (S)= 1'763
Vin (V)= 220.00
Fin (Hz)= 50.00
On Phase Delay(ms)= 90.00
UUT Off Time (s)= 0.00
Trigger: 1:TTL1R, 2:TTL2R, 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:TTL1F, 9:TTL2F,10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1.00
2 1.00
3 1.00
4 1.00
Load Loading Start End VcmpA VcmpB
Name (A/Ohm/V) Trigger Trigger (V) (V)
------------- ---------- ------- ------- ------- -------
12V 161.500 8 5 11.590 12.810
12Vsb 2.500 8 5 11.400 12.600
PWOK 0.000 8 5 2.600 3.460
Vin_Good 0.000 8 1 2.600 3.460
SMBAlert 0.000 8 1 2.600 3.460
Load Ton Ton Ton
Name Max Min (ms)
------------- -------- -------- ---------
12V 3000.00 1.00 1032.40
12Vsb 1500.00 1.00 786.78
PWOK ******** ******** 1237.86
Vin_Good ******** ******** 0.06
SMBAlert ******** ******** 0.06
Load Ref Load Td Td Td
Name No. Max Min (ms)
------------- ------------- -------- -------- ---------
12V 3 -500.00 -100.00 -205.46
12Vsb 1 -1500.00 -50.00 -245.62
PWOK 1 500.00 100.00 205.46
Vin_Good 0 ******** ******** 0.06
SMBAlert 0 ******** ******** 0.06
STEP.64(UUT Test seq.64) : PS OFF Time 80611(220V_50Hz_HH) ---- (2'511) --- PASS
Vin (V)= Refer to the previous item
Fin (Hz)= Refer to the previous item
On Phase Delay(ms)= Refer to the previous item
UUT Off Time (s)= Refer to the previous item
Loading (A/Ohm/V)= Refer to the previous item
Trigger: 1:Trig1R(AC), 2:Trig2R(PS on), 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:Trig1F(AC), 9:Trig2F(PS on),10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1
2 1
3 1
4 1
Load Start End VcmpA VcmpB
Name Trigger Trigger (V) (V)
------------- ------- ------- ------- -------
12V 2 12 11.590 12.810
12Vsb 2 2 11.400 12.600
PWOK 2 12 2.600 2.600
Vin_Good 2 2 2.600 2.600
SMBAlert 2 2 2.600 2.600
Load Ton Ton Ton
Name Max Min (ms)
------------- -------- -------- ---------
12V ******** ******** 2.41
12Vsb ******** ******** --------
PWOK 50.00 0.01 0.71
Vin_Good ******** ******** --------
SMBAlert ******** ******** --------
Load Ref Load Td Td Td
Name No. Max Min (ms)
------------- ---------- -------- -------- ---------
12V 3 100.00 1.00 1.70
12Vsb 0 ******** ******** --------
PWOK 1 -100.00 -1.00 -1.70
Vin_Good 0 ******** ******** --------
SMBAlert 0 ******** ******** --------
STEP.65(UUT Test seq.65) : PS ON Delay time 80611(220V_50Hz_HH) ---- (0'873 PASS
Vin (V)= Refer to the previous item
Fin (Hz)= Refer to the previous item
On Phase Delay(ms)= Refer to the previous item
UUT Off Time (s)= Refer to the previous item
Loading (A/Ohm/V)= Refer to the previous item
Trigger: 1:Trig1R(AC), 2:Trig2R(PS on), 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:Trig1F(AC), 9:Trig2F(PS on),10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1
2 1
3 1
4 1
Load Start End VcmpA VcmpB
Name Trigger Trigger (V) (V)
------------- ------- ------- ------- -------
12V 9 5 11.590 12.810
12Vsb 9 9 11.400 12.600
PWOK 9 5 2.600 2.600
Vin_Good 9 9 2.600 2.600
SMBAlert 9 9 2.600 2.600
Load Ton Ton Ton
Name Max Min (ms)
------------- -------- -------- ---------
12V 400.00 5.00 62.76
12Vsb ******** ******** 0.12
PWOK ******** ******** 268.20
Vin_Good ******** ******** 0.12
SMBAlert ******** ******** 0.12
Load Ref Load Td Td Td
Name No. Max Min (ms)
------------- ---------- -------- -------- ---------
12V 3 -500.000 -100.000 -205.439
12Vsb 0 ********* ********* 0.120
PWOK 1 500.000 100.000 205.439
Vin_Good 0 ********* ********* 0.120
SMBAlert 0 ********* ********* 0.120
STEP.66(UUT Test seq.66) : Turn On Timing Test_Multi or Single(220V_50Hz_HH PASS
ElaspedTime (S)= 2'137
Vin (V)= 220.00
Fin (Hz)= 50.00
On Phase Delay(ms)= 90.00
UUT Off Time (s)= 0.50
Trigger: 1:TTL1R, 2:TTL2R, 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:TTL1F, 9:TTL2F,10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1.00
2 1.00
3 1.00
4 1.00
Load Loading Start End VcmpA VcmpB
Name (A/Ohm/V) Trigger Trigger (V) (V)
------------- ---------- ------- ------- ------- -------
12V 161.500 5 6 1.220 11.590
12Vsb 2.500 5 6 1.200 10.800
PWOK 0.000 8 1 2.600 3.460
Vin_Good 0.000 8 1 2.600 3.460
SMBAlert 0.000 8 1 2.600 3.460
Load Ton Ton Ton
Name Max Min (ms)
------------- -------- -------- ---------
12V 70.00 5.00 51.29
12Vsb 70.00 1.00 11.90
PWOK ******** ******** 0.06
Vin_Good ******** ******** 0.06
SMBAlert ******** ******** 0.06
Load Ref Load Td Td Td
Name No. Max Min (ms)
------------- ------------- -------- -------- ---------
12V 0 ******** ******** 51.29
12Vsb 0 ******** ******** 11.90
PWOK 0 ******** ******** 0.06
Vin_Good 0 ******** ******** 0.06
SMBAlert 0 ******** ******** 0.06
STEP.67(UUT Test seq.67) : TTL & Relay Setup ---- (0'016) ----------------- PASS
(The Report Format of this Sequence was not found)
STEP.68(UUT Test seq.68) : PS ON Delay time 80611(220V_50Hz_HH_Tpson_12V_Ri PASS
Vin (V)= Refer to the previous item
Fin (Hz)= Refer to the previous item
On Phase Delay(ms)= Refer to the previous item
UUT Off Time (s)= Refer to the previous item
Loading (A/Ohm/V)= Refer to the previous item
Trigger: 1:Trig1R(AC), 2:Trig2R(PS on), 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:Trig1F(AC), 9:Trig2F(PS on),10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1
2 1
3 1
4 1
Load Start End VcmpA VcmpB
Name Trigger Trigger (V) (V)
------------- ------- ------- ------- -------
12V 5 6 1.220 11.590
12Vsb 9 9 1.200 10.800
PWOK 9 9 2.600 2.600
Vin_Good 9 9 2.600 2.600
SMBAlert 9 9 2.600 2.600
Load Ton Ton Ton
Name Max Min (ms)
------------- -------- -------- ---------
12V 70.00 5.00 51.30
12Vsb ******** ******** 0.13
PWOK ******** ******** 0.13
Vin_Good ******** ******** 0.13
SMBAlert ******** ******** 0.13
Load Ref Load Td Td Td
Name No. Max Min (ms)
------------- ---------- -------- -------- ---------
12V 0 ********* ********* 51.303
12Vsb 0 ********* ********* 0.131
PWOK 0 ********* ********* 0.131
Vin_Good 0 ********* ********* 0.131
SMBAlert 0 ********* ********* 0.131
STEP.69(UUT Test seq.69) : Hold Up Timing Test_Multi or Single(220V_50Hz_70 PASS
ElapsedTime (S)= 0'702
Vin (V)= 220.00
Fin (Hz)= 50.00
Delay Time (ms)= 0.00
On Phase Delay(ms)= 90.00
UUT Off Time (s)= 0.00
Trigger: 1:Trig1R(AC), 2:Trig2R(PS on), 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:Trig1F(AC), 9:Trig2F(PS on),10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1
2 1
3 1
4 1
Load Loading Start End VcmpA VcmpB
Name (A/Ohm/V) Trigger Trigger (V) (V)
------------- ---------- ------- ------- ------- -------
12V 113.050 8 12 11.590 12.810
12Vsb 1.750 8 12 11.400 12.600
PWOK 0.000 8 12 2.600 3.460
Vin_Good 0.000 8 12 2.600 3.460
SMBAlert 0.000 8 1 2.600 3.460
Load Tholdup Tholdup Tholdup
Name Max Min (ms)
------------- -------- -------- ---------
12V 1000.00 10.00 21.75
12Vsb 1000.00 70.00 78.34
PWOK 300.00 9.00 20.12
Vin_Good 4.00 0.01 2.76
SMBAlert ******** ******** 0.06
Load Ref Load Tholdup Tholdup Tholdup
Name No. Max Min (ms)
------------- ---------- -------- -------- ---------
12V 3 100.00 1.00 1.63
12Vsb 0 ******** ******** 78.34
PWOK 1 -100.00 -1.00 -1.63
Vin_Good 0 ******** ******** 2.76
SMBAlert 0 ******** ******** 0.06
STEP.70(UUT Test seq.70) : FAN Full Speed delay time Multi ---- (8'097) --- PASS
STEP.71(UUT Test seq.71) : FAN Speed Normal_Multi ---- (0'109) ------------ PASS
(The Report Format of this Sequence was not found)
STEP.72(UUT Test seq.72) : Turn On Timing Test_Multi or Single(264V_63Hz_LL PASS
ElaspedTime (S)= 2'902
Vin (V)= 264.00
Fin (Hz)= 63.00
On Phase Delay(ms)= 90.00
UUT Off Time (s)= 1.00
Trigger: 1:TTL1R, 2:TTL2R, 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:TTL1F, 9:TTL2F,10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1.00
2 1.00
3 1.00
4 1.00
Load Loading Start End VcmpA VcmpB
Name (A/Ohm/V) Trigger Trigger (V) (V)
------------- ---------- ------- ------- ------- -------
12V 1.000 8 5 11.590 12.810
12Vsb 0.100 8 5 11.400 12.600
PWOK 0.000 8 5 2.600 3.460
Vin_Good 0.000 8 1 2.600 3.460
SMBAlert 0.000 8 1 2.600 3.460
Load Ton Ton Ton
Name Max Min (ms)
------------- -------- -------- ---------
12V 3000.00 1.00 1005.77
12Vsb 1500.00 1.00 761.36
PWOK ******** ******** 1211.66
Vin_Good ******** ******** 0.06
SMBAlert ******** ******** 0.06
Load Ref Load Td Td Td
Name No. Max Min (ms)
------------- ------------- -------- -------- ---------
12V 3 -500.00 -100.00 -205.90
12Vsb 1 -1500.00 -50.00 -244.41
PWOK 1 500.00 100.00 205.90
Vin_Good 0 ******** ******** 0.06
SMBAlert 0 ******** ******** 0.06
STEP.73(UUT Test seq.73) : PS OFF Time 80611(264V_63Hz_LL) ---- (2'511) --- PASS
Vin (V)= Refer to the previous item
Fin (Hz)= Refer to the previous item
On Phase Delay(ms)= Refer to the previous item
UUT Off Time (s)= Refer to the previous item
Loading (A/Ohm/V)= Refer to the previous item
Trigger: 1:Trig1R(AC), 2:Trig2R(PS on), 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:Trig1F(AC), 9:Trig2F(PS on),10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1
2 1
3 1
4 1
Load Start End VcmpA VcmpB
Name Trigger Trigger (V) (V)
------------- ------- ------- ------- -------
12V 2 12 11.590 12.810
12Vsb 2 2 11.400 12.600
PWOK 2 12 2.600 2.600
Vin_Good 2 2 2.600 2.600
SMBAlert 2 2 2.600 2.600
Load Ton Ton Ton
Name Max Min (ms)
------------- -------- -------- ---------
12V ******** ******** 22.21
12Vsb ******** ******** --------
PWOK 50.00 0.01 0.69
Vin_Good ******** ******** --------
SMBAlert ******** ******** --------
Load Ref Load Td Td Td
Name No. Max Min (ms)
------------- ---------- -------- -------- ---------
12V 3 100.00 1.00 21.52
12Vsb 0 ******** ******** --------
PWOK 1 -100.00 -1.00 -21.52
Vin_Good 0 ******** ******** --------
SMBAlert 0 ******** ******** --------
STEP.74(UUT Test seq.74) : PS ON Delay time 80611(264V_63Hz_LL) ---- (0'873 PASS
Vin (V)= Refer to the previous item
Fin (Hz)= Refer to the previous item
On Phase Delay(ms)= Refer to the previous item
UUT Off Time (s)= Refer to the previous item
Loading (A/Ohm/V)= Refer to the previous item
Trigger: 1:Trig1R(AC), 2:Trig2R(PS on), 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:Trig1F(AC), 9:Trig2F(PS on),10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1
2 1
3 1
4 1
Load Start End VcmpA VcmpB
Name Trigger Trigger (V) (V)
------------- ------- ------- ------- -------
12V 9 5 11.590 12.810
12Vsb 9 9 11.400 12.600
PWOK 9 5 2.600 2.600
Vin_Good 9 9 2.600 2.600
SMBAlert 9 9 2.600 2.600
Load Ton Ton Ton
Name Max Min (ms)
------------- -------- -------- ---------
12V 400.00 5.00 62.15
12Vsb ******** ******** 0.12
PWOK ******** ******** 268.12
Vin_Good ******** ******** 0.12
SMBAlert ******** ******** 0.12
Load Ref Load Td Td Td
Name No. Max Min (ms)
------------- ---------- -------- -------- ---------
12V 3 -500.000 -100.000 -205.970
12Vsb 0 ********* ********* 0.122
PWOK 1 500.000 100.000 205.970
Vin_Good 0 ********* ********* 0.122
SMBAlert 0 ********* ********* 0.122
STEP.75(UUT Test seq.75) : Turn On Timing Test_Multi or Single(264V_63Hz_LL PASS
ElaspedTime (S)= 2'028
Vin (V)= 264.00
Fin (Hz)= 63.00
On Phase Delay(ms)= 90.00
UUT Off Time (s)= 0.50
Trigger: 1:TTL1R, 2:TTL2R, 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:TTL1F, 9:TTL2F,10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1.00
2 1.00
3 1.00
4 1.00
Load Loading Start End VcmpA VcmpB
Name (A/Ohm/V) Trigger Trigger (V) (V)
------------- ---------- ------- ------- ------- -------
12V 1.000 5 6 1.220 11.590
12Vsb 0.100 5 6 1.200 10.800
PWOK 0.000 8 1 2.600 3.460
Vin_Good 0.000 8 1 2.600 3.460
SMBAlert 0.000 8 1 2.600 3.460
Load Ton Ton Ton
Name Max Min (ms)
------------- -------- -------- ---------
12V 70.00 5.00 51.28
12Vsb 70.00 1.00 12.81
PWOK ******** ******** 0.06
Vin_Good ******** ******** 0.06
SMBAlert ******** ******** 0.06
Load Ref Load Td Td Td
Name No. Max Min (ms)
------------- ------------- -------- -------- ---------
12V 0 ******** ******** 51.28
12Vsb 0 ******** ******** 12.81
PWOK 0 ******** ******** 0.06
Vin_Good 0 ******** ******** 0.06
SMBAlert 0 ******** ******** 0.06
STEP.76(UUT Test seq.76) : TTL & Relay Setup ---- (0'000) ----------------- PASS
(The Report Format of this Sequence was not found)
STEP.77(UUT Test seq.77) : PS ON Delay time 80611(264V_63Hz_LL_Tpson_12V_Ri PASS
Vin (V)= Refer to the previous item
Fin (Hz)= Refer to the previous item
On Phase Delay(ms)= Refer to the previous item
UUT Off Time (s)= Refer to the previous item
Loading (A/Ohm/V)= Refer to the previous item
Trigger: 1:Trig1R(AC), 2:Trig2R(PS on), 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:Trig1F(AC), 9:Trig2F(PS on),10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1
2 1
3 1
4 1
Load Start End VcmpA VcmpB
Name Trigger Trigger (V) (V)
------------- ------- ------- ------- -------
12V 5 6 1.220 11.590
12Vsb 9 9 1.200 10.800
PWOK 9 9 2.600 2.600
Vin_Good 9 9 2.600 2.600
SMBAlert 9 9 2.600 2.600
Load Ton Ton Ton
Name Max Min (ms)
------------- -------- -------- ---------
12V 70.00 5.00 51.28
12Vsb ******** ******** 0.14
PWOK ******** ******** 0.14
Vin_Good ******** ******** 0.14
SMBAlert ******** ******** 0.14
Load Ref Load Td Td Td
Name No. Max Min (ms)
------------- ---------- -------- -------- ---------
12V 0 ********* ********* 51.277
12Vsb 0 ********* ********* 0.136
PWOK 0 ********* ********* 0.136
Vin_Good 0 ********* ********* 0.136
SMBAlert 0 ********* ********* 0.136
STEP.78(UUT Test seq.78) : Hold Up Timing Test_Multi or Single(264V_63Hz_LL PASS
ElapsedTime (S)= 0'687
Vin (V)= 264.00
Fin (Hz)= 63.00
Delay Time (ms)= 0.00
On Phase Delay(ms)= 90.00
UUT Off Time (s)= 0.00
Trigger: 1:Trig1R(AC), 2:Trig2R(PS on), 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:Trig1F(AC), 9:Trig2F(PS on),10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1
2 1
3 1
4 1
Load Loading Start End VcmpA VcmpB
Name (A/Ohm/V) Trigger Trigger (V) (V)
------------- ---------- ------- ------- ------- -------
12V 1.000 8 12 11.590 12.810
12Vsb 0.100 8 12 11.400 12.600
PWOK 0.000 8 12 2.600 3.460
Vin_Good 0.000 8 12 2.600 3.460
SMBAlert 0.000 8 1 2.600 3.460
Load Tholdup Tholdup Tholdup
Name Max Min (ms)
------------- -------- -------- ---------
12V 1000.00 10.00 64.28
12Vsb 1000.00 70.00 92.45
PWOK 300.00 9.00 42.94
Vin_Good 4.00 0.01 2.83
SMBAlert ******** ******** 0.06
Load Ref Load Tholdup Tholdup Tholdup
Name No. Max Min (ms)
------------- ---------- -------- -------- ---------
12V 3 100.00 1.00 21.35
12Vsb 0 ******** ******** 92.45
PWOK 1 -100.00 -1.00 -21.35
Vin_Good 0 ******** ******** 2.83
SMBAlert 0 ******** ******** 0.06
STEP.79(UUT Test seq.79) : FAN Full Speed delay time Multi ---- (8'097) --- PASS
STEP.80(UUT Test seq.80) : FAN Speed Normal_Multi ---- (0'093) ------------ PASS
(The Report Format of this Sequence was not found)
STEP.81(UUT Test seq.81) : Turn On Timing Test_Multi or Single(264V_63Hz_HH PASS
ElaspedTime (S)= 3'386
Vin (V)= 264.00
Fin (Hz)= 63.00
On Phase Delay(ms)= 90.00
UUT Off Time (s)= 1.00
Trigger: 1:TTL1R, 2:TTL2R, 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:TTL1F, 9:TTL2F,10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1.00
2 1.00
3 1.00
4 1.00
Load Loading Start End VcmpA VcmpB
Name (A/Ohm/V) Trigger Trigger (V) (V)
------------- ---------- ------- ------- ------- -------
12V 161.500 8 5 11.590 12.810
12Vsb 2.500 8 5 11.400 12.600
PWOK 0.000 8 5 2.600 3.460
Vin_Good 0.000 8 1 2.600 3.460
SMBAlert 0.000 8 1 2.600 3.460
Load Ton Ton Ton
Name Max Min (ms)
------------- -------- -------- ---------
12V 3000.00 1.00 1554.59
12Vsb 1500.00 1.00 1309.10
PWOK ******** ******** 1760.09
Vin_Good ******** ******** 0.06
SMBAlert ******** ******** 0.06
Load Ref Load Td Td Td
Name No. Max Min (ms)
------------- ------------- -------- -------- ---------
12V 3 -500.00 -100.00 -205.51
12Vsb 1 -1500.00 -50.00 -245.48
PWOK 1 500.00 100.00 205.51
Vin_Good 0 ******** ******** 0.06
SMBAlert 0 ******** ******** 0.06
STEP.82(UUT Test seq.82) : PS OFF Time 80611(264V_63Hz_HH) ---- (2'496) --- PASS
Vin (V)= Refer to the previous item
Fin (Hz)= Refer to the previous item
On Phase Delay(ms)= Refer to the previous item
UUT Off Time (s)= Refer to the previous item
Loading (A/Ohm/V)= Refer to the previous item
Trigger: 1:Trig1R(AC), 2:Trig2R(PS on), 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:Trig1F(AC), 9:Trig2F(PS on),10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1
2 1
3 1
4 1
Load Start End VcmpA VcmpB
Name Trigger Trigger (V) (V)
------------- ------- ------- ------- -------
12V 2 12 11.590 12.810
12Vsb 2 2 11.400 12.600
PWOK 2 12 2.600 2.600
Vin_Good 2 2 2.600 2.600
SMBAlert 2 2 2.600 2.600
Load Ton Ton Ton
Name Max Min (ms)
------------- -------- -------- ---------
12V ******** ******** 2.40
12Vsb ******** ******** --------
PWOK 50.00 0.01 0.70
Vin_Good ******** ******** --------
SMBAlert ******** ******** --------
Load Ref Load Td Td Td
Name No. Max Min (ms)
------------- ---------- -------- -------- ---------
12V 3 100.00 1.00 1.70
12Vsb 0 ******** ******** --------
PWOK 1 -100.00 -1.00 -1.70
Vin_Good 0 ******** ******** --------
SMBAlert 0 ******** ******** --------
STEP.83(UUT Test seq.83) : PS ON Delay time 80611(264V_63Hz_HH) ---- (0'890 PASS
Vin (V)= Refer to the previous item
Fin (Hz)= Refer to the previous item
On Phase Delay(ms)= Refer to the previous item
UUT Off Time (s)= Refer to the previous item
Loading (A/Ohm/V)= Refer to the previous item
Trigger: 1:Trig1R(AC), 2:Trig2R(PS on), 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:Trig1F(AC), 9:Trig2F(PS on),10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1
2 1
3 1
4 1
Load Start End VcmpA VcmpB
Name Trigger Trigger (V) (V)
------------- ------- ------- ------- -------
12V 9 5 11.590 12.810
12Vsb 9 9 11.400 12.600
PWOK 9 5 2.600 2.600
Vin_Good 9 9 2.600 2.600
SMBAlert 9 9 2.600 2.600
Load Ton Ton Ton
Name Max Min (ms)
------------- -------- -------- ---------
12V 400.00 5.00 62.65
12Vsb ******** ******** 0.12
PWOK ******** ******** 268.19
Vin_Good ******** ******** 0.12
SMBAlert ******** ******** 0.12
Load Ref Load Td Td Td
Name No. Max Min (ms)
------------- ---------- -------- -------- ---------
12V 3 -500.000 -100.000 -205.544
12Vsb 0 ********* ********* 0.119
PWOK 1 500.000 100.000 205.544
Vin_Good 0 ********* ********* 0.119
SMBAlert 0 ********* ********* 0.119
STEP.84(UUT Test seq.84) : Turn On Timing Test_Multi or Single(264V_63Hz_HH PASS
ElaspedTime (S)= 2'138
Vin (V)= 264.00
Fin (Hz)= 63.00
On Phase Delay(ms)= 90.00
UUT Off Time (s)= 0.50
Trigger: 1:TTL1R, 2:TTL2R, 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:TTL1F, 9:TTL2F,10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1.00
2 1.00
3 1.00
4 1.00
Load Loading Start End VcmpA VcmpB
Name (A/Ohm/V) Trigger Trigger (V) (V)
------------- ---------- ------- ------- ------- -------
12V 161.500 5 6 1.220 11.590
12Vsb 2.500 5 6 1.200 10.800
PWOK 0.000 8 1 2.600 3.460
Vin_Good 0.000 8 1 2.600 3.460
SMBAlert 0.000 8 1 2.600 3.460
Load Ton Ton Ton
Name Max Min (ms)
------------- -------- -------- ---------
12V 70.00 5.00 51.28
12Vsb 70.00 1.00 11.89
PWOK ******** ******** 0.06
Vin_Good ******** ******** 0.06
SMBAlert ******** ******** 0.06
Load Ref Load Td Td Td
Name No. Max Min (ms)
------------- ------------- -------- -------- ---------
12V 0 ******** ******** 51.28
12Vsb 0 ******** ******** 11.89
PWOK 0 ******** ******** 0.06
Vin_Good 0 ******** ******** 0.06
SMBAlert 0 ******** ******** 0.06
STEP.85(UUT Test seq.85) : TTL & Relay Setup ---- (0'016) ----------------- PASS
(The Report Format of this Sequence was not found)
STEP.86(UUT Test seq.86) : PS ON Delay time 80611(264V_63Hz_HH_Tpson_12V_Ri PASS
Vin (V)= Refer to the previous item
Fin (Hz)= Refer to the previous item
On Phase Delay(ms)= Refer to the previous item
UUT Off Time (s)= Refer to the previous item
Loading (A/Ohm/V)= Refer to the previous item
Trigger: 1:Trig1R(AC), 2:Trig2R(PS on), 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:Trig1F(AC), 9:Trig2F(PS on),10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1
2 1
3 1
4 1
Load Start End VcmpA VcmpB
Name Trigger Trigger (V) (V)
------------- ------- ------- ------- -------
12V 5 6 1.220 11.590
12Vsb 9 9 1.200 10.800
PWOK 9 9 2.600 2.600
Vin_Good 9 9 2.600 2.600
SMBAlert 9 9 2.600 2.600
Load Ton Ton Ton
Name Max Min (ms)
------------- -------- -------- ---------
12V 70.00 5.00 51.29
12Vsb ******** ******** 0.14
PWOK ******** ******** 0.14
Vin_Good ******** ******** 0.14
SMBAlert ******** ******** 0.14
Load Ref Load Td Td Td
Name No. Max Min (ms)
------------- ---------- -------- -------- ---------
12V 0 ********* ********* 51.286
12Vsb 0 ********* ********* 0.139
PWOK 0 ********* ********* 0.138
Vin_Good 0 ********* ********* 0.139
SMBAlert 0 ********* ********* 0.138
STEP.87(UUT Test seq.87) : Hold Up Timing Test_Multi or Single(264V_63Hz_70 PASS
ElapsedTime (S)= 0'702
Vin (V)= 264.00
Fin (Hz)= 63.00
Delay Time (ms)= 0.00
On Phase Delay(ms)= 90.00
UUT Off Time (s)= 0.00
Trigger: 1:Trig1R(AC), 2:Trig2R(PS on), 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:Trig1F(AC), 9:Trig2F(PS on),10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1
2 1
3 1
4 1
Load Loading Start End VcmpA VcmpB
Name (A/Ohm/V) Trigger Trigger (V) (V)
------------- ---------- ------- ------- ------- -------
12V 113.050 8 12 11.590 12.810
12Vsb 1.750 8 12 11.400 12.600
PWOK 0.000 8 12 2.600 3.460
Vin_Good 0.000 8 12 2.600 3.460
SMBAlert 0.000 8 1 2.600 3.460
Load Tholdup Tholdup Tholdup
Name Max Min (ms)
------------- -------- -------- ---------
12V 1000.00 10.00 22.15
12Vsb 1000.00 70.00 79.07
PWOK 300.00 9.00 20.43
Vin_Good 4.00 0.01 2.67
SMBAlert ******** ******** 0.06
Load Ref Load Tholdup Tholdup Tholdup
Name No. Max Min (ms)
------------- ---------- -------- -------- ---------
12V 3 100.00 1.00 1.72
12Vsb 0 ******** ******** 79.07
PWOK 1 -100.00 -1.00 -1.72
Vin_Good 0 ******** ******** 2.67
SMBAlert 0 ******** ******** 0.06
STEP.88(UUT Test seq.88) : FAN Full Speed delay time Multi ---- (8'096) --- PASS
STEP.89(UUT Test seq.89) : FAN Speed Normal_Multi ---- (0'094) ------------ PASS
(The Report Format of this Sequence was not found)
STEP.90(UUT Test seq.90) : 61512 Ac Source ACDC Mode_Multi_S2 ---- (0'172) PASS
(The Report Format of this Sequence was not found)
STEP.91(UUT Test seq.91) : Turn On Timing Test_Multi or Single(164VDC_LL) - PASS
ElaspedTime (S)= 2'122
Vin (V)= 164.00
Fin (Hz)= 30.00
On Phase Delay(ms)= 90.00
UUT Off Time (s)= 0.00
Trigger: 1:TTL1R, 2:TTL2R, 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:TTL1F, 9:TTL2F,10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1.00
2 1.00
3 1.00
4 1.00
Load Loading Start End VcmpA VcmpB
Name (A/Ohm/V) Trigger Trigger (V) (V)
------------- ---------- ------- ------- ------- -------
12V 1.000 8 5 11.590 12.810
12Vsb 0.100 8 5 11.400 12.600
PWOK 0.000 8 5 2.600 3.460
Vin_Good 0.000 8 1 2.600 3.460
SMBAlert 0.000 8 1 2.600 3.460
Load Ton Ton Ton
Name Max Min (ms)
------------- -------- -------- ---------
12V 3000.00 1.00 1269.02
12Vsb 1500.00 1.00 1024.60
PWOK ******** ******** 1474.93
Vin_Good ******** ******** 0.06
SMBAlert ******** ******** 0.06
Load Ref Load Td Td Td
Name No. Max Min (ms)
------------- ------------- -------- -------- ---------
12V 3 -500.00 -100.00 -205.91
12Vsb 1 -1500.00 -50.00 -244.42
PWOK 1 500.00 100.00 205.91
Vin_Good 0 ******** ******** 0.06
SMBAlert 0 ******** ******** 0.06
STEP.92(UUT Test seq.92) : PS OFF Time 80611(164VDC_LL) ---- (2'434) ------ PASS
Vin (V)= Refer to the previous item
Fin (Hz)= Refer to the previous item
On Phase Delay(ms)= Refer to the previous item
UUT Off Time (s)= Refer to the previous item
Loading (A/Ohm/V)= Refer to the previous item
Trigger: 1:Trig1R(AC), 2:Trig2R(PS on), 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:Trig1F(AC), 9:Trig2F(PS on),10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1
2 1
3 1
4 1
Load Start End VcmpA VcmpB
Name Trigger Trigger (V) (V)
------------- ------- ------- ------- -------
12V 2 12 11.590 12.810
12Vsb 2 2 11.400 12.600
PWOK 2 12 2.600 2.600
Vin_Good 2 2 2.600 2.600
SMBAlert 2 2 2.600 2.600
Load Ton Ton Ton
Name Max Min (ms)
------------- -------- -------- ---------
12V ******** ******** 22.27
12Vsb ******** ******** --------
PWOK 50.00 0.01 0.64
Vin_Good ******** ******** --------
SMBAlert ******** ******** --------
Load Ref Load Td Td Td
Name No. Max Min (ms)
------------- ---------- -------- -------- ---------
12V 3 100.00 1.00 21.63
12Vsb 0 ******** ******** --------
PWOK 1 -100.00 -1.00 -21.63
Vin_Good 0 ******** ******** --------
SMBAlert 0 ******** ******** --------
STEP.93(UUT Test seq.93) : PS ON Delay time 80611(164VDC_LL) ---- (0'842) - PASS
Vin (V)= Refer to the previous item
Fin (Hz)= Refer to the previous item
On Phase Delay(ms)= Refer to the previous item
UUT Off Time (s)= Refer to the previous item
Loading (A/Ohm/V)= Refer to the previous item
Trigger: 1:Trig1R(AC), 2:Trig2R(PS on), 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:Trig1F(AC), 9:Trig2F(PS on),10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1
2 1
3 1
4 1
Load Start End VcmpA VcmpB
Name Trigger Trigger (V) (V)
------------- ------- ------- ------- -------
12V 9 5 11.590 12.810
12Vsb 9 9 11.400 12.600
PWOK 9 5 2.600 2.600
Vin_Good 9 9 2.600 2.600
SMBAlert 9 9 2.600 2.600
Load Ton Ton Ton
Name Max Min (ms)
------------- -------- -------- ---------
12V 400.00 5.00 62.11
12Vsb ******** ******** 0.12
PWOK ******** ******** 268.00
Vin_Good ******** ******** 0.12
SMBAlert ******** ******** 0.12
Load Ref Load Td Td Td
Name No. Max Min (ms)
------------- ---------- -------- -------- ---------
12V 3 -500.000 -100.000 -205.895
12Vsb 0 ********* ********* 0.119
PWOK 1 500.000 100.000 205.895
Vin_Good 0 ********* ********* 0.119
SMBAlert 0 ********* ********* 0.119
STEP.94(UUT Test seq.94) : Turn On Timing Test_Multi or Single(164VDC_LL_Ta PASS
ElaspedTime (S)= 1'747
Vin (V)= 164.00
Fin (Hz)= 30.00
On Phase Delay(ms)= 90.00
UUT Off Time (s)= 0.50
Trigger: 1:TTL1R, 2:TTL2R, 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:TTL1F, 9:TTL2F,10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1.00
2 1.00
3 1.00
4 1.00
Load Loading Start End VcmpA VcmpB
Name (A/Ohm/V) Trigger Trigger (V) (V)
------------- ---------- ------- ------- ------- -------
12V 1.000 5 6 1.220 11.590
12Vsb 0.100 5 6 1.200 10.800
PWOK 0.000 8 1 2.600 3.460
Vin_Good 0.000 8 1 2.600 3.460
SMBAlert 0.000 8 1 2.600 3.460
Load Ton Ton Ton
Name Max Min (ms)
------------- -------- -------- ---------
12V 70.00 5.00 51.30
12Vsb 70.00 1.00 12.79
PWOK ******** ******** 0.06
Vin_Good ******** ******** 0.06
SMBAlert ******** ******** 0.06
Load Ref Load Td Td Td
Name No. Max Min (ms)
------------- ------------- -------- -------- ---------
12V 0 ******** ******** 51.30
12Vsb 0 ******** ******** 12.79
PWOK 0 ******** ******** 0.06
Vin_Good 0 ******** ******** 0.06
SMBAlert 0 ******** ******** 0.06
STEP.95(UUT Test seq.95) : TTL & Relay Setup ---- (0'000) ----------------- PASS
(The Report Format of this Sequence was not found)
STEP.96(UUT Test seq.96) : PS ON Delay time 80611(164VDC_LL_Tpson_12V_Rise) PASS
Vin (V)= Refer to the previous item
Fin (Hz)= Refer to the previous item
On Phase Delay(ms)= Refer to the previous item
UUT Off Time (s)= Refer to the previous item
Loading (A/Ohm/V)= Refer to the previous item
Trigger: 1:Trig1R(AC), 2:Trig2R(PS on), 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:Trig1F(AC), 9:Trig2F(PS on),10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1
2 1
3 1
4 1
Load Start End VcmpA VcmpB
Name Trigger Trigger (V) (V)
------------- ------- ------- ------- -------
12V 5 6 1.220 11.590
12Vsb 9 9 1.200 10.800
PWOK 9 9 2.600 2.600
Vin_Good 9 9 2.600 2.600
SMBAlert 9 9 2.600 2.600
Load Ton Ton Ton
Name Max Min (ms)
------------- -------- -------- ---------
12V 70.00 5.00 51.26
12Vsb ******** ******** 0.14
PWOK ******** ******** 0.14
Vin_Good ******** ******** 0.14
SMBAlert ******** ******** 0.14
Load Ref Load Td Td Td
Name No. Max Min (ms)
------------- ---------- -------- -------- ---------
12V 0 ********* ********* 51.257
12Vsb 0 ********* ********* 0.141
PWOK 0 ********* ********* 0.141
Vin_Good 0 ********* ********* 0.141
SMBAlert 0 ********* ********* 0.141
STEP.97(UUT Test seq.97) : Hold Up Timing Test_Multi or Single(164VDC_LL) - PASS
ElapsedTime (S)= 0'702
Vin (V)= 164.00
Fin (Hz)= 30.00
Delay Time (ms)= 0.00
On Phase Delay(ms)= 90.00
UUT Off Time (s)= 0.00
Trigger: 1:Trig1R(AC), 2:Trig2R(PS on), 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:Trig1F(AC), 9:Trig2F(PS on),10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1
2 1
3 1
4 1
Load Loading Start End VcmpA VcmpB
Name (A/Ohm/V) Trigger Trigger (V) (V)
------------- ---------- ------- ------- ------- -------
12V 1.000 8 12 11.590 12.810
12Vsb 0.100 8 12 11.400 12.600
PWOK 0.000 8 12 2.600 3.460
Vin_Good 0.000 8 12 2.600 3.460
SMBAlert 0.000 8 1 2.600 3.460
Load Tholdup Tholdup Tholdup
Name Max Min (ms)
------------- -------- -------- ---------
12V 1000.00 10.00 64.69
12Vsb 1000.00 70.00 92.57
PWOK 300.00 9.00 43.27
Vin_Good 4.00 0.01 2.58
SMBAlert ******** ******** 0.06
Load Ref Load Tholdup Tholdup Tholdup
Name No. Max Min (ms)
------------- ---------- -------- -------- ---------
12V 3 100.00 1.00 21.42
12Vsb 0 ******** ******** 92.57
PWOK 1 -100.00 -1.00 -21.42
Vin_Good 0 ******** ******** 2.58
SMBAlert 0 ******** ******** 0.06
STEP.98(UUT Test seq.98) : FAN Full Speed delay time Multi ---- (8'097) --- PASS
STEP.99(UUT Test seq.99) : FAN Speed Normal_Multi ---- (0'093) ------------ PASS
(The Report Format of this Sequence was not found)
STEP.100(UUT Test seq.100) : Turn On Timing Test_Multi or Single(164VDC_HH) PASS
ElaspedTime (S)= 2'059
Vin (V)= 164.00
Fin (Hz)= 30.00
On Phase Delay(ms)= 90.00
UUT Off Time (s)= 0.00
Trigger: 1:TTL1R, 2:TTL2R, 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:TTL1F, 9:TTL2F,10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1.00
2 1.00
3 1.00
4 1.00
Load Loading Start End VcmpA VcmpB
Name (A/Ohm/V) Trigger Trigger (V) (V)
------------- ---------- ------- ------- ------- -------
12V 128.700 8 5 11.590 12.810
12Vsb 2.500 8 5 11.400 12.600
PWOK 0.000 8 5 2.600 3.460
Vin_Good 0.000 8 1 2.600 3.460
SMBAlert 0.000 8 1 2.600 3.460
Load Ton Ton Ton
Name Max Min (ms)
------------- -------- -------- ---------
12V 3000.00 1.00 1263.99
12Vsb 1500.00 1.00 1018.59
PWOK ******** ******** 1469.69
Vin_Good ******** ******** 0.06
SMBAlert ******** ******** 0.06
Load Ref Load Td Td Td
Name No. Max Min (ms)
------------- ------------- -------- -------- ---------
12V 3 -500.00 -100.00 -205.70
12Vsb 1 -1500.00 -50.00 -245.40
PWOK 1 500.00 100.00 205.70
Vin_Good 0 ******** ******** 0.06
SMBAlert 0 ******** ******** 0.06
STEP.101(UUT Test seq.101) : PS OFF Time 80611(164VDC_HH) ---- (2'543) ---- PASS
Vin (V)= Refer to the previous item
Fin (Hz)= Refer to the previous item
On Phase Delay(ms)= Refer to the previous item
UUT Off Time (s)= Refer to the previous item
Loading (A/Ohm/V)= Refer to the previous item
Trigger: 1:Trig1R(AC), 2:Trig2R(PS on), 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:Trig1F(AC), 9:Trig2F(PS on),10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1
2 1
3 1
4 1
Load Start End VcmpA VcmpB
Name Trigger Trigger (V) (V)
------------- ------- ------- ------- -------
12V 2 12 11.590 12.810
12Vsb 2 2 11.400 12.600
PWOK 2 12 2.600 2.600
Vin_Good 2 2 2.600 2.600
SMBAlert 2 2 2.600 2.600
Load Ton Ton Ton
Name Max Min (ms)
------------- -------- -------- ---------
12V ******** ******** 2.34
12Vsb ******** ******** --------
PWOK 50.00 0.01 0.61
Vin_Good ******** ******** --------
SMBAlert ******** ******** --------
Load Ref Load Td Td Td
Name No. Max Min (ms)
------------- ---------- -------- -------- ---------
12V 3 100.00 1.00 1.73
12Vsb 0 ******** ******** --------
PWOK 1 -100.00 -1.00 -1.73
Vin_Good 0 ******** ******** --------
SMBAlert 0 ******** ******** --------
STEP.102(UUT Test seq.102) : PS ON Delay time 80611(164VDC_HH) ---- (0'952) PASS
Vin (V)= Refer to the previous item
Fin (Hz)= Refer to the previous item
On Phase Delay(ms)= Refer to the previous item
UUT Off Time (s)= Refer to the previous item
Loading (A/Ohm/V)= Refer to the previous item
Trigger: 1:Trig1R(AC), 2:Trig2R(PS on), 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:Trig1F(AC), 9:Trig2F(PS on),10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1
2 1
3 1
4 1
Load Start End VcmpA VcmpB
Name Trigger Trigger (V) (V)
------------- ------- ------- ------- -------
12V 9 5 11.590 12.810
12Vsb 9 9 11.400 12.600
PWOK 9 5 2.600 2.600
Vin_Good 9 9 2.600 2.600
SMBAlert 9 9 2.600 2.600
Load Ton Ton Ton
Name Max Min (ms)
------------- -------- -------- ---------
12V 400.00 5.00 62.51
12Vsb ******** ******** 0.14
PWOK ******** ******** 268.13
Vin_Good ******** ******** 0.14
SMBAlert ******** ******** 0.14
Load Ref Load Td Td Td
Name No. Max Min (ms)
------------- ---------- -------- -------- ---------
12V 3 -500.000 -100.000 -205.614
12Vsb 0 ********* ********* 0.140
PWOK 1 500.000 100.000 205.614
Vin_Good 0 ********* ********* 0.140
SMBAlert 0 ********* ********* 0.140
STEP.103(UUT Test seq.103) : Turn On Timing Test_Multi or Single(164VDC_HH_ PASS
ElaspedTime (S)= 2'059
Vin (V)= 164.00
Fin (Hz)= 30.00
On Phase Delay(ms)= 90.00
UUT Off Time (s)= 0.50
Trigger: 1:TTL1R, 2:TTL2R, 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:TTL1F, 9:TTL2F,10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1.00
2 1.00
3 1.00
4 1.00
Load Loading Start End VcmpA VcmpB
Name (A/Ohm/V) Trigger Trigger (V) (V)
------------- ---------- ------- ------- ------- -------
12V 128.700 5 6 1.220 11.590
12Vsb 2.500 5 6 1.200 10.800
PWOK 0.000 8 1 2.600 3.460
Vin_Good 0.000 8 1 2.600 3.460
SMBAlert 0.000 8 1 2.600 3.460
Load Ton Ton Ton
Name Max Min (ms)
------------- -------- -------- ---------
12V 70.00 5.00 51.24
12Vsb 70.00 1.00 11.89
PWOK ******** ******** 0.06
Vin_Good ******** ******** 0.06
SMBAlert ******** ******** 0.06
Load Ref Load Td Td Td
Name No. Max Min (ms)
------------- ------------- -------- -------- ---------
12V 0 ******** ******** 51.24
12Vsb 0 ******** ******** 11.89
PWOK 0 ******** ******** 0.06
Vin_Good 0 ******** ******** 0.06
SMBAlert 0 ******** ******** 0.06
STEP.104(UUT Test seq.104) : TTL & Relay Setup ---- (0'000) --------------- PASS
(The Report Format of this Sequence was not found)
STEP.105(UUT Test seq.105) : PS ON Delay time 80611(164VDC_HH_Tpson_12V_Ris PASS
Vin (V)= Refer to the previous item
Fin (Hz)= Refer to the previous item
On Phase Delay(ms)= Refer to the previous item
UUT Off Time (s)= Refer to the previous item
Loading (A/Ohm/V)= Refer to the previous item
Trigger: 1:Trig1R(AC), 2:Trig2R(PS on), 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:Trig1F(AC), 9:Trig2F(PS on),10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1
2 1
3 1
4 1
Load Start End VcmpA VcmpB
Name Trigger Trigger (V) (V)
------------- ------- ------- ------- -------
12V 5 6 1.220 11.590
12Vsb 9 9 1.200 10.800
PWOK 9 9 2.600 2.600
Vin_Good 9 9 2.600 2.600
SMBAlert 9 9 2.600 2.600
Load Ton Ton Ton
Name Max Min (ms)
------------- -------- -------- ---------
12V 70.00 5.00 51.26
12Vsb ******** ******** 0.14
PWOK ******** ******** 0.14
Vin_Good ******** ******** 0.14
SMBAlert ******** ******** 0.14
Load Ref Load Td Td Td
Name No. Max Min (ms)
------------- ---------- -------- -------- ---------
12V 0 ********* ********* 51.261
12Vsb 0 ********* ********* 0.141
PWOK 0 ********* ********* 0.141
Vin_Good 0 ********* ********* 0.141
SMBAlert 0 ********* ********* 0.141
STEP.106(UUT Test seq.106) : Hold Up Timing Test_Multi or Single(164VDC_70% PASS
ElapsedTime (S)= 0'733
Vin (V)= 164.00
Fin (Hz)= 30.00
Delay Time (ms)= 0.00
On Phase Delay(ms)= 90.00
UUT Off Time (s)= 0.00
Trigger: 1:Trig1R(AC), 2:Trig2R(PS on), 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:Trig1F(AC), 9:Trig2F(PS on),10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1
2 1
3 1
4 1
Load Loading Start End VcmpA VcmpB
Name (A/Ohm/V) Trigger Trigger (V) (V)
------------- ---------- ------- ------- ------- -------
12V 90.090 8 12 11.590 12.810
12Vsb 1.750 8 12 11.400 12.600
PWOK 0.000 8 12 2.600 3.460
Vin_Good 0.000 8 12 2.600 3.460
SMBAlert 0.000 8 1 2.600 3.460
Load Tholdup Tholdup Tholdup
Name Max Min (ms)
------------- -------- -------- ---------
12V 1000.00 10.00 26.46
12Vsb 1000.00 70.00 78.30
PWOK 300.00 9.00 24.67
Vin_Good 4.00 0.01 2.53
SMBAlert ******** ******** 0.06
Load Ref Load Tholdup Tholdup Tholdup
Name No. Max Min (ms)
------------- ---------- -------- -------- ---------
12V 3 100.00 1.00 1.79
12Vsb 0 ******** ******** 78.30
PWOK 1 -100.00 -1.00 -1.79
Vin_Good 0 ******** ******** 2.53
SMBAlert 0 ******** ******** 0.06
STEP.107(UUT Test seq.107) : FAN Full Speed delay time Multi ---- (8'096) - PASS
STEP.108(UUT Test seq.108) : FAN Speed Normal_Multi ---- (0'109) ---------- PASS
(The Report Format of this Sequence was not found)
STEP.109(UUT Test seq.109) : Turn On Timing Test_Multi or Single(200VDC_HH) PASS
ElaspedTime (S)= 2'012
Vin (V)= 200.00
Fin (Hz)= 30.00
On Phase Delay(ms)= 90.00
UUT Off Time (s)= 0.00
Trigger: 1:TTL1R, 2:TTL2R, 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:TTL1F, 9:TTL2F,10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1.00
2 1.00
3 1.00
4 1.00
Load Loading Start End VcmpA VcmpB
Name (A/Ohm/V) Trigger Trigger (V) (V)
------------- ---------- ------- ------- ------- -------
12V 145.100 8 5 11.590 12.810
12Vsb 2.500 8 5 11.400 12.600
PWOK 0.000 8 5 2.600 3.460
Vin_Good 0.000 8 1 2.600 3.460
SMBAlert 0.000 8 1 2.600 3.460
Load Ton Ton Ton
Name Max Min (ms)
------------- -------- -------- ---------
12V 3000.00 1.00 1180.26
12Vsb 1500.00 1.00 934.75
PWOK ******** ******** 1385.75
Vin_Good ******** ******** 0.06
SMBAlert ******** ******** 0.06
Load Ref Load Td Td Td
Name No. Max Min (ms)
------------- ------------- -------- -------- ---------
12V 3 -500.00 -100.00 -205.50
12Vsb 1 -1500.00 -50.00 -245.51
PWOK 1 500.00 100.00 205.50
Vin_Good 0 ******** ******** 0.06
SMBAlert 0 ******** ******** 0.06
STEP.110(UUT Test seq.110) : PS OFF Time 80611(200VDC_HH) ---- (2'481) ---- PASS
Vin (V)= Refer to the previous item
Fin (Hz)= Refer to the previous item
On Phase Delay(ms)= Refer to the previous item
UUT Off Time (s)= Refer to the previous item
Loading (A/Ohm/V)= Refer to the previous item
Trigger: 1:Trig1R(AC), 2:Trig2R(PS on), 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:Trig1F(AC), 9:Trig2F(PS on),10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1
2 1
3 1
4 1
Load Start End VcmpA VcmpB
Name Trigger Trigger (V) (V)
------------- ------- ------- ------- -------
12V 2 12 11.590 12.810
12Vsb 2 2 11.400 12.600
PWOK 2 12 2.600 2.600
Vin_Good 2 2 2.600 2.600
SMBAlert 2 2 2.600 2.600
Load Ton Ton Ton
Name Max Min (ms)
------------- -------- -------- ---------
12V ******** ******** 2.38
12Vsb ******** ******** --------
PWOK 50.00 0.01 0.67
Vin_Good ******** ******** --------
SMBAlert ******** ******** --------
Load Ref Load Td Td Td
Name No. Max Min (ms)
------------- ---------- -------- -------- ---------
12V 3 100.00 1.00 1.71
12Vsb 0 ******** ******** --------
PWOK 1 -100.00 -1.00 -1.71
Vin_Good 0 ******** ******** --------
SMBAlert 0 ******** ******** --------
STEP.111(UUT Test seq.111) : PS ON Delay time 80611(200VDC_HH) ---- (0'874) PASS
Vin (V)= Refer to the previous item
Fin (Hz)= Refer to the previous item
On Phase Delay(ms)= Refer to the previous item
UUT Off Time (s)= Refer to the previous item
Loading (A/Ohm/V)= Refer to the previous item
Trigger: 1:Trig1R(AC), 2:Trig2R(PS on), 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:Trig1F(AC), 9:Trig2F(PS on),10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1
2 1
3 1
4 1
Load Start End VcmpA VcmpB
Name Trigger Trigger (V) (V)
------------- ------- ------- ------- -------
12V 9 5 11.590 12.810
12Vsb 9 9 11.400 12.600
PWOK 9 5 2.600 2.600
Vin_Good 9 9 2.600 2.600
SMBAlert 9 9 2.600 2.600
Load Ton Ton Ton
Name Max Min (ms)
------------- -------- -------- ---------
12V 400.00 5.00 62.71
12Vsb ******** ******** 0.13
PWOK ******** ******** 268.32
Vin_Good ******** ******** 0.13
SMBAlert ******** ******** 0.13
Load Ref Load Td Td Td
Name No. Max Min (ms)
------------- ---------- -------- -------- ---------
12V 3 -500.000 -100.000 -205.611
12Vsb 0 ********* ********* 0.134
PWOK 1 500.000 100.000 205.611
Vin_Good 0 ********* ********* 0.134
SMBAlert 0 ********* ********* 0.134
STEP.112(UUT Test seq.112) : Turn On Timing Test_Multi or Single(200VDC_HH_ PASS
ElaspedTime (S)= 1'997
Vin (V)= 200.00
Fin (Hz)= 30.00
On Phase Delay(ms)= 90.00
UUT Off Time (s)= 0.50
Trigger: 1:TTL1R, 2:TTL2R, 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:TTL1F, 9:TTL2F,10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1.00
2 1.00
3 1.00
4 1.00
Load Loading Start End VcmpA VcmpB
Name (A/Ohm/V) Trigger Trigger (V) (V)
------------- ---------- ------- ------- ------- -------
12V 145.100 5 6 1.220 11.590
12Vsb 2.500 5 6 1.200 10.800
PWOK 0.000 8 1 2.600 3.460
Vin_Good 0.000 8 1 2.600 3.460
SMBAlert 0.000 8 1 2.600 3.460
Load Ton Ton Ton
Name Max Min (ms)
------------- -------- -------- ---------
12V 70.00 5.00 51.28
12Vsb 70.00 1.00 11.88
PWOK ******** ******** 0.06
Vin_Good ******** ******** 0.06
SMBAlert ******** ******** 0.06
Load Ref Load Td Td Td
Name No. Max Min (ms)
------------- ------------- -------- -------- ---------
12V 0 ******** ******** 51.28
12Vsb 0 ******** ******** 11.88
PWOK 0 ******** ******** 0.06
Vin_Good 0 ******** ******** 0.06
SMBAlert 0 ******** ******** 0.06
STEP.113(UUT Test seq.113) : TTL & Relay Setup ---- (0'000) --------------- PASS
(The Report Format of this Sequence was not found)
STEP.114(UUT Test seq.114) : PS ON Delay time 80611(200VDC_HH_Tpson_12V_Ris PASS
Vin (V)= Refer to the previous item
Fin (Hz)= Refer to the previous item
On Phase Delay(ms)= Refer to the previous item
UUT Off Time (s)= Refer to the previous item
Loading (A/Ohm/V)= Refer to the previous item
Trigger: 1:Trig1R(AC), 2:Trig2R(PS on), 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:Trig1F(AC), 9:Trig2F(PS on),10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1
2 1
3 1
4 1
Load Start End VcmpA VcmpB
Name Trigger Trigger (V) (V)
------------- ------- ------- ------- -------
12V 5 6 1.220 11.590
12Vsb 9 9 1.200 10.800
PWOK 9 9 2.600 2.600
Vin_Good 9 9 2.600 2.600
SMBAlert 9 9 2.600 2.600
Load Ton Ton Ton
Name Max Min (ms)
------------- -------- -------- ---------
12V 70.00 5.00 51.27
12Vsb ******** ******** 0.13
PWOK ******** ******** 0.13
Vin_Good ******** ******** 0.13
SMBAlert ******** ******** 0.13
Load Ref Load Td Td Td
Name No. Max Min (ms)
------------- ---------- -------- -------- ---------
12V 0 ********* ********* 51.271
12Vsb 0 ********* ********* 0.134
PWOK 0 ********* ********* 0.134
Vin_Good 0 ********* ********* 0.134
SMBAlert 0 ********* ********* 0.134
STEP.115(UUT Test seq.115) : Hold Up Timing Test_Multi or Single(200VDC_70% PASS
ElapsedTime (S)= 0'718
Vin (V)= 200.00
Fin (Hz)= 30.00
Delay Time (ms)= 0.00
On Phase Delay(ms)= 90.00
UUT Off Time (s)= 0.00
Trigger: 1:Trig1R(AC), 2:Trig2R(PS on), 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:Trig1F(AC), 9:Trig2F(PS on),10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1
2 1
3 1
4 1
Load Loading Start End VcmpA VcmpB
Name (A/Ohm/V) Trigger Trigger (V) (V)
------------- ---------- ------- ------- ------- -------
12V 101.570 8 12 11.590 12.810
12Vsb 1.750 8 12 11.400 12.600
PWOK 0.000 8 12 2.600 3.460
Vin_Good 0.000 8 12 2.600 3.460
SMBAlert 0.000 8 1 2.600 3.460
Load Tholdup Tholdup Tholdup
Name Max Min (ms)
------------- -------- -------- ---------
12V 1000.00 10.00 24.00
12Vsb 1000.00 70.00 78.99
PWOK 300.00 9.00 22.35
Vin_Good 4.00 0.01 2.80
SMBAlert ******** ******** 0.06
Load Ref Load Tholdup Tholdup Tholdup
Name No. Max Min (ms)
------------- ---------- -------- -------- ---------
12V 3 100.00 1.00 1.65
12Vsb 0 ******** ******** 78.99
PWOK 1 -100.00 -1.00 -1.65
Vin_Good 0 ******** ******** 2.80
SMBAlert 0 ******** ******** 0.06
STEP.116(UUT Test seq.116) : FAN Full Speed delay time Multi ---- (8'096) - PASS
STEP.117(UUT Test seq.117) : Turn On Timing Test_Multi or Single(220VDC_HH) PASS
ElaspedTime (S)= 1'887
Vin (V)= 220.00
Fin (Hz)= 30.00
On Phase Delay(ms)= 90.00
UUT Off Time (s)= 0.00
Trigger: 1:TTL1R, 2:TTL2R, 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:TTL1F, 9:TTL2F,10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1.00
2 1.00
3 1.00
4 1.00
Load Loading Start End VcmpA VcmpB
Name (A/Ohm/V) Trigger Trigger (V) (V)
------------- ---------- ------- ------- ------- -------
12V 161.500 8 5 11.590 12.810
12Vsb 2.500 8 5 11.400 12.600
PWOK 0.000 8 5 2.600 3.460
Vin_Good 0.000 8 1 2.600 3.460
SMBAlert 0.000 8 1 2.600 3.460
Load Ton Ton Ton
Name Max Min (ms)
------------- -------- -------- ---------
12V 3000.00 1.00 1140.04
12Vsb 1500.00 1.00 894.46
PWOK ******** ******** 1345.55
Vin_Good ******** ******** 0.06
SMBAlert ******** ******** 0.06
Load Ref Load Td Td Td
Name No. Max Min (ms)
------------- ------------- -------- -------- ---------
12V 3 -500.00 -100.00 -205.51
12Vsb 1 -1500.00 -50.00 -245.58
PWOK 1 500.00 100.00 205.51
Vin_Good 0 ******** ******** 0.06
SMBAlert 0 ******** ******** 0.06
STEP.118(UUT Test seq.118) : PS OFF Time 80611(220VDC_HH) ---- (2'512) ---- PASS
Vin (V)= Refer to the previous item
Fin (Hz)= Refer to the previous item
On Phase Delay(ms)= Refer to the previous item
UUT Off Time (s)= Refer to the previous item
Loading (A/Ohm/V)= Refer to the previous item
Trigger: 1:Trig1R(AC), 2:Trig2R(PS on), 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:Trig1F(AC), 9:Trig2F(PS on),10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1
2 1
3 1
4 1
Load Start End VcmpA VcmpB
Name Trigger Trigger (V) (V)
------------- ------- ------- ------- -------
12V 2 12 11.590 12.810
12Vsb 2 2 11.400 12.600
PWOK 2 12 2.600 2.600
Vin_Good 2 2 2.600 2.600
SMBAlert 2 2 2.600 2.600
Load Ton Ton Ton
Name Max Min (ms)
------------- -------- -------- ---------
12V ******** ******** 2.31
12Vsb ******** ******** --------
PWOK 50.00 0.01 0.61
Vin_Good ******** ******** --------
SMBAlert ******** ******** --------
Load Ref Load Td Td Td
Name No. Max Min (ms)
------------- ---------- -------- -------- ---------
12V 3 100.00 1.00 1.70
12Vsb 0 ******** ******** --------
PWOK 1 -100.00 -1.00 -1.70
Vin_Good 0 ******** ******** --------
SMBAlert 0 ******** ******** --------
STEP.119(UUT Test seq.119) : PS ON Delay time 80611(220VDC_HH) ---- (0'858) PASS
Vin (V)= Refer to the previous item
Fin (Hz)= Refer to the previous item
On Phase Delay(ms)= Refer to the previous item
UUT Off Time (s)= Refer to the previous item
Loading (A/Ohm/V)= Refer to the previous item
Trigger: 1:Trig1R(AC), 2:Trig2R(PS on), 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:Trig1F(AC), 9:Trig2F(PS on),10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1
2 1
3 1
4 1
Load Start End VcmpA VcmpB
Name Trigger Trigger (V) (V)
------------- ------- ------- ------- -------
12V 9 5 11.590 12.810
12Vsb 9 9 11.400 12.600
PWOK 9 5 2.600 2.600
Vin_Good 9 9 2.600 2.600
SMBAlert 9 9 2.600 2.600
Load Ton Ton Ton
Name Max Min (ms)
------------- -------- -------- ---------
12V 400.00 5.00 62.70
12Vsb ******** ******** 0.14
PWOK ******** ******** 268.19
Vin_Good ******** ******** 0.14
SMBAlert ******** ******** 0.14
Load Ref Load Td Td Td
Name No. Max Min (ms)
------------- ---------- -------- -------- ---------
12V 3 -500.000 -100.000 -205.497
12Vsb 0 ********* ********* 0.139
PWOK 1 500.000 100.000 205.497
Vin_Good 0 ********* ********* 0.139
SMBAlert 0 ********* ********* 0.139
STEP.120(UUT Test seq.120) : Turn On Timing Test_Multi or Single(220VDC_HH_ PASS
ElaspedTime (S)= 2'012
Vin (V)= 220.00
Fin (Hz)= 30.00
On Phase Delay(ms)= 90.00
UUT Off Time (s)= 0.50
Trigger: 1:TTL1R, 2:TTL2R, 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:TTL1F, 9:TTL2F,10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1.00
2 1.00
3 1.00
4 1.00
Load Loading Start End VcmpA VcmpB
Name (A/Ohm/V) Trigger Trigger (V) (V)
------------- ---------- ------- ------- ------- -------
12V 161.500 5 6 1.220 11.590
12Vsb 2.500 5 6 1.200 10.800
PWOK 0.000 8 1 2.600 3.460
Vin_Good 0.000 8 1 2.600 3.460
SMBAlert 0.000 8 1 2.600 3.460
Load Ton Ton Ton
Name Max Min (ms)
------------- -------- -------- ---------
12V 70.00 5.00 51.28
12Vsb 70.00 1.00 11.87
PWOK ******** ******** 0.06
Vin_Good ******** ******** 0.06
SMBAlert ******** ******** 0.06
Load Ref Load Td Td Td
Name No. Max Min (ms)
------------- ------------- -------- -------- ---------
12V 0 ******** ******** 51.28
12Vsb 0 ******** ******** 11.87
PWOK 0 ******** ******** 0.06
Vin_Good 0 ******** ******** 0.06
SMBAlert 0 ******** ******** 0.06
STEP.121(UUT Test seq.121) : TTL & Relay Setup ---- (0'000) --------------- PASS
(The Report Format of this Sequence was not found)
STEP.122(UUT Test seq.122) : PS ON Delay time 80611(220VDC_HH_Tpson_12V_Ris PASS
Vin (V)= Refer to the previous item
Fin (Hz)= Refer to the previous item
On Phase Delay(ms)= Refer to the previous item
UUT Off Time (s)= Refer to the previous item
Loading (A/Ohm/V)= Refer to the previous item
Trigger: 1:Trig1R(AC), 2:Trig2R(PS on), 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:Trig1F(AC), 9:Trig2F(PS on),10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1
2 1
3 1
4 1
Load Start End VcmpA VcmpB
Name Trigger Trigger (V) (V)
------------- ------- ------- ------- -------
12V 5 6 1.220 11.590
12Vsb 9 9 1.200 10.800
PWOK 9 9 2.600 2.600
Vin_Good 9 9 2.600 2.600
SMBAlert 9 9 2.600 2.600
Load Ton Ton Ton
Name Max Min (ms)
------------- -------- -------- ---------
12V 70.00 5.00 51.30
12Vsb ******** ******** 0.15
PWOK ******** ******** 0.15
Vin_Good ******** ******** 0.15
SMBAlert ******** ******** 0.15
Load Ref Load Td Td Td
Name No. Max Min (ms)
------------- ---------- -------- -------- ---------
12V 0 ********* ********* 51.299
12Vsb 0 ********* ********* 0.147
PWOK 0 ********* ********* 0.147
Vin_Good 0 ********* ********* 0.147
SMBAlert 0 ********* ********* 0.147
STEP.123(UUT Test seq.123) : Hold Up Timing Test_Multi or Single(220VDC_70% PASS
ElapsedTime (S)= 0'718
Vin (V)= 220.00
Fin (Hz)= 30.00
Delay Time (ms)= 0.00
On Phase Delay(ms)= 90.00
UUT Off Time (s)= 0.00
Trigger: 1:Trig1R(AC), 2:Trig2R(PS on), 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:Trig1F(AC), 9:Trig2F(PS on),10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1
2 1
3 1
4 1
Load Loading Start End VcmpA VcmpB
Name (A/Ohm/V) Trigger Trigger (V) (V)
------------- ---------- ------- ------- ------- -------
12V 113.050 8 12 11.590 12.810
12Vsb 1.750 8 12 11.400 12.600
PWOK 0.000 8 12 2.600 3.460
Vin_Good 0.000 8 12 2.600 3.460
SMBAlert 0.000 8 1 2.600 3.460
Load Tholdup Tholdup Tholdup
Name Max Min (ms)
------------- -------- -------- ---------
12V 1000.00 10.00 21.76
12Vsb 1000.00 70.00 78.54
PWOK 300.00 9.00 20.10
Vin_Good 4.00 0.01 2.75
SMBAlert ******** ******** 0.06
Load Ref Load Tholdup Tholdup Tholdup
Name No. Max Min (ms)
------------- ---------- -------- -------- ---------
12V 3 100.00 1.00 1.65
12Vsb 0 ******** ******** 78.54
PWOK 1 -100.00 -1.00 -1.65
Vin_Good 0 ******** ******** 2.75
SMBAlert 0 ******** ******** 0.06
STEP.124(UUT Test seq.124) : FAN Full Speed delay time Multi ---- (8'112) - PASS
STEP.125(UUT Test seq.125) : FAN Speed Normal_Multi ---- (0'093) ---------- PASS
(The Report Format of this Sequence was not found)
STEP.126(UUT Test seq.126) : Turn On Timing Test_Multi or Single(300VDC_LL) PASS
ElaspedTime (S)= 1'794
Vin (V)= 300.00
Fin (Hz)= 30.00
On Phase Delay(ms)= 90.00
UUT Off Time (s)= 0.00
Trigger: 1:TTL1R, 2:TTL2R, 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:TTL1F, 9:TTL2F,10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1.00
2 1.00
3 1.00
4 1.00
Load Loading Start End VcmpA VcmpB
Name (A/Ohm/V) Trigger Trigger (V) (V)
------------- ---------- ------- ------- ------- -------
12V 1.000 8 5 11.590 12.810
12Vsb 0.100 8 5 11.400 12.600
PWOK 0.000 8 5 2.600 3.460
Vin_Good 0.000 8 1 2.600 3.460
SMBAlert 0.000 8 1 2.600 3.460
Load Ton Ton Ton
Name Max Min (ms)
------------- -------- -------- ---------
12V 3000.00 1.00 979.96
12Vsb 1500.00 1.00 735.50
PWOK ******** ******** 1185.92
Vin_Good ******** ******** 0.06
SMBAlert ******** ******** 0.06
Load Ref Load Td Td Td
Name No. Max Min (ms)
------------- ------------- -------- -------- ---------
12V 3 -500.00 -100.00 -205.95
12Vsb 1 -1500.00 -50.00 -244.46
PWOK 1 500.00 100.00 205.95
Vin_Good 0 ******** ******** 0.06
SMBAlert 0 ******** ******** 0.06
STEP.127(UUT Test seq.127) : PS OFF Time 80611(300VDC_LL) ---- (2'528) ---- PASS
Vin (V)= Refer to the previous item
Fin (Hz)= Refer to the previous item
On Phase Delay(ms)= Refer to the previous item
UUT Off Time (s)= Refer to the previous item
Loading (A/Ohm/V)= Refer to the previous item
Trigger: 1:Trig1R(AC), 2:Trig2R(PS on), 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:Trig1F(AC), 9:Trig2F(PS on),10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1
2 1
3 1
4 1
Load Start End VcmpA VcmpB
Name Trigger Trigger (V) (V)
------------- ------- ------- ------- -------
12V 2 12 11.590 12.810
12Vsb 2 2 11.400 12.600
PWOK 2 12 2.600 2.600
Vin_Good 2 2 2.600 2.600
SMBAlert 2 2 2.600 2.600
Load Ton Ton Ton
Name Max Min (ms)
------------- -------- -------- ---------
12V ******** ******** 22.44
12Vsb ******** ******** --------
PWOK 50.00 0.01 0.72
Vin_Good ******** ******** --------
SMBAlert ******** ******** --------
Load Ref Load Td Td Td
Name No. Max Min (ms)
------------- ---------- -------- -------- ---------
12V 3 100.00 1.00 21.72
12Vsb 0 ******** ******** --------
PWOK 1 -100.00 -1.00 -21.72
Vin_Good 0 ******** ******** --------
SMBAlert 0 ******** ******** --------
STEP.128(UUT Test seq.128) : PS ON Delay time 80611(300VDC_LL) ---- (0'952) PASS
Vin (V)= Refer to the previous item
Fin (Hz)= Refer to the previous item
On Phase Delay(ms)= Refer to the previous item
UUT Off Time (s)= Refer to the previous item
Loading (A/Ohm/V)= Refer to the previous item
Trigger: 1:Trig1R(AC), 2:Trig2R(PS on), 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:Trig1F(AC), 9:Trig2F(PS on),10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1
2 1
3 1
4 1
Load Start End VcmpA VcmpB
Name Trigger Trigger (V) (V)
------------- ------- ------- ------- -------
12V 9 5 11.590 12.810
12Vsb 9 9 11.400 12.600
PWOK 9 5 2.600 2.600
Vin_Good 9 9 2.600 2.600
SMBAlert 9 9 2.600 2.600
Load Ton Ton Ton
Name Max Min (ms)
------------- -------- -------- ---------
12V 400.00 5.00 62.10
12Vsb ******** ******** 0.13
PWOK ******** ******** 268.00
Vin_Good ******** ******** 0.14
SMBAlert ******** ******** 0.14
Load Ref Load Td Td Td
Name No. Max Min (ms)
------------- ---------- -------- -------- ---------
12V 3 -500.000 -100.000 -205.895
12Vsb 0 ********* ********* 0.134
PWOK 1 500.000 100.000 205.895
Vin_Good 0 ********* ********* 0.135
SMBAlert 0 ********* ********* 0.135
STEP.129(UUT Test seq.129) : Turn On Timing Test_Multi or Single(300VDC_LL_ PASS
ElaspedTime (S)= 1'700
Vin (V)= 300.00
Fin (Hz)= 30.00
On Phase Delay(ms)= 90.00
UUT Off Time (s)= 0.50
Trigger: 1:TTL1R, 2:TTL2R, 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:TTL1F, 9:TTL2F,10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1.00
2 1.00
3 1.00
4 1.00
Load Loading Start End VcmpA VcmpB
Name (A/Ohm/V) Trigger Trigger (V) (V)
------------- ---------- ------- ------- ------- -------
12V 1.000 5 6 1.220 11.590
12Vsb 0.100 5 6 1.200 10.800
PWOK 0.000 8 1 2.600 3.460
Vin_Good 0.000 8 1 2.600 3.460
SMBAlert 0.000 8 1 2.600 3.460
Load Ton Ton Ton
Name Max Min (ms)
------------- -------- -------- ---------
12V 70.00 5.00 51.26
12Vsb 70.00 1.00 12.76
PWOK ******** ******** 0.06
Vin_Good ******** ******** 0.06
SMBAlert ******** ******** 0.06
Load Ref Load Td Td Td
Name No. Max Min (ms)
------------- ------------- -------- -------- ---------
12V 0 ******** ******** 51.26
12Vsb 0 ******** ******** 12.76
PWOK 0 ******** ******** 0.06
Vin_Good 0 ******** ******** 0.06
SMBAlert 0 ******** ******** 0.06
STEP.130(UUT Test seq.130) : TTL & Relay Setup ---- (0'000) --------------- PASS
(The Report Format of this Sequence was not found)
STEP.131(UUT Test seq.131) : PS ON Delay time 80611(300VDC_LL_Tpson_12V_Ris PASS
Vin (V)= Refer to the previous item
Fin (Hz)= Refer to the previous item
On Phase Delay(ms)= Refer to the previous item
UUT Off Time (s)= Refer to the previous item
Loading (A/Ohm/V)= Refer to the previous item
Trigger: 1:Trig1R(AC), 2:Trig2R(PS on), 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:Trig1F(AC), 9:Trig2F(PS on),10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1
2 1
3 1
4 1
Load Start End VcmpA VcmpB
Name Trigger Trigger (V) (V)
------------- ------- ------- ------- -------
12V 5 6 1.220 11.590
12Vsb 9 9 1.200 10.800
PWOK 9 9 2.600 2.600
Vin_Good 9 9 2.600 2.600
SMBAlert 9 9 2.600 2.600
Load Ton Ton Ton
Name Max Min (ms)
------------- -------- -------- ---------
12V 70.00 5.00 51.29
12Vsb ******** ******** 0.13
PWOK ******** ******** 0.13
Vin_Good ******** ******** 0.13
SMBAlert ******** ******** 0.13
Load Ref Load Td Td Td
Name No. Max Min (ms)
------------- ---------- -------- -------- ---------
12V 0 ********* ********* 51.286
12Vsb 0 ********* ********* 0.130
PWOK 0 ********* ********* 0.130
Vin_Good 0 ********* ********* 0.130
SMBAlert 0 ********* ********* 0.130
STEP.132(UUT Test seq.132) : Hold Up Timing Test_Multi or Single(300VDC_LL) PASS
ElapsedTime (S)= 0'686
Vin (V)= 300.00
Fin (Hz)= 30.00
Delay Time (ms)= 0.00
On Phase Delay(ms)= 90.00
UUT Off Time (s)= 0.00
Trigger: 1:Trig1R(AC), 2:Trig2R(PS on), 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:Trig1F(AC), 9:Trig2F(PS on),10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1
2 1
3 1
4 1
Load Loading Start End VcmpA VcmpB
Name (A/Ohm/V) Trigger Trigger (V) (V)
------------- ---------- ------- ------- ------- -------
12V 1.000 8 12 11.590 12.810
12Vsb 0.100 8 12 11.400 12.600
PWOK 0.000 8 12 2.600 3.460
Vin_Good 0.000 8 12 2.600 3.460
SMBAlert 0.000 8 1 2.600 3.460
Load Tholdup Tholdup Tholdup
Name Max Min (ms)
------------- -------- -------- ---------
12V 1000.00 10.00 64.78
12Vsb 1000.00 70.00 92.94
PWOK 300.00 9.00 43.28
Vin_Good 4.00 0.01 2.79
SMBAlert ******** ******** 0.06
Load Ref Load Tholdup Tholdup Tholdup
Name No. Max Min (ms)
------------- ---------- -------- -------- ---------
12V 3 100.00 1.00 21.50
12Vsb 0 ******** ******** 92.94
PWOK 1 -100.00 -1.00 -21.50
Vin_Good 0 ******** ******** 2.79
SMBAlert 0 ******** ******** 0.06
STEP.133(UUT Test seq.133) : FAN Full Speed delay time Multi ---- (8'097) - PASS
STEP.134(UUT Test seq.134) : FAN Speed Normal_Multi ---- (0'094) ---------- PASS
(The Report Format of this Sequence was not found)
STEP.135(UUT Test seq.135) : Turn On Timing Test_Multi or Single(300VDC_HH) PASS
ElaspedTime (S)= 1'779
Vin (V)= 300.00
Fin (Hz)= 30.00
On Phase Delay(ms)= 90.00
UUT Off Time (s)= 0.00
Trigger: 1:TTL1R, 2:TTL2R, 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:TTL1F, 9:TTL2F,10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1.00
2 1.00
3 1.00
4 1.00
Load Loading Start End VcmpA VcmpB
Name (A/Ohm/V) Trigger Trigger (V) (V)
------------- ---------- ------- ------- ------- -------
12V 161.500 8 5 11.590 12.810
12Vsb 2.500 8 5 11.400 12.600
PWOK 0.000 8 5 2.600 3.460
Vin_Good 0.000 8 1 2.600 3.460
SMBAlert 0.000 8 1 2.600 3.460
Load Ton Ton Ton
Name Max Min (ms)
------------- -------- -------- ---------
12V 3000.00 1.00 986.88
12Vsb 1500.00 1.00 741.37
PWOK ******** ******** 1192.31
Vin_Good ******** ******** 0.06
SMBAlert ******** ******** 0.06
Load Ref Load Td Td Td
Name No. Max Min (ms)
------------- ------------- -------- -------- ---------
12V 3 -500.00 -100.00 -205.43
12Vsb 1 -1500.00 -50.00 -245.51
PWOK 1 500.00 100.00 205.43
Vin_Good 0 ******** ******** 0.06
SMBAlert 0 ******** ******** 0.06
STEP.136(UUT Test seq.136) : PS OFF Time 80611(300VDC_HH) ---- (2'464) ---- PASS
Vin (V)= Refer to the previous item
Fin (Hz)= Refer to the previous item
On Phase Delay(ms)= Refer to the previous item
UUT Off Time (s)= Refer to the previous item
Loading (A/Ohm/V)= Refer to the previous item
Trigger: 1:Trig1R(AC), 2:Trig2R(PS on), 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:Trig1F(AC), 9:Trig2F(PS on),10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1
2 1
3 1
4 1
Load Start End VcmpA VcmpB
Name Trigger Trigger (V) (V)
------------- ------- ------- ------- -------
12V 2 12 11.590 12.810
12Vsb 2 2 11.400 12.600
PWOK 2 12 2.600 2.600
Vin_Good 2 2 2.600 2.600
SMBAlert 2 2 2.600 2.600
Load Ton Ton Ton
Name Max Min (ms)
------------- -------- -------- ---------
12V ******** ******** 2.35
12Vsb ******** ******** --------
PWOK 50.00 0.01 0.65
Vin_Good ******** ******** --------
SMBAlert ******** ******** --------
Load Ref Load Td Td Td
Name No. Max Min (ms)
------------- ---------- -------- -------- ---------
12V 3 100.00 1.00 1.70
12Vsb 0 ******** ******** --------
PWOK 1 -100.00 -1.00 -1.70
Vin_Good 0 ******** ******** --------
SMBAlert 0 ******** ******** --------
STEP.137(UUT Test seq.137) : PS ON Delay time 80611(300VDC_HH) ---- (0'858) PASS
Vin (V)= Refer to the previous item
Fin (Hz)= Refer to the previous item
On Phase Delay(ms)= Refer to the previous item
UUT Off Time (s)= Refer to the previous item
Loading (A/Ohm/V)= Refer to the previous item
Trigger: 1:Trig1R(AC), 2:Trig2R(PS on), 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:Trig1F(AC), 9:Trig2F(PS on),10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1
2 1
3 1
4 1
Load Start End VcmpA VcmpB
Name Trigger Trigger (V) (V)
------------- ------- ------- ------- -------
12V 9 5 11.590 12.810
12Vsb 9 9 11.400 12.600
PWOK 9 5 2.600 2.600
Vin_Good 9 9 2.600 2.600
SMBAlert 9 9 2.600 2.600
Load Ton Ton Ton
Name Max Min (ms)
------------- -------- -------- ---------
12V 400.00 5.00 62.63
12Vsb ******** ******** 0.16
PWOK ******** ******** 268.10
Vin_Good ******** ******** 0.16
SMBAlert ******** ******** 0.16
Load Ref Load Td Td Td
Name No. Max Min (ms)
------------- ---------- -------- -------- ---------
12V 3 -500.000 -100.000 -205.465
12Vsb 0 ********* ********* 0.155
PWOK 1 500.000 100.000 205.465
Vin_Good 0 ********* ********* 0.155
SMBAlert 0 ********* ********* 0.155
STEP.138(UUT Test seq.138) : Turn On Timing Test_Multi or Single(300VDC_HH_ PASS
ElaspedTime (S)= 1'856
Vin (V)= 300.00
Fin (Hz)= 30.00
On Phase Delay(ms)= 90.00
UUT Off Time (s)= 0.50
Trigger: 1:TTL1R, 2:TTL2R, 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:TTL1F, 9:TTL2F,10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1.00
2 1.00
3 1.00
4 1.00
Load Loading Start End VcmpA VcmpB
Name (A/Ohm/V) Trigger Trigger (V) (V)
------------- ---------- ------- ------- ------- -------
12V 161.500 5 6 1.220 11.590
12Vsb 2.500 5 6 1.200 10.800
PWOK 0.000 8 1 2.600 3.460
Vin_Good 0.000 8 1 2.600 3.460
SMBAlert 0.000 8 1 2.600 3.460
Load Ton Ton Ton
Name Max Min (ms)
------------- -------- -------- ---------
12V 70.00 5.00 51.27
12Vsb 70.00 1.00 11.85
PWOK ******** ******** 0.06
Vin_Good ******** ******** 0.06
SMBAlert ******** ******** 0.06
Load Ref Load Td Td Td
Name No. Max Min (ms)
------------- ------------- -------- -------- ---------
12V 0 ******** ******** 51.27
12Vsb 0 ******** ******** 11.85
PWOK 0 ******** ******** 0.06
Vin_Good 0 ******** ******** 0.06
SMBAlert 0 ******** ******** 0.06
STEP.139(UUT Test seq.139) : TTL & Relay Setup ---- (0'000) --------------- PASS
(The Report Format of this Sequence was not found)
STEP.140(UUT Test seq.140) : PS ON Delay time 80611(300VDC_HH_Tpson_12V_Ris PASS
Vin (V)= Refer to the previous item
Fin (Hz)= Refer to the previous item
On Phase Delay(ms)= Refer to the previous item
UUT Off Time (s)= Refer to the previous item
Loading (A/Ohm/V)= Refer to the previous item
Trigger: 1:Trig1R(AC), 2:Trig2R(PS on), 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:Trig1F(AC), 9:Trig2F(PS on),10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1
2 1
3 1
4 1
Load Start End VcmpA VcmpB
Name Trigger Trigger (V) (V)
------------- ------- ------- ------- -------
12V 5 6 1.220 11.590
12Vsb 9 9 1.200 10.800
PWOK 9 9 2.600 2.600
Vin_Good 9 9 2.600 2.600
SMBAlert 9 9 2.600 2.600
Load Ton Ton Ton
Name Max Min (ms)
------------- -------- -------- ---------
12V 70.00 5.00 51.27
12Vsb ******** ******** 0.14
PWOK ******** ******** 0.14
Vin_Good ******** ******** 0.14
SMBAlert ******** ******** 0.14
Load Ref Load Td Td Td
Name No. Max Min (ms)
------------- ---------- -------- -------- ---------
12V 0 ********* ********* 51.275
12Vsb 0 ********* ********* 0.145
PWOK 0 ********* ********* 0.145
Vin_Good 0 ********* ********* 0.145
SMBAlert 0 ********* ********* 0.145
STEP.141(UUT Test seq.141) : Hold Up Timing Test_Multi or Single(300VDC_70% PASS
ElapsedTime (S)= 0'687
Vin (V)= 300.00
Fin (Hz)= 30.00
Delay Time (ms)= 0.00
On Phase Delay(ms)= 90.00
UUT Off Time (s)= 0.00
Trigger: 1:Trig1R(AC), 2:Trig2R(PS on), 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:Trig1F(AC), 9:Trig2F(PS on),10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1
2 1
3 1
4 1
Load Loading Start End VcmpA VcmpB
Name (A/Ohm/V) Trigger Trigger (V) (V)
------------- ---------- ------- ------- ------- -------
12V 113.050 8 12 11.590 12.810
12Vsb 1.750 8 12 11.400 12.600
PWOK 0.000 8 12 2.600 3.460
Vin_Good 0.000 8 12 2.600 3.460
SMBAlert 0.000 8 1 2.600 3.460
Load Tholdup Tholdup Tholdup
Name Max Min (ms)
------------- -------- -------- ---------
12V 1000.00 10.00 21.96
12Vsb 1000.00 70.00 78.92
PWOK 300.00 9.00 20.30
Vin_Good 4.00 0.01 2.75
SMBAlert ******** ******** 0.06
Load Ref Load Tholdup Tholdup Tholdup
Name No. Max Min (ms)
------------- ---------- -------- -------- ---------
12V 3 100.00 1.00 1.66
12Vsb 0 ******** ******** 78.92
PWOK 1 -100.00 -1.00 -1.66
Vin_Good 0 ******** ******** 2.75
SMBAlert 0 ******** ******** 0.06
STEP.142(UUT Test seq.142) : FAN Full Speed delay time Multi ---- (8'097) - PASS
STEP.143(UUT Test seq.143) : FAN Speed Normal_Multi ---- (0'078) ---------- PASS
(The Report Format of this Sequence was not found)
STEP.144(UUT Test seq.144) : Pause Message(Remove Cap Laod) ---- (14'680) - PASS
STEP.145(UUT Test seq.145) : TTL & Relay Setup ---- (0'202) --------------- PASS
(The Report Format of this Sequence was not found)
STEP.146(UUT Test seq.146) : 61512 Ac Source ACDC Mode_Multi_S2 ---- (0'156 PASS
(The Report Format of this Sequence was not found)
STEP.147(UUT Test seq.147) : Turn On Timing Test_Multi or Single(90V_47Hz_L PASS
ElaspedTime (S)= 2'215
Vin (V)= 90.00
Fin (Hz)= 47.00
On Phase Delay(ms)= 90.00
UUT Off Time (s)= 0.00
Trigger: 1:TTL1R, 2:TTL2R, 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:TTL1F, 9:TTL2F,10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1.00
2 1.00
3 1.00
4 1.00
Load Loading Start End VcmpA VcmpB
Name (A/Ohm/V) Trigger Trigger (V) (V)
------------- ---------- ------- ------- ------- -------
12V 1.000 8 5 11.590 12.810
12Vsb 0.100 8 5 11.400 12.600
PWOK 0.000 8 5 2.600 3.460
Vin_Good 0.000 8 1 2.600 3.460
SMBAlert 0.000 8 1 2.600 3.460
Load Ton Ton Ton
Name Max Min (ms)
------------- -------- -------- ---------
12V 3000.00 1.00 1449.24
12Vsb 1500.00 1.00 1204.82
PWOK ******** ******** 1655.09
Vin_Good ******** ******** 0.06
SMBAlert ******** ******** 0.06
Load Ref Load Td Td Td
Name No. Max Min (ms)
------------- ------------- -------- -------- ---------
12V 3 -500.00 -100.00 -205.84
12Vsb 1 -1500.00 -50.00 -244.42
PWOK 1 500.00 100.00 205.84
Vin_Good 0 ******** ******** 0.06
SMBAlert 0 ******** ******** 0.06
STEP.148(UUT Test seq.148) : I2C Read Status Multi_S6(90V_47Hz_LL) ---- (0' PASS
Adderss :B0
Command Page00 :060200
Command Page01 :060201
Status Word :79
Status Byte :78
Status VOUT :7A
Status IOUT :7B
Status INPUT :7C
Status TEMPERATURE :7D
Status CML :7E
Status FANS :81
---------------------------------
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
----------------------------------
Word_Page_00 : 0
Word_Page_01 : 0
Status_Byte_P00 : 0
Status_Byte_P01 : 0
Status_VOUT_P00 : 0
Status_VOUT_P01 : 0
Status_IOUT_P00 : 0
Status_IOUT_P01 : 0
Status_INPUT_P00 : 0
Status_INPUT_P01 : 0
Status_TEM_P00 : 0
Status_TEM_P01 : 0
Status_CML_P00 : 0
Status_CML_P01 : 0
Status_FANS_P00 : 0
Status_FANS_P01 : 0
STEP.149(UUT Test seq.149) : PS OFF Time 80611 ---- (1'576) --------------- PASS
Vin (V)= Refer to the previous item
Fin (Hz)= Refer to the previous item
On Phase Delay(ms)= Refer to the previous item
UUT Off Time (s)= Refer to the previous item
Loading (A/Ohm/V)= Refer to the previous item
Trigger: 1:Trig1R(AC), 2:Trig2R(PS on), 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:Trig1F(AC), 9:Trig2F(PS on),10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1
2 1
3 1
4 1
Load Start End VcmpA VcmpB
Name Trigger Trigger (V) (V)
------------- ------- ------- ------- -------
12V 2 12 11.590 12.810
12Vsb 2 2 11.400 12.600
PWOK 2 12 2.600 2.600
Vin_Good 2 2 2.600 2.600
SMBAlert 2 2 2.600 2.600
Load Ton Ton Ton
Name Max Min (ms)
------------- -------- -------- ---------
12V ******** ******** 5.44
12Vsb ******** ******** --------
PWOK 50.00 0.01 0.81
Vin_Good ******** ******** --------
SMBAlert ******** ******** --------
Load Ref Load Td Td Td
Name No. Max Min (ms)
------------- ---------- -------- -------- ---------
12V 3 100.00 1.00 4.64
12Vsb 0 ******** ******** --------
PWOK 1 -100.00 -1.00 -4.64
Vin_Good 0 ******** ******** --------
SMBAlert 0 ******** ******** --------
STEP.150(UUT Test seq.150) : Input Output Eff Noise Multi or Single(90V_47H PASS
ElapsedTime (S)= 2'730
Vin (V)= 90.00
Fin (Hz)= 47.00
Delay Time (ms)= 1000.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 0.000 ******* ******* 0.000
12Vsb 0.000 ******* ******* 0.000
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
-------Load---------------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V ???.??? ???.??? ???.???
12Vsb ???.??? ???.??? ???.???
PWOK ???.??? ???.??? ???.???
Vin_Good ???.??? ???.??? ???.???
SMBAlert ???.??? ???.??? ???.???
--------34970----------------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 0.400 ******* 0.203
12VSb 12.600 11.400 12.185
PWOK 0.400 ******* 0.039
Vin_Good 3.460 2.500 3.242
SMBAlert 3.460 2.500 3.216
IBUS ******* ******* 0.130
CR 0.400 ******* 0.003
Max Min Reading
------------- ---------- ---------- ----------
Vrms (V) ******** ******** 90.1240
PF 1.0000 ******** 0.0000
THDi (%) ******** * 19.4734
Irms (A) ******** ******** 0.0000
Pin (W) ******** ******** 0.0000
Pout (W) ******** ******** 0.0000
Eff (%) ******** ******** 0.0000
Load Noise Range Noise B.W
Name (V) (MHz)
------------- ----------- ---------
12V 2 20.000
12Vsb 2 20.000
PWOK 2 20.000
Vin_Good 2 20.000
SMBAlert 2 20.000
Load Vpp Noise Vpp Noise Vpp Noise
Name Max(mV) Min(mV) (mV)
------------- ------------ ------------ ------------
12V 120.000 0.000 0.180
12Vsb 120.000 0.000 4.690
PWOK ********* ********* 14.870
Vin_Good ********* ********* 21.330
SMBAlert ********* ********* 22.630
STEP.151(UUT Test seq.151) : I2C Read Status Multi_S6(StandBy) ---- (0'109) PASS
Adderss :B0
Command Page00 :060200
Command Page01 :060201
Status Word :79
Status Byte :78
Status VOUT :7A
Status IOUT :7B
Status INPUT :7C
Status TEMPERATURE :7D
Status CML :7E
Status FANS :81
---------------------------------
Word SPEC: 16392
Word SPEC: 16392
Word SPEC: 16392
Word SPEC: 16392
Word SPEC: 16392
Word SPEC: 16392
Word SPEC: 16392
Word SPEC: 16392
Word SPEC_Page1: 16392
Word SPEC_Page1: 16392
Word SPEC_Page1: 16392
Word SPEC_Page1: 16392
Word SPEC_Page1: 16392
Word SPEC_Page1: 16392
Word SPEC_Page1: 16392
Word SPEC_Page1: 16392
Byte SPEC : 64
Byte SPEC : 64
Byte SPEC : 64
Byte SPEC : 64
Byte SPEC : 64
Byte SPEC : 64
Byte SPEC : 64
Byte SPEC : 64
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
----------------------------------
Word_Page_00 : 16392
Word_Page_01 : 16392
Status_Byte_P00 : 64
Status_Byte_P01 : 64
Status_VOUT_P00 : 0
Status_VOUT_P01 : 0
Status_IOUT_P00 : 0
Status_IOUT_P01 : 0
Status_INPUT_P00 : 0
Status_INPUT_P01 : 0
Status_TEM_P00 : 0
Status_TEM_P01 : 0
Status_CML_P00 : 0
Status_CML_P01 : 0
Status_FANS_P00 : 0
Status_FANS_P01 : 0
STEP.152(UUT Test seq.152) : Input Output Eff Noise Multi or Single(90V_47H PASS
ElapsedTime (S)= 1'794
Vin (V)= 90.00
Fin (Hz)= 47.00
Delay Time (ms)= 500.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 1.000 ******* ******* 0.000
12Vsb 2.500 ******* ******* 2.500
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
-------Load---------------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V ???.??? ???.??? ???.???
12Vsb ???.??? ???.??? ???.???
PWOK ???.??? ???.??? ???.???
Vin_Good ???.??? ???.??? ???.???
SMBAlert ???.??? ???.??? ???.???
--------34970----------------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 0.400 ******* 0.001
12VSb 12.600 11.400 12.009
PWOK 0.400 ******* 0.037
Vin_Good 3.460 2.500 3.245
SMBAlert 3.460 2.500 3.211
IBUS ******* ******* 0.337
CR 0.400 ******* 0.001
Max Min Reading
------------- ---------- ---------- ----------
Vrms (V) ******** ******** 90.0853
PF 1.0000 ******** 0.9857
THDi (%) ******** * 13.3285
Irms (A) ******** ******** 0.4708
Pin (W) ******** ******** 41.8042
Pout (W) ******** ******** 30.0193
Eff (%) ******** ******** 71.8093
Load Noise Range Noise B.W
Name (V) (MHz)
------------- ----------- ---------
12V 2 20.000
12Vsb 2 20.000
PWOK 2 20.000
Vin_Good 2 20.000
SMBAlert 2 20.000
Load Vpp Noise Vpp Noise Vpp Noise
Name Max(mV) Min(mV) (mV)
------------- ------------ ------------ ------------
12V 120.000 0.000 0.000
12Vsb 120.000 0.000 1.920
PWOK ********* ********* 18.820
Vin_Good ********* ********* 25.810
SMBAlert ********* ********* 23.260
STEP.153(UUT Test seq.153) : Static ACDC 34970_or_Load_Multi or Single(12Vs PASS
ElapsedTime (S)= 1'248
Vin (V)= 90.00
Fin (Hz)= 47.00
Delay Time (ms)= 500.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 0.000 ******* ******* 0.000
12Vsb 2.750 ******* ******* 2.750
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 0.400 ******* 0.001
12VSb 12.600 11.400 12.008
PWOK 0.400 ******* 0.037
Vin_Good 3.460 2.500 3.239
SMBAlert 3.460 2.500 3.220
IBUS ******* ******* 0.305
CR 0.400 ******* 0.001
Max Min Reading
------------- --------- --------- ---------
Pout (W) ******* ******* 33.018
STEP.154(UUT Test seq.154) : Static ACDC 34970_or_Load_Multi or Single(12Vs PASS
ElapsedTime (S)= 1'264
Vin (V)= 90.00
Fin (Hz)= 47.00
Delay Time (ms)= 500.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 0.000 ******* ******* 0.000
12Vsb 3.650 ******* ******* 3.650
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 0.400 ******* 0.000
12VSb 12.600 ******* 11.973
PWOK 0.400 ******* 0.036
Vin_Good 3.460 2.400 3.241
SMBAlert 3.460 ******* 3.211
IBUS ******* ******* 0.312
CR 0.400 ******* 0.004
Max Min Reading
------------- --------- --------- ---------
Pout (W) ******* ******* 43.698
STEP.155(UUT Test seq.155) : Static ACDC 34970_or_Load_Multi or Single(12Vs PASS
ElapsedTime (S)= 1'747
Vin (V)= 90.00
Fin (Hz)= 47.00
Delay Time (ms)= 1000.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 0.000 ******* ******* 0.000
12Vsb 2.750 ******* ******* 2.750
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 0.400 ******* 0.001
12VSb 12.600 11.400 12.006
PWOK 0.400 ******* 0.037
Vin_Good 3.460 2.500 3.245
SMBAlert 3.460 2.500 3.211
IBUS ******* ******* 0.342
CR 0.400 ******* 0.001
Max Min Reading
------------- --------- --------- ---------
Pout (W) ******* ******* 33.013
STEP.156(UUT Test seq.156) : Input Output Eff Noise Multi or Single(90V_47H PASS
ElapsedTime (S)= 1'747
Vin (V)= 90.00
Fin (Hz)= 47.00
Delay Time (ms)= 500.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 1.000 ******* ******* 0.000
12Vsb 0.100 ******* ******* 0.100
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
-------Load---------------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V ???.??? ???.??? ???.???
12Vsb ???.??? ???.??? ???.???
PWOK ???.??? ???.??? ???.???
Vin_Good ???.??? ???.??? ???.???
SMBAlert ???.??? ???.??? ???.???
--------34970----------------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 0.400 ******* 0.000
12VSb 12.600 11.400 12.144
PWOK 0.400 ******* 0.039
Vin_Good 3.460 2.500 3.240
SMBAlert 3.460 2.500 3.219
IBUS ******* ******* 0.308
CR 0.400 ******* 0.003
Max Min Reading
------------- ---------- ---------- ----------
Vrms (V) ******** ******** 90.1222
PF 1.0000 ******** 0.7930
THDi (%) ******** * 18.2037
Irms (A) ******** ******** 0.0885
Pin (W) ******** ******** 6.3238
Pout (W) ******** ******** 1.2167
Eff (%) ******** ******** 19.2409
Load Noise Range Noise B.W
Name (V) (MHz)
------------- ----------- ---------
12V 2 20.000
12Vsb 2 20.000
PWOK 2 20.000
Vin_Good 2 20.000
SMBAlert 2 20.000
Load Vpp Noise Vpp Noise Vpp Noise
Name Max(mV) Min(mV) (mV)
------------- ------------ ------------ ------------
12V 120.000 0.000 0.000
12Vsb 120.000 0.000 7.820
PWOK ********* ********* 14.790
Vin_Good ********* ********* 21.720
SMBAlert ********* ********* 22.220
STEP.157(UUT Test seq.157) : PS ON Delay time 80611(90V_47Hz_LL) ---- (0'96 PASS
Vin (V)= Refer to the previous item
Fin (Hz)= Refer to the previous item
On Phase Delay(ms)= Refer to the previous item
UUT Off Time (s)= Refer to the previous item
Loading (A/Ohm/V)= Refer to the previous item
Trigger: 1:Trig1R(AC), 2:Trig2R(PS on), 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:Trig1F(AC), 9:Trig2F(PS on),10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1
2 1
3 1
4 1
Load Start End VcmpA VcmpB
Name Trigger Trigger (V) (V)
------------- ------- ------- ------- -------
12V 9 5 11.590 12.810
12Vsb 9 9 11.400 12.600
PWOK 9 5 2.600 2.600
Vin_Good 9 9 2.600 2.600
SMBAlert 9 9 2.600 2.600
Load Ton Ton Ton
Name Max Min (ms)
------------- -------- -------- ---------
12V 400.00 5.00 62.31
12Vsb ******** ******** 0.14
PWOK ******** ******** 268.14
Vin_Good ******** ******** 0.14
SMBAlert ******** ******** 0.14
Load Ref Load Td Td Td
Name No. Max Min (ms)
------------- ---------- -------- -------- ---------
12V 3 -500.000 -100.000 -205.828
12Vsb 0 ********* ********* 0.138
PWOK 1 500.000 100.000 205.828
Vin_Good 0 ********* ********* 0.138
SMBAlert 0 ********* ********* 0.138
STEP.158(UUT Test seq.158) : Turn On Timing Test_Multi or Single(90V_47Hz_L PASS
ElaspedTime (S)= 1'748
Vin (V)= 90.00
Fin (Hz)= 47.00
On Phase Delay(ms)= 90.00
UUT Off Time (s)= 0.50
Trigger: 1:TTL1R, 2:TTL2R, 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:TTL1F, 9:TTL2F,10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1.00
2 1.00
3 1.00
4 1.00
Load Loading Start End VcmpA VcmpB
Name (A/Ohm/V) Trigger Trigger (V) (V)
------------- ---------- ------- ------- ------- -------
12V 1.000 5 6 1.220 11.590
12Vsb 0.100 5 6 1.200 10.800
PWOK 0.000 8 1 2.600 3.460
Vin_Good 0.000 8 1 2.600 3.460
SMBAlert 0.000 8 1 2.600 3.460
Load Ton Ton Ton
Name Max Min (ms)
------------- -------- -------- ---------
12V 70.00 5.00 51.26
12Vsb 70.00 1.00 12.74
PWOK ******** ******** 0.06
Vin_Good ******** ******** 0.06
SMBAlert ******** ******** 0.06
Load Ref Load Td Td Td
Name No. Max Min (ms)
------------- ------------- -------- -------- ---------
12V 0 ******** ******** 51.26
12Vsb 0 ******** ******** 12.74
PWOK 0 ******** ******** 0.06
Vin_Good 0 ******** ******** 0.06
SMBAlert 0 ******** ******** 0.06
STEP.159(UUT Test seq.159) : TTL & Relay Setup ---- (0'016) --------------- PASS
(The Report Format of this Sequence was not found)
STEP.160(UUT Test seq.160) : PS ON Delay time 80611(90V_47Hz_LL_Tpson_12V_R PASS
Vin (V)= Refer to the previous item
Fin (Hz)= Refer to the previous item
On Phase Delay(ms)= Refer to the previous item
UUT Off Time (s)= Refer to the previous item
Loading (A/Ohm/V)= Refer to the previous item
Trigger: 1:Trig1R(AC), 2:Trig2R(PS on), 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:Trig1F(AC), 9:Trig2F(PS on),10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1
2 1
3 1
4 1
Load Start End VcmpA VcmpB
Name Trigger Trigger (V) (V)
------------- ------- ------- ------- -------
12V 5 6 1.220 11.590
12Vsb 9 9 1.200 10.800
PWOK 9 9 2.600 2.600
Vin_Good 9 9 2.600 2.600
SMBAlert 9 9 2.600 2.600
Load Ton Ton Ton
Name Max Min (ms)
------------- -------- -------- ---------
12V 70.00 5.00 51.28
12Vsb ******** ******** 0.14
PWOK ******** ******** 0.14
Vin_Good ******** ******** 0.14
SMBAlert ******** ******** 0.14
Load Ref Load Td Td Td
Name No. Max Min (ms)
------------- ---------- -------- -------- ---------
12V 0 ********* ********* 51.285
12Vsb 0 ********* ********* 0.145
PWOK 0 ********* ********* 0.145
Vin_Good 0 ********* ********* 0.145
SMBAlert 0 ********* ********* 0.145
STEP.161(UUT Test seq.161) : Input Output Eff Noise Multi or Single(90V_47H PASS
ElapsedTime (S)= 2'995
Vin (V)= 90.00
Fin (Hz)= 47.00
Delay Time (ms)= 1500.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 0.000 ******* ******* 0.000
12Vsb 0.000 ******* ******* 0.000
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
-------Load---------------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V ???.??? ???.??? ???.???
12Vsb ???.??? ???.??? ???.???
PWOK ???.??? ???.??? ???.???
Vin_Good ???.??? ???.??? ???.???
SMBAlert ???.??? ???.??? ???.???
--------34970----------------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 12.810 11.590 12.258
12VSb 12.600 11.400 12.186
PWOK 3.460 2.500 3.248
Vin_Good 3.460 2.500 3.244
SMBAlert 3.460 2.500 3.217
IBUS 0.300 -0.300 0.017
CR 0.400 ******* 0.003
Max Min Reading
------------- ---------- ---------- ----------
Vrms (V) ******** ******** 90.1236
PF 1.0000 ******** 0.0000
THDi (%) ******** * 19.1582
Irms (A) ******** ******** 0.0000
Pin (W) ******** ******** 0.0000
Pout (W) ******** ******** 0.0000
Eff (%) ******** ******** 0.0000
Load Noise Range Noise B.W
Name (V) (MHz)
------------- ----------- ---------
12V 2 20.000
12Vsb 2 20.000
PWOK 2 20.000
Vin_Good 2 20.000
SMBAlert 2 20.000
Load Vpp Noise Vpp Noise Vpp Noise
Name Max(mV) Min(mV) (mV)
------------- ------------ ------------ ------------
12V 120.000 0.000 8.330
12Vsb 120.000 0.000 4.380
PWOK ********* ********* 19.670
Vin_Good ********* ********* 18.310
SMBAlert ********* ********* 22.350
STEP.162(UUT Test seq.162) : I2C Read Status Multi_S6(90V_47Hz_No Load) --- PASS
Adderss :B0
Command Page00 :060200
Command Page01 :060201
Status Word :79
Status Byte :78
Status VOUT :7A
Status IOUT :7B
Status INPUT :7C
Status TEMPERATURE :7D
Status CML :7E
Status FANS :81
---------------------------------
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
----------------------------------
Word_Page_00 : 0
Word_Page_01 : 0
Status_Byte_P00 : 0
Status_Byte_P01 : 0
Status_VOUT_P00 : 0
Status_VOUT_P01 : 0
Status_IOUT_P00 : 0
Status_IOUT_P01 : 0
Status_INPUT_P00 : 0
Status_INPUT_P01 : 0
Status_TEM_P00 : 0
Status_TEM_P01 : 0
Status_CML_P00 : 0
Status_CML_P01 : 0
Status_FANS_P00 : 0
Status_FANS_P01 : 0
STEP.163(UUT Test seq.163) : Static ACDC 34970_or_Load_Multi or Single(12Vs PASS
ElapsedTime (S)= 1'264
Vin (V)= 90.00
Fin (Hz)= 47.00
Delay Time (ms)= 500.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 1.000 ******* ******* 0.998
12Vsb 2.750 ******* ******* 2.750
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 12.810 11.590 12.259
12VSb 12.600 11.400 12.003
PWOK 3.460 2.500 3.243
Vin_Good 3.460 2.500 3.243
SMBAlert 3.460 2.500 3.219
IBUS ******* ******* 0.060
CR 0.400 ******* 0.001
Max Min Reading
------------- --------- --------- ---------
Pout (W) ******* ******* 45.234
STEP.164(UUT Test seq.164) : Static ACDC 34970_or_Load_Multi or Single(12Vs PASS
ElapsedTime (S)= 1'388
Vin (V)= 90.00
Fin (Hz)= 47.00
Delay Time (ms)= 500.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 1.000 ******* ******* 0.000
12Vsb 3.650 ******* ******* 0.010
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 0.400 ******* 0.001
12VSb 12.600 ******* 11.976
PWOK 0.400 ******* 0.039
Vin_Good 3.460 2.400 3.242
SMBAlert 3.460 ******* 3.211
IBUS ******* ******* 0.121
CR 0.400 ******* 0.004
Max Min Reading
------------- --------- --------- ---------
Pout (W) ******* ******* 0.124
STEP.165(UUT Test seq.165) : Static ACDC 34970_or_Load_Multi or Single(12Vs PASS
ElapsedTime (S)= 1'841
Vin (V)= 90.00
Fin (Hz)= 47.00
Delay Time (ms)= 1000.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 1.000 ******* ******* 0.998
12Vsb 2.750 ******* ******* 2.750
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 12.810 11.590 12.251
12VSb 12.600 11.400 12.007
PWOK 3.460 2.500 3.243
Vin_Good 3.460 2.500 3.243
SMBAlert 3.460 2.500 3.219
IBUS ******* ******* 0.061
CR 0.400 ******* 0.001
Max Min Reading
------------- --------- --------- ---------
Pout (W) ******* ******* 45.237
STEP.166(UUT Test seq.166) : Input Output Eff Noise Multi or Single(90V_47H PASS
ElapsedTime (S)= 1'903
Vin (V)= 90.00
Fin (Hz)= 47.00
Delay Time (ms)= 500.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 1.000 ******* ******* 0.998
12Vsb 0.100 ******* ******* 0.100
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
-------Load---------------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V ???.??? ???.??? ???.???
12Vsb ???.??? ???.??? ???.???
PWOK ???.??? ???.??? ???.???
Vin_Good ???.??? ???.??? ???.???
SMBAlert ???.??? ???.??? ???.???
--------34970----------------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 12.810 11.590 12.259
12VSb 12.600 11.400 12.142
PWOK 3.460 2.500 3.245
Vin_Good 3.460 2.500 3.249
SMBAlert 3.460 2.500 3.215
IBUS ******* ******* 0.060
CR 0.400 ******* 0.003
Max Min Reading
------------- ---------- ---------- ----------
Vrms (V) ******** ******** 90.1067
PF 1.0000 ******** 0.9617
THDi (%) ******** * 15.3982
Irms (A) ******** ******** 0.2491
Pin (W) ******** ******** 21.5872
Pout (W) ******** ******** 13.4461
Eff (%) ******** ******** 62.2872
Load Noise Range Noise B.W
Name (V) (MHz)
------------- ----------- ---------
12V 2 20.000
12Vsb 2 20.000
PWOK 2 20.000
Vin_Good 2 20.000
SMBAlert 2 20.000
Load Vpp Noise Vpp Noise Vpp Noise
Name Max(mV) Min(mV) (mV)
------------- ------------ ------------ ------------
12V 120.000 0.000 10.610
12Vsb 120.000 0.000 7.300
PWOK ********* ********* 18.920
Vin_Good ********* ********* 17.390
SMBAlert ********* ********* 21.770
STEP.167(UUT Test seq.167) : Input Output Eff Noise Multi or Single(90V_47H PASS
ElapsedTime (S)= 1'685
Vin (V)= 90.00
Fin (Hz)= 47.00
Delay Time (ms)= 500.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 1.000 ******* ******* 0.998
12Vsb 2.500 ******* ******* 2.500
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
-------Load---------------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V ???.??? ???.??? ???.???
12Vsb ???.??? ???.??? ???.???
PWOK ???.??? ???.??? ???.???
Vin_Good ???.??? ???.??? ???.???
SMBAlert ???.??? ???.??? ???.???
--------34970----------------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 12.810 11.590 12.259
12VSb 12.600 11.400 12.010
PWOK 3.460 2.500 3.243
Vin_Good 3.460 2.500 3.247
SMBAlert 3.460 2.500 3.216
IBUS ******* ******* 0.060
CR 0.400 ******* 0.001
Max Min Reading
------------- ---------- ---------- ----------
Vrms (V) ******** ******** 90.0691
PF 1.0000 ******** 0.9920
THDi (%) ******** * 11.2357
Irms (A) ******** ******** 0.6400
Pin (W) ******** ******** 57.1812
Pout (W) ******** ******** 42.2531
Eff (%) ******** ******** 73.8934
Load Noise Range Noise B.W
Name (V) (MHz)
------------- ----------- ---------
12V 2 20.000
12Vsb 2 20.000
PWOK 2 20.000
Vin_Good 2 20.000
SMBAlert 2 20.000
Load Vpp Noise Vpp Noise Vpp Noise
Name Max(mV) Min(mV) (mV)
------------- ------------ ------------ ------------
12V 120.000 0.000 7.150
12Vsb 120.000 0.000 2.160
PWOK ********* ********* 19.470
Vin_Good ********* ********* 18.830
SMBAlert ********* ********* 21.660
STEP.168(UUT Test seq.168) : Cold Redundant Master Multi _S2 ---- (0'094) - PASS
(The Report Format of this Sequence was not found)
STEP.169(UUT Test seq.169) : Static ACDC 34970_or_Load_Multi or Single(90V_ PASS
ElapsedTime (S)= 1'248
Vin (V)= 90.00
Fin (Hz)= 47.00
Delay Time (ms)= 500.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 1.000 ******* ******* 0.998
12Vsb 0.100 ******* ******* 0.100
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 12.810 11.590 12.258
12VSb 12.600 11.400 12.141
PWOK 3.460 2.500 3.247
Vin_Good 3.460 2.500 3.243
SMBAlert 3.460 2.500 3.214
IBUS ******* ******* 0.061
CR 3.460 2.500 3.190
Max Min Reading
------------- --------- --------- ---------
Pout (W) ******* ******* 13.445
STEP.170(UUT Test seq.170) : Disable Cold Redundant Master Multi_S2 ---- (0 PASS
(The Report Format of this Sequence was not found)
STEP.171(UUT Test seq.171) : Static ACDC 34970_or_Load_Multi or Single(90V_ PASS
ElapsedTime (S)= 1'232
Vin (V)= 90.00
Fin (Hz)= 47.00
Delay Time (ms)= 500.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 1.000 ******* ******* 0.998
12Vsb 0.100 ******* ******* 0.100
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 12.810 11.590 12.259
12VSb 12.600 11.400 12.136
PWOK 3.460 2.500 3.251
Vin_Good 3.460 2.500 3.245
SMBAlert 3.460 2.500 3.216
IBUS ******* ******* 0.061
CR 0.400 ******* 0.003
Max Min Reading
------------- --------- --------- ---------
Pout (W) ******* ******* 13.447
STEP.172(UUT Test seq.172) : Hold Up Timing Test_Multi or Single(90V_47Hz_L PASS
ElapsedTime (S)= 0'733
Vin (V)= 90.00
Fin (Hz)= 47.00
Delay Time (ms)= 0.00
On Phase Delay(ms)= 90.00
UUT Off Time (s)= 0.00
Trigger: 1:Trig1R(AC), 2:Trig2R(PS on), 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:Trig1F(AC), 9:Trig2F(PS on),10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1
2 1
3 1
4 1
Load Loading Start End VcmpA VcmpB
Name (A/Ohm/V) Trigger Trigger (V) (V)
------------- ---------- ------- ------- ------- -------
12V 1.000 8 12 11.590 12.810
12Vsb 0.100 8 12 11.400 12.600
PWOK 0.000 8 12 2.600 3.460
Vin_Good 0.000 8 12 2.600 3.460
SMBAlert 0.000 8 1 2.600 3.460
Load Tholdup Tholdup Tholdup
Name Max Min (ms)
------------- -------- -------- ---------
12V 1000.00 10.00 47.91
12Vsb 1000.00 70.00 91.89
PWOK 300.00 9.00 43.39
Vin_Good 4.00 0.01 2.70
SMBAlert ******** ******** 0.06
Load Ref Load Tholdup Tholdup Tholdup
Name No. Max Min (ms)
------------- ---------- -------- -------- ---------
12V 3 100.00 1.00 4.52
12Vsb 0 ******** ******** 91.89
PWOK 1 -100.00 -1.00 -4.52
Vin_Good 0 ******** ******** 2.70
SMBAlert 0 ******** ******** 0.06
STEP.173(UUT Test seq.173) : FAN Full Speed delay time Multi ---- (8'097) - PASS
STEP.174(UUT Test seq.174) : FAN Speed Normal_Multi ---- (0'078) ---------- PASS
(The Report Format of this Sequence was not found)
STEP.175(UUT Test seq.175) : Turn On Timing Test_Multi or Single(90V_47Hz_H PASS
ElaspedTime (S)= 2'090
Vin (V)= 90.00
Fin (Hz)= 47.00
On Phase Delay(ms)= 90.00
UUT Off Time (s)= 0.00
Trigger: 1:TTL1R, 2:TTL2R, 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:TTL1F, 9:TTL2F,10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1.00
2 1.00
3 1.00
4 1.00
Load Loading Start End VcmpA VcmpB
Name (A/Ohm/V) Trigger Trigger (V) (V)
------------- ---------- ------- ------- ------- -------
12V 71.300 8 5 11.590 12.810
12Vsb 2.500 8 5 11.400 12.600
PWOK 0.000 8 5 2.600 3.460
Vin_Good 0.000 8 1 2.600 3.460
SMBAlert 0.000 8 1 2.600 3.460
Load Ton Ton Ton
Name Max Min (ms)
------------- -------- -------- ---------
12V 3000.00 1.00 1352.78
12Vsb 1500.00 1.00 1107.66
PWOK ******** ******** 1558.58
Vin_Good ******** ******** 0.06
SMBAlert ******** ******** 0.06
Load Ref Load Td Td Td
Name No. Max Min (ms)
------------- ------------- -------- -------- ---------
12V 3 -500.00 -100.00 -205.80
12Vsb 1 -1500.00 -50.00 -245.12
PWOK 1 500.00 100.00 205.80
Vin_Good 0 ******** ******** 0.06
SMBAlert 0 ******** ******** 0.06
STEP.176(UUT Test seq.176) : I2C Read Status Multi_S6(90V_47Hz_HH) ---- (0' PASS
Adderss :B0
Command Page00 :060200
Command Page01 :060201
Status Word :79
Status Byte :78
Status VOUT :7A
Status IOUT :7B
Status INPUT :7C
Status TEMPERATURE :7D
Status CML :7E
Status FANS :81
---------------------------------
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
----------------------------------
Word_Page_00 : 0
Word_Page_01 : 0
Status_Byte_P00 : 0
Status_Byte_P01 : 0
Status_VOUT_P00 : 0
Status_VOUT_P01 : 0
Status_IOUT_P00 : 0
Status_IOUT_P01 : 0
Status_INPUT_P00 : 0
Status_INPUT_P01 : 0
Status_TEM_P00 : 0
Status_TEM_P01 : 0
Status_CML_P00 : 0
Status_CML_P01 : 0
Status_FANS_P00 : 0
Status_FANS_P01 : 0
STEP.177(UUT Test seq.177) : 12V OVP I2C Multi(90V_47Hz_I2C_OVP) ---- (0'06 PASS
STEP.178(UUT Test seq.178) : Static ACDC 34970_or_Load_Multi or Single(90V_ PASS
ElapsedTime (S)= 1'373
Vin (V)= 90.00
Fin (Hz)= 47.00
Delay Time (ms)= 500.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 71.300 ******* ******* 0.000
12Vsb 2.500 ******* ******* 2.500
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 0.400 ******* 0.001
12VSb 12.600 11.400 12.014
PWOK 0.400 ******* 0.037
Vin_Good 3.460 2.500 3.239
SMBAlert 3.460 2.500 3.217
IBUS ******* ******* 0.134
CR 0.400 ******* 0.003
Max Min Reading
------------- --------- --------- ---------
Pout (W) ******* ******* 30.033
STEP.179(UUT Test seq.179) : I2C Read Status OR Multi_S6(90V_47Hz_HH_I2C_OV PASS
Command Page00 :060200
Command Page01 :060201
Status Word :79
Status Byte :78
Status VOUT :7A
Status IOUT :7B
Status INPUT :7C
Status TEMPERATURE :7D
Status CML :7E
Status FANS :81
---------------------------------
Word SPEC: 25224
Word SPEC: 25224
Word SPEC: 25224
Word SPEC: 25224
Word SPEC: 25224
Word SPEC: 25224
Word SPEC: 25224
Word SPEC: 25224
Word SPEC_Page1: 25224
Word SPEC_Page1: 25224
Word SPEC_Page1: 25224
Word SPEC_Page1: 25224
Word SPEC_Page1: 25224
Word SPEC_Page1: 25224
Word SPEC_Page1: 25224
Word SPEC_Page1: 25224
Byte SPEC : 98
Byte SPEC : 98
Byte SPEC : 98
Byte SPEC : 98
Byte SPEC : 98
Byte SPEC : 98
Byte SPEC : 98
Byte SPEC : 98
VOUT SPEC : 192
VOUT SPEC : 192
VOUT SPEC : 192
VOUT SPEC : 192
VOUT SPEC : 192
VOUT SPEC : 192
VOUT SPEC : 192
VOUT SPEC : 192
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
CML SPEC : 128
CML SPEC : 128
CML SPEC : 128
CML SPEC : 128
CML SPEC : 128
CML SPEC : 128
CML SPEC : 128
CML SPEC : 128
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
Word Page0 OR : 0200
Word Page1 OR : 0200
Byte OR : 02
Input OR : 00
IOUT OR : 00
TEMP OR : 00
CML OR : 80
----------------------------------
Word_Page_00 : 25224
Word_Page_01 : 25224
Status_Byte_P00 : 98
Status_Byte_P01 : 98
Status_VOUT_P00 : 192
Status_VOUT_P01 : 192
Status_IOUT_P00 : 0
Status_IOUT_P01 : 0
Status_INPUT_P00 : 0
Status_INPUT_P01 : 0
Status_TEM_P00 : 0
Status_TEM_P01 : 0
Status_CML_P00 : 128
Status_CML_P01 : 128
Status_FANS_P00 : 0
Status_FANS_P01 : 0
STEP.180(UUT Test seq.180) : 12V OVP Disable I2C Multi ---- (0'062) ------- PASS
STEP.181(UUT Test seq.181) : TTL & Relay Setup ---- (0'640) --------------- PASS
(The Report Format of this Sequence was not found)
STEP.182(UUT Test seq.182) : PS OFF Time 80611(90V_47Hz_HH) ---- (1'591) -- PASS
Vin (V)= Refer to the previous item
Fin (Hz)= Refer to the previous item
On Phase Delay(ms)= Refer to the previous item
UUT Off Time (s)= Refer to the previous item
Loading (A/Ohm/V)= Refer to the previous item
Trigger: 1:Trig1R(AC), 2:Trig2R(PS on), 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:Trig1F(AC), 9:Trig2F(PS on),10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1
2 1
3 1
4 1
Load Start End VcmpA VcmpB
Name Trigger Trigger (V) (V)
------------- ------- ------- ------- -------
12V 2 12 11.590 12.810
12Vsb 2 2 11.400 12.600
PWOK 2 12 2.600 2.600
Vin_Good 2 2 2.600 2.600
SMBAlert 2 2 2.600 2.600
Load Ton Ton Ton
Name Max Min (ms)
------------- -------- -------- ---------
12V ******** ******** 2.40
12Vsb ******** ******** --------
PWOK 50.00 0.01 0.71
Vin_Good ******** ******** --------
SMBAlert ******** ******** --------
Load Ref Load Td Td Td
Name No. Max Min (ms)
------------- ---------- -------- -------- ---------
12V 3 100.00 1.00 1.70
12Vsb 0 ******** ******** --------
PWOK 1 -100.00 -1.00 -1.70
Vin_Good 0 ******** ******** --------
SMBAlert 0 ******** ******** --------
STEP.183(UUT Test seq.183) : PS ON Delay time 80611(90V_47Hz_HH) ---- (0'96 PASS
Vin (V)= Refer to the previous item
Fin (Hz)= Refer to the previous item
On Phase Delay(ms)= Refer to the previous item
UUT Off Time (s)= Refer to the previous item
Loading (A/Ohm/V)= Refer to the previous item
Trigger: 1:Trig1R(AC), 2:Trig2R(PS on), 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:Trig1F(AC), 9:Trig2F(PS on),10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1
2 1
3 1
4 1
Load Start End VcmpA VcmpB
Name Trigger Trigger (V) (V)
------------- ------- ------- ------- -------
12V 9 5 11.590 12.810
12Vsb 9 9 11.400 12.600
PWOK 9 5 2.600 2.600
Vin_Good 9 9 2.600 2.600
SMBAlert 9 9 2.600 2.600
Load Ton Ton Ton
Name Max Min (ms)
------------- -------- -------- ---------
12V 400.00 5.00 62.24
12Vsb ******** ******** 0.17
PWOK ******** ******** 267.99
Vin_Good ******** ******** 0.17
SMBAlert ******** ******** 0.17
Load Ref Load Td Td Td
Name No. Max Min (ms)
------------- ---------- -------- -------- ---------
12V 3 -500.000 -100.000 -205.744
12Vsb 0 ********* ********* 0.167
PWOK 1 500.000 100.000 205.744
Vin_Good 0 ********* ********* 0.167
SMBAlert 0 ********* ********* 0.167
STEP.184(UUT Test seq.184) : Turn On Timing Test_Multi or Single(90V_47Hz_H PASS
ElaspedTime (S)= 2'121
Vin (V)= 90.00
Fin (Hz)= 47.00
On Phase Delay(ms)= 90.00
UUT Off Time (s)= 0.50
Trigger: 1:TTL1R, 2:TTL2R, 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:TTL1F, 9:TTL2F,10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1.00
2 1.00
3 1.00
4 1.00
Load Loading Start End VcmpA VcmpB
Name (A/Ohm/V) Trigger Trigger (V) (V)
------------- ---------- ------- ------- ------- -------
12V 71.300 5 6 1.220 11.590
12Vsb 2.500 5 6 1.200 10.800
PWOK 0.000 8 1 2.600 3.460
Vin_Good 0.000 8 1 2.600 3.460
SMBAlert 0.000 8 1 2.600 3.460
Load Ton Ton Ton
Name Max Min (ms)
------------- -------- -------- ---------
12V 70.00 5.00 51.25
12Vsb 70.00 1.00 11.88
PWOK ******** ******** 0.06
Vin_Good ******** ******** 0.06
SMBAlert ******** ******** 0.06
Load Ref Load Td Td Td
Name No. Max Min (ms)
------------- ------------- -------- -------- ---------
12V 0 ******** ******** 51.25
12Vsb 0 ******** ******** 11.88
PWOK 0 ******** ******** 0.06
Vin_Good 0 ******** ******** 0.06
SMBAlert 0 ******** ******** 0.06
STEP.185(UUT Test seq.185) : TTL & Relay Setup ---- (0'000) --------------- PASS
(The Report Format of this Sequence was not found)
STEP.186(UUT Test seq.186) : PS ON Delay time 80611(90V_47Hz_HH_Tpson_12V_R PASS
Vin (V)= Refer to the previous item
Fin (Hz)= Refer to the previous item
On Phase Delay(ms)= Refer to the previous item
UUT Off Time (s)= Refer to the previous item
Loading (A/Ohm/V)= Refer to the previous item
Trigger: 1:Trig1R(AC), 2:Trig2R(PS on), 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:Trig1F(AC), 9:Trig2F(PS on),10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1
2 1
3 1
4 1
Load Start End VcmpA VcmpB
Name Trigger Trigger (V) (V)
------------- ------- ------- ------- -------
12V 5 6 1.220 11.590
12Vsb 9 9 1.200 10.800
PWOK 9 9 2.600 2.600
Vin_Good 9 9 2.600 2.600
SMBAlert 9 9 2.600 2.600
Load Ton Ton Ton
Name Max Min (ms)
------------- -------- -------- ---------
12V 70.00 5.00 51.25
12Vsb ******** ******** 0.14
PWOK ******** ******** 0.14
Vin_Good ******** ******** 0.14
SMBAlert ******** ******** 0.14
Load Ref Load Td Td Td
Name No. Max Min (ms)
------------- ---------- -------- -------- ---------
12V 0 ********* ********* 51.254
12Vsb 0 ********* ********* 0.145
PWOK 0 ********* ********* 0.145
Vin_Good 0 ********* ********* 0.145
SMBAlert 0 ********* ********* 0.145
STEP.187(UUT Test seq.187) : Input Output Eff Noise Multi or Single(90V_47H PASS
ElapsedTime (S)= 1'888
Vin (V)= 90.00
Fin (Hz)= 47.00
Delay Time (ms)= 500.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 71.300 71.800 70.800 71.298
12Vsb 0.100 ******* ******* 0.100
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
-------Load---------------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V ???.??? ???.??? ???.???
12Vsb ???.??? ???.??? ???.???
PWOK ???.??? ???.??? ???.???
Vin_Good ???.??? ???.??? ???.???
SMBAlert ???.??? ???.??? ???.???
--------34970----------------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 12.810 11.590 12.220
12VSb 12.600 11.400 12.133
PWOK 3.460 2.500 3.241
Vin_Good 3.460 2.500 3.241
SMBAlert 3.460 2.500 3.218
IBUS ******* ******* 3.530
CR 0.400 ******* -0.007
Max Min Reading
------------- ---------- ---------- ----------
Vrms (V) ******** ******** 89.2317
PF 1.0000 ******** 0.9993
THDi (%) ******** * 3.1305
Irms (A) ******** ******** 11.2315
Pin (W) ******** ******** XXXXXXXX
Pout (W) ******** ******** 872.4798
Eff (%) ******** ******** 87.1183
Load Noise Range Noise B.W
Name (V) (MHz)
------------- ----------- ---------
12V 2 20.000
12Vsb 2 20.000
PWOK 2 20.000
Vin_Good 2 20.000
SMBAlert 2 20.000
Load Vpp Noise Vpp Noise Vpp Noise
Name Max(mV) Min(mV) (mV)
------------- ------------ ------------ ------------
12V 120.000 0.000 12.690
12Vsb 120.000 0.000 6.450
PWOK ********* ********* 26.800
Vin_Good ********* ********* 22.880
SMBAlert ********* ********* 29.740
STEP.188(UUT Test seq.188) : Cold Redundant Master Multi _S2 ---- (0'109) - PASS
(The Report Format of this Sequence was not found)
STEP.189(UUT Test seq.189) : Static ACDC 34970_or_Load_Multi or Single(90V_ PASS
ElapsedTime (S)= 1'264
Vin (V)= 90.00
Fin (Hz)= 47.00
Delay Time (ms)= 500.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 71.300 ******* ******* 71.298
12Vsb 2.500 ******* ******* 2.500
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 12.810 11.590 12.219
12VSb 12.600 11.400 12.002
PWOK 3.460 2.500 3.229
Vin_Good 3.460 2.500 3.236
SMBAlert 3.460 2.500 3.216
IBUS ******* ******* 3.530
CR 3.460 2.500 3.179
Max Min Reading
------------- --------- --------- ---------
Pout (W) ******* ******* 901.215
STEP.190(UUT Test seq.190) : Disable Cold Redundant Master Multi_S2 ---- (0 PASS
(The Report Format of this Sequence was not found)
STEP.191(UUT Test seq.191) : Static ACDC 34970_or_Load_Multi or Single(90V_ PASS
ElapsedTime (S)= 1'248
Vin (V)= 90.00
Fin (Hz)= 47.00
Delay Time (ms)= 500.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 71.300 ******* ******* 71.298
12Vsb 2.500 ******* ******* 2.500
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 12.810 11.590 12.219
12VSb 12.600 11.400 12.005
PWOK 3.460 2.500 3.238
Vin_Good 3.460 2.500 3.235
SMBAlert 3.460 2.500 3.218
IBUS ******* ******* 3.530
CR 0.400 ******* -0.009
Max Min Reading
------------- --------- --------- ---------
Pout (W) ******* ******* 901.169
STEP.192(UUT Test seq.192) : Input Output Eff Noise Multi or Single(90V_47H PASS
ElapsedTime (S)= 1'732
Vin (V)= 90.00
Fin (Hz)= 47.00
Delay Time (ms)= 500.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 71.300 ******* ******* 71.298
12Vsb 2.500 ******* ******* 2.500
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
-------Load---------------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V ???.??? ???.??? ???.???
12Vsb ???.??? ???.??? ???.???
PWOK ???.??? ???.??? ???.???
Vin_Good ???.??? ???.??? ???.???
SMBAlert ???.??? ???.??? ???.???
--------34970----------------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 12.810 11.590 12.219
12VSb 12.600 11.400 12.006
PWOK 3.460 2.500 3.235
Vin_Good 3.460 2.500 3.238
SMBAlert 3.460 2.500 3.222
IBUS ******* ******* 3.530
CR 0.400 ******* -0.009
Max Min Reading
------------- ---------- ---------- ----------
Vrms (V) ******** ******** 89.1952
PF 1.0000 ******** 0.9992
THDi (%) ******** * 3.3224
Irms (A) ******** ******** 11.6824
Pin (W) ******** ******** XXXXXXXX
Pout (W) ******** ******** 901.2234
Eff (%) ******** ******** 86.5585
Load Noise Range Noise B.W
Name (V) (MHz)
------------- ----------- ---------
12V 2 20.000
12Vsb 2 20.000
PWOK 2 20.000
Vin_Good 2 20.000
SMBAlert 2 20.000
Load Vpp Noise Vpp Noise Vpp Noise
Name Max(mV) Min(mV) (mV)
------------- ------------ ------------ ------------
12V 120.000 0.000 11.110
12Vsb 120.000 0.000 13.900
PWOK ********* ********* 28.260
Vin_Good ********* ********* 24.040
SMBAlert ********* ********* 30.110
STEP.193(UUT Test seq.193) : Select OCP Mode(OCP Mode) ---- (0'000) ------- PASS
Slect OCP Mode= 0 (OCP Mode=0 ; Static Mode=1)
STEP.194(UUT Test seq.194) : Over Load Protection 34970 or Load_Multi or Si PASS
ElapsedTime (S)= 5'523
Vin (V)= 90.00
Fin (Hz)= 47.00
Delay Time (ms)= 1500.00
Slect OCP Mode= 0 (OCP Mode=0 ; Static Mode=1)
Load Loading
Name (A/Ohm/V)
------------- ----------
12V 71.300
12Vsb 2.500
PWOK 0.000
Vin_Good 0.000
SMBAlert 0.000
Pre Load (%)= 111
Post Load (%)= 128
Load Vout_1 Vout_1 Vout_1
Name Max Min (V)
------------ ------- ------- -------
12V 12.810 11.590 12.213
12VSb 12.600 11.400 12.005
PWOK 3.460 2.500 3.232
Vin_Good 3.460 2.500 3.239
SMBAlert 3.460 2.500 3.216
IBUS ******* ******* 3.920
CR 0.400 ******* -0.010
Load Vout_2 Vout_2 Vout_2
Name Max Min (V)
------------ ------- ------- -------
12V 0.400 ******* 0.001
12VSb 12.600 11.400 12.017
PWOK 0.400 ******* 0.037
Vin_Good 3.460 2.500 3.244
SMBAlert 0.400 ******* 0.069
IBUS ******* ******* 0.001
CR 0.400 ******* 0.003
--------------OCP Mode-----------------
Vin (V)= 90.00
Fin (Hz)= 47.00
Delay Time (ms)= 1500.00
UUT Off Time (s)= 0.00
Step Time (ms)= 51.00
Volp (V)= 10.000
OLP Test Channel= 1
UUT Type = 1 (0:Auto Recovery, 1:Power Off Reset)
Recovery Time Out (ms)= 100.00
Load Loading
Name (A/Ohm/V)
------------- ----------
12V 71.3000
12Vsb 2.5000
PWOK 0.0000
Vin_Good 0.0000
SMBAlert 0.0000
Loading Loading Loading
Start(%) End(%) Step
------------- ---------- ----------
110.0000 135.0000 1.0000
Max Min Reading
-------------------- ---------- ---------- ----------
OLP Trip Point (%) 130.0000 110.0000 121.2202
Reading
-------------------- ----------
OLP Trip Point (A) 86.4300
STEP.195(UUT Test seq.195) : I2C Read Status OR Multi_S6(90V-OCP2) ---- (0' PASS
Command Page00 :060200
Command Page01 :060201
Status Word :79
Status Byte :78
Status VOUT :7A
Status IOUT :7B
Status INPUT :7C
Status TEMPERATURE :7D
Status CML :7E
Status FANS :81
---------------------------------
Word SPEC: 20584
Word SPEC: 20584
Word SPEC: 20584
Word SPEC: 20584
Word SPEC: 20584
Word SPEC: 20584
Word SPEC: 20584
Word SPEC: 20584
Word SPEC_Page1: 20584
Word SPEC_Page1: 20584
Word SPEC_Page1: 20584
Word SPEC_Page1: 20584
Word SPEC_Page1: 20584
Word SPEC_Page1: 20584
Word SPEC_Page1: 20584
Word SPEC_Page1: 20584
Byte SPEC : 80
Byte SPEC : 80
Byte SPEC : 80
Byte SPEC : 80
Byte SPEC : 80
Byte SPEC : 80
Byte SPEC : 80
Byte SPEC : 80
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
Iout SPEC : 163
Iout SPEC : 163
Iout SPEC : 163
Iout SPEC : 163
Iout SPEC : 163
Iout SPEC : 163
Iout SPEC : 163
Iout SPEC : 163
Input SPEC : 7
Input SPEC : 7
Input SPEC : 7
Input SPEC : 7
Input SPEC : 7
Input SPEC : 7
Input SPEC : 7
Input SPEC : 7
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
CML SPEC : 128
CML SPEC : 128
CML SPEC : 128
CML SPEC : 128
CML SPEC : 128
CML SPEC : 128
CML SPEC : 128
CML SPEC : 128
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
Word Page0 OR : 0020
Word Page1 OR : 0020
Byte OR : 00
Input OR : 07
IOUT OR : 00
TEMP OR : 00
CML OR : 80
----------------------------------
Word_Page_00 : 20584
Word_Page_01 : 20584
Status_Byte_P00 : 80
Status_Byte_P01 : 80
Status_VOUT_P00 : 0
Status_VOUT_P01 : 0
Status_IOUT_P00 : 163
Status_IOUT_P01 : 163
Status_INPUT_P00 : 7
Status_INPUT_P01 : 7
Status_TEM_P00 : 0
Status_TEM_P01 : 0
Status_CML_P00 : 128
Status_CML_P01 : 128
Status_FANS_P00 : 0
Status_FANS_P01 : 0
STEP.196(UUT Test seq.196) : Static ACDC 34970_or_Load_Multi or Single(90V- PASS
ElapsedTime (S)= 0'796
Vin (V)= 90.00
Fin (Hz)= 47.00
Delay Time (ms)= 100.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 71.300 ******* ******* 0.000
12Vsb 2.500 ******* ******* 2.500
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 0.400 ******* 0.001
12VSb 12.600 11.400 12.016
PWOK 0.400 ******* 0.037
Vin_Good 3.460 2.500 3.239
SMBAlert 0.400 ******* 0.069
IBUS ******* ******* -0.006
CR 0.400 ******* 0.003
Max Min Reading
------------- --------- --------- ---------
Pout (W) ******* ******* 30.037
STEP.197(UUT Test seq.197) : TTL & Relay Setup(PS OnOff) ---- (1'045) ----- PASS
(The Report Format of this Sequence was not found)
STEP.198(UUT Test seq.198) : Static ACDC 34970_or_Load_Multi or Single(90V- PASS
ElapsedTime (S)= 1'014
Vin (V)= 90.00
Fin (Hz)= 47.00
Delay Time (ms)= 100.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 71.300 ******* ******* 71.298
12Vsb 2.500 ******* ******* 2.500
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 12.810 11.590 12.218
12VSb 12.600 11.400 12.006
PWOK 3.460 2.500 3.236
Vin_Good 3.460 2.500 3.240
SMBAlert 3.460 2.500 3.216
IBUS ******* ******* 3.531
CR 0.400 ******* -0.009
Max Min Reading
------------- --------- --------- ---------
Pout (W) ******* ******* 901.117
STEP.199(UUT Test seq.199) : I2C Read Status Multi_S6(90V-OCP2_Recover Chec PASS
Adderss :B0
Command Page00 :060200
Command Page01 :060201
Status Word :79
Status Byte :78
Status VOUT :7A
Status IOUT :7B
Status INPUT :7C
Status TEMPERATURE :7D
Status CML :7E
Status FANS :81
---------------------------------
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
----------------------------------
Word_Page_00 : 0
Word_Page_01 : 0
Status_Byte_P00 : 0
Status_Byte_P01 : 0
Status_VOUT_P00 : 0
Status_VOUT_P01 : 0
Status_IOUT_P00 : 0
Status_IOUT_P01 : 0
Status_INPUT_P00 : 0
Status_INPUT_P01 : 0
Status_TEM_P00 : 0
Status_TEM_P01 : 0
Status_CML_P00 : 0
Status_CML_P01 : 0
Status_FANS_P00 : 0
Status_FANS_P01 : 0
STEP.200(UUT Test seq.200) : Hold Up Timing Test_Multi or Single(90V_47Hz_7 PASS
ElapsedTime (S)= 0'873
Vin (V)= 90.00
Fin (Hz)= 47.00
Delay Time (ms)= 200.00
On Phase Delay(ms)= 90.00
UUT Off Time (s)= 0.00
Trigger: 1:Trig1R(AC), 2:Trig2R(PS on), 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:Trig1F(AC), 9:Trig2F(PS on),10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1
2 1
3 1
4 1
Load Loading Start End VcmpA VcmpB
Name (A/Ohm/V) Trigger Trigger (V) (V)
------------- ---------- ------- ------- ------- -------
12V 49.910 8 12 11.590 12.810
12Vsb 1.750 8 12 11.400 12.600
PWOK 0.000 8 12 2.600 3.460
Vin_Good 0.000 8 12 2.600 3.460
SMBAlert 0.000 8 1 2.600 3.460
Load Tholdup Tholdup Tholdup
Name Max Min (ms)
------------- -------- -------- ---------
12V 1000.00 10.00 36.42
12Vsb 1000.00 70.00 78.58
PWOK 300.00 9.00 34.70
Vin_Good 4.00 0.01 2.77
SMBAlert ******** ******** 0.06
Load Ref Load Tholdup Tholdup Tholdup
Name No. Max Min (ms)
------------- ---------- -------- -------- ---------
12V 3 100.00 1.00 1.73
12Vsb 0 ******** ******** 78.58
PWOK 1 -100.00 -1.00 -1.73
Vin_Good 0 ******** ******** 2.77
SMBAlert 0 ******** ******** 0.06
STEP.201(UUT Test seq.201) : FAN Full Speed delay time Multi ---- (8'096) - PASS
STEP.202(UUT Test seq.202) : FAN Speed Normal_Multi ---- (0'094) ---------- PASS
(The Report Format of this Sequence was not found)
STEP.203(UUT Test seq.203) : Turn On Timing Test_Multi or Single(100V_60Hz_ PASS
ElaspedTime (S)= 2'090
Vin (V)= 100.00
Fin (Hz)= 60.00
On Phase Delay(ms)= 90.00
UUT Off Time (s)= 0.00
Trigger: 1:TTL1R, 2:TTL2R, 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:TTL1F, 9:TTL2F,10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1.00
2 1.00
3 1.00
4 1.00
Load Loading Start End VcmpA VcmpB
Name (A/Ohm/V) Trigger Trigger (V) (V)
------------- ---------- ------- ------- ------- -------
12V 79.500 8 5 11.590 12.810
12Vsb 2.500 8 5 11.400 12.600
PWOK 0.000 8 5 2.600 3.460
Vin_Good 0.000 8 1 2.600 3.460
SMBAlert 0.000 8 1 2.600 3.460
Load Ton Ton Ton
Name Max Min (ms)
------------- -------- -------- ---------
12V 3000.00 1.00 1256.65
12Vsb 1500.00 1.00 1011.40
PWOK ******** ******** 1462.48
Vin_Good ******** ******** 0.06
SMBAlert ******** ******** 0.06
Load Ref Load Td Td Td
Name No. Max Min (ms)
------------- ------------- -------- -------- ---------
12V 3 -500.00 -100.00 -205.83
12Vsb 1 -1500.00 -50.00 -245.25
PWOK 1 500.00 100.00 205.83
Vin_Good 0 ******** ******** 0.06
SMBAlert 0 ******** ******** 0.06
STEP.204(UUT Test seq.204) : I2C Read Status Multi_S6(100V_60Hz_HH) ---- (0 PASS
Adderss :B0
Command Page00 :060200
Command Page01 :060201
Status Word :79
Status Byte :78
Status VOUT :7A
Status IOUT :7B
Status INPUT :7C
Status TEMPERATURE :7D
Status CML :7E
Status FANS :81
---------------------------------
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
----------------------------------
Word_Page_00 : 0
Word_Page_01 : 0
Status_Byte_P00 : 0
Status_Byte_P01 : 0
Status_VOUT_P00 : 0
Status_VOUT_P01 : 0
Status_IOUT_P00 : 0
Status_IOUT_P01 : 0
Status_INPUT_P00 : 0
Status_INPUT_P01 : 0
Status_TEM_P00 : 0
Status_TEM_P01 : 0
Status_CML_P00 : 0
Status_CML_P01 : 0
Status_FANS_P00 : 0
Status_FANS_P01 : 0
STEP.205(UUT Test seq.205) : PS OFF Time 80611(100V_60Hz_HH) ---- (1'638) - PASS
Vin (V)= Refer to the previous item
Fin (Hz)= Refer to the previous item
On Phase Delay(ms)= Refer to the previous item
UUT Off Time (s)= Refer to the previous item
Loading (A/Ohm/V)= Refer to the previous item
Trigger: 1:Trig1R(AC), 2:Trig2R(PS on), 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:Trig1F(AC), 9:Trig2F(PS on),10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1
2 1
3 1
4 1
Load Start End VcmpA VcmpB
Name Trigger Trigger (V) (V)
------------- ------- ------- ------- -------
12V 2 12 11.590 12.810
12Vsb 2 2 11.400 12.600
PWOK 2 12 2.600 2.600
Vin_Good 2 2 2.600 2.600
SMBAlert 2 2 2.600 2.600
Load Ton Ton Ton
Name Max Min (ms)
------------- -------- -------- ---------
12V ******** ******** 2.33
12Vsb ******** ******** --------
PWOK 50.00 0.01 0.64
Vin_Good ******** ******** --------
SMBAlert ******** ******** --------
Load Ref Load Td Td Td
Name No. Max Min (ms)
------------- ---------- -------- -------- ---------
12V 3 100.00 1.00 1.69
12Vsb 0 ******** ******** --------
PWOK 1 -100.00 -1.00 -1.69
Vin_Good 0 ******** ******** --------
SMBAlert 0 ******** ******** --------
STEP.206(UUT Test seq.206) : PS ON Delay time 80611(100V_60Hz_HH) ---- (0'9 PASS
Vin (V)= Refer to the previous item
Fin (Hz)= Refer to the previous item
On Phase Delay(ms)= Refer to the previous item
UUT Off Time (s)= Refer to the previous item
Loading (A/Ohm/V)= Refer to the previous item
Trigger: 1:Trig1R(AC), 2:Trig2R(PS on), 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:Trig1F(AC), 9:Trig2F(PS on),10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1
2 1
3 1
4 1
Load Start End VcmpA VcmpB
Name Trigger Trigger (V) (V)
------------- ------- ------- ------- -------
12V 9 5 11.590 12.810
12Vsb 9 9 11.400 12.600
PWOK 9 5 2.600 2.600
Vin_Good 9 9 2.600 2.600
SMBAlert 9 9 2.600 2.600
Load Ton Ton Ton
Name Max Min (ms)
------------- -------- -------- ---------
12V 400.00 5.00 62.41
12Vsb ******** ******** 0.15
PWOK ******** ******** 268.18
Vin_Good ******** ******** 0.15
SMBAlert ******** ******** 0.15
Load Ref Load Td Td Td
Name No. Max Min (ms)
------------- ---------- -------- -------- ---------
12V 3 -500.000 -100.000 -205.774
12Vsb 0 ********* ********* 0.154
PWOK 1 500.000 100.000 205.774
Vin_Good 0 ********* ********* 0.154
SMBAlert 0 ********* ********* 0.154
STEP.207(UUT Test seq.207) : Turn On Timing Test_Multi or Single(100V_60Hz_ PASS
ElaspedTime (S)= 2'137
Vin (V)= 100.00
Fin (Hz)= 60.00
On Phase Delay(ms)= 90.00
UUT Off Time (s)= 0.50
Trigger: 1:TTL1R, 2:TTL2R, 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:TTL1F, 9:TTL2F,10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1.00
2 1.00
3 1.00
4 1.00
Load Loading Start End VcmpA VcmpB
Name (A/Ohm/V) Trigger Trigger (V) (V)
------------- ---------- ------- ------- ------- -------
12V 79.500 5 6 1.220 11.590
12Vsb 2.500 5 6 1.200 10.800
PWOK 0.000 8 1 2.600 3.460
Vin_Good 0.000 8 1 2.600 3.460
SMBAlert 0.000 8 1 2.600 3.460
Load Ton Ton Ton
Name Max Min (ms)
------------- -------- -------- ---------
12V 70.00 5.00 51.27
12Vsb 70.00 1.00 11.89
PWOK ******** ******** 0.06
Vin_Good ******** ******** 0.06
SMBAlert ******** ******** 0.06
Load Ref Load Td Td Td
Name No. Max Min (ms)
------------- ------------- -------- -------- ---------
12V 0 ******** ******** 51.27
12Vsb 0 ******** ******** 11.89
PWOK 0 ******** ******** 0.06
Vin_Good 0 ******** ******** 0.06
SMBAlert 0 ******** ******** 0.06
STEP.208(UUT Test seq.208) : TTL & Relay Setup ---- (0'016) --------------- PASS
(The Report Format of this Sequence was not found)
STEP.209(UUT Test seq.209) : PS ON Delay time 80611(100V_60Hz_HH_Tpson_12V_ PASS
Vin (V)= Refer to the previous item
Fin (Hz)= Refer to the previous item
On Phase Delay(ms)= Refer to the previous item
UUT Off Time (s)= Refer to the previous item
Loading (A/Ohm/V)= Refer to the previous item
Trigger: 1:Trig1R(AC), 2:Trig2R(PS on), 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:Trig1F(AC), 9:Trig2F(PS on),10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1
2 1
3 1
4 1
Load Start End VcmpA VcmpB
Name Trigger Trigger (V) (V)
------------- ------- ------- ------- -------
12V 5 6 1.220 11.590
12Vsb 9 2 1.200 10.800
PWOK 9 2 2.600 2.600
Vin_Good 9 2 2.600 2.600
SMBAlert 9 2 2.600 2.600
Load Ton Ton Ton
Name Max Min (ms)
------------- -------- -------- ---------
12V 70.00 5.00 51.25
12Vsb ******** ******** 0.10
PWOK ******** ******** 0.10
Vin_Good ******** ******** 0.10
SMBAlert ******** ******** 0.10
Load Ref Load Td Td Td
Name No. Max Min (ms)
------------- ---------- -------- -------- ---------
12V 0 ********* ********* 51.252
12Vsb 0 ********* ********* 0.097
PWOK 0 ********* ********* 0.097
Vin_Good 0 ********* ********* 0.097
SMBAlert 0 ********* ********* 0.097
STEP.210(UUT Test seq.210) : Input Output Eff Noise Multi or Single(100V_60 PASS
ElapsedTime (S)= 1'576
Vin (V)= 100.00
Fin (Hz)= 60.00
Delay Time (ms)= 300.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 79.500 ******* ******* 79.498
12Vsb 0.100 ******* ******* 0.100
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
-------Load---------------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V ???.??? ???.??? ???.???
12Vsb ???.??? ???.??? ???.???
PWOK ???.??? ???.??? ???.???
Vin_Good ???.??? ???.??? ???.???
SMBAlert ???.??? ???.??? ???.???
--------34970----------------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 12.810 11.590 12.210
12VSb 12.600 11.400 12.132
PWOK 3.460 2.500 3.240
Vin_Good 3.460 2.500 3.234
SMBAlert 3.460 2.500 3.220
IBUS ******* ******* 3.933
CR 0.400 ******* -0.009
Max Min Reading
------------- ---------- ---------- ----------
Vrms (V) ******** ******** 99.1760
PF 1.0000 ******** 0.9994
THDi (%) ******** * 2.7033
Irms (A) ******** ******** 11.1664
Pin (W) ******** ******** XXXXXXXX
Pout (W) ******** ******** 971.9199
Eff (%) ******** ******** 87.8127
Load Noise Range Noise B.W
Name (V) (MHz)
------------- ----------- ---------
12V 2 20.000
12Vsb 2 20.000
PWOK 2 20.000
Vin_Good 2 20.000
SMBAlert 2 20.000
Load Vpp Noise Vpp Noise Vpp Noise
Name Max(mV) Min(mV) (mV)
------------- ------------ ------------ ------------
12V 120.000 0.000 12.390
12Vsb 120.000 0.000 6.690
PWOK ********* ********* 26.130
Vin_Good ********* ********* 23.040
SMBAlert ********* ********* 28.990
STEP.211(UUT Test seq.211) : Static ACDC 34970_or_Load_Multi or Single(100V PASS
ElapsedTime (S)= 1'216
Vin (V)= 100.00
Fin (Hz)= 60.00
Delay Time (ms)= 500.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 79.500 ******* ******* 79.498
12Vsb 2.750 ******* ******* 2.750
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 12.810 11.590 12.214
12VSb 12.600 11.400 11.994
PWOK 3.460 2.500 3.235
Vin_Good 3.460 2.500 3.237
SMBAlert 3.460 2.500 3.216
IBUS ******* ******* 3.933
CR 0.400 ******* -0.010
Max Min Reading
------------- --------- --------- ---------
Pout (W) ******* ******* XXXXXXX
STEP.212(UUT Test seq.212) : Static ACDC 34970_or_Load_Multi or Single(100V PASS
ElapsedTime (S)= 1'388
Vin (V)= 100.00
Fin (Hz)= 60.00
Delay Time (ms)= 500.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 79.500 ******* ******* 0.000
12Vsb 3.650 ******* ******* 0.010
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 0.400 ******* 0.001
12VSb 12.600 ******* 11.976
PWOK 0.400 ******* 0.038
Vin_Good 3.460 2.400 3.244
SMBAlert 3.460 ******* 3.218
IBUS ******* ******* 0.161
CR 0.400 ******* 0.004
Max Min Reading
------------- --------- --------- ---------
Pout (W) ******* ******* 0.123
STEP.213(UUT Test seq.213) : Static ACDC 34970_or_Load_Multi or Single(100V PASS
ElapsedTime (S)= 1'857
Vin (V)= 100.00
Fin (Hz)= 60.00
Delay Time (ms)= 1000.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 79.500 ******* ******* 79.498
12Vsb 2.750 ******* ******* 2.750
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 12.810 11.590 12.199
12VSb 12.600 11.400 11.994
PWOK 3.460 2.500 3.238
Vin_Good 3.460 2.500 3.237
SMBAlert 3.460 2.500 3.218
IBUS ******* ******* 3.933
CR 0.400 ******* -0.010
Max Min Reading
------------- --------- --------- ---------
Pout (W) ******* ******* XXXXXXX
STEP.214(UUT Test seq.214) : Cold Redundant Master Multi _S2 ---- (0'094) - PASS
(The Report Format of this Sequence was not found)
STEP.215(UUT Test seq.215) : Static ACDC 34970_or_Load_Multi or Single(100V PASS
ElapsedTime (S)= 1'233
Vin (V)= 100.00
Fin (Hz)= 60.00
Delay Time (ms)= 500.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 79.500 ******* ******* 79.498
12Vsb 2.500 ******* ******* 2.500
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 12.810 11.590 12.216
12VSb 12.600 11.400 12.005
PWOK 3.460 2.500 3.228
Vin_Good 3.460 2.500 3.235
SMBAlert 3.460 2.500 3.217
IBUS ******* ******* 3.934
CR 3.460 2.500 3.178
Max Min Reading
------------- --------- --------- ---------
Pout (W) ******* ******* XXXXXXX
STEP.216(UUT Test seq.216) : Disable Cold Redundant Master Multi_S2 ---- (0 PASS
(The Report Format of this Sequence was not found)
STEP.217(UUT Test seq.217) : Static ACDC 34970_or_Load_Multi or Single(100V PASS
ElapsedTime (S)= 1'279
Vin (V)= 100.00
Fin (Hz)= 60.00
Delay Time (ms)= 500.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 79.500 ******* ******* 79.498
12Vsb 2.500 ******* ******* 2.500
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 12.810 11.590 12.214
12VSb 12.600 11.400 12.005
PWOK 3.460 2.500 3.236
Vin_Good 3.460 2.500 3.233
SMBAlert 3.460 2.500 3.222
IBUS ******* ******* 3.934
CR 0.400 ******* -0.010
Max Min Reading
------------- --------- --------- ---------
Pout (W) ******* ******* XXXXXXX
STEP.218(UUT Test seq.218) : Input Output Eff Noise Multi or Single(HH) --- PASS
ElapsedTime (S)= 1'545
Vin (V)= 100.00
Fin (Hz)= 60.00
Delay Time (ms)= 300.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 79.500 ******* ******* 79.498
12Vsb 2.500 ******* ******* 2.500
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
-------Load---------------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V ???.??? ???.??? ???.???
12Vsb ???.??? ???.??? ???.???
PWOK ???.??? ???.??? ???.???
Vin_Good ???.??? ???.??? ???.???
SMBAlert ???.??? ???.??? ???.???
--------34970----------------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 12.810 11.590 12.214
12VSb 12.600 11.400 12.005
PWOK 3.460 2.500 3.232
Vin_Good 3.460 2.500 3.236
SMBAlert 3.460 2.500 3.221
IBUS ******* ******* 3.934
CR 0.400 ******* -0.010
Max Min Reading
------------- ---------- ---------- ----------
Vrms (V) ******** ******** 99.1522
PF 1.0000 ******** 0.9994
THDi (%) ******** * 2.7271
Irms (A) 13.0000 ******** 11.5624
Pin (W) ******** ******** XXXXXXXX
Pout (W) ******** ******** XXXXXXXX
Eff (%) ******** ******** 87.3680
Load Noise Range Noise B.W
Name (V) (MHz)
------------- ----------- ---------
12V 2 20.000
12Vsb 2 20.000
PWOK 2 20.000
Vin_Good 2 20.000
SMBAlert 2 20.000
Load Vpp Noise Vpp Noise Vpp Noise
Name Max(mV) Min(mV) (mV)
------------- ------------ ------------ ------------
12V 120.000 0.000 12.530
12Vsb 120.000 0.000 14.020
PWOK ********* ********* 27.650
Vin_Good ********* ********* 24.460
SMBAlert ********* ********* 29.550
STEP.219(UUT Test seq.219) : Static ACDC 34970_or_Load_Multi or Single(110V PASS
ElapsedTime (S)= 3'776
Vin (V)= 110.00
Fin (Hz)= 60.00
Delay Time (ms)= 3000.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 91.425 ******* ******* 91.423
12Vsb 2.500 ******* ******* 2.500
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 12.810 11.590 12.209
12VSb 12.600 11.400 12.002
PWOK 3.460 2.500 3.236
Vin_Good 3.460 2.500 3.230
SMBAlert 3.460 ******* 0.056
IBUS ******* ******* 4.510
CR 0.400 ******* -0.012
Max Min Reading
------------- --------- --------- ---------
Pout (W) ******* ******* XXXXXXX
STEP.220(UUT Test seq.220) : TTL & Relay Setup(PS OnOff) ---- (1'030) ----- PASS
(The Report Format of this Sequence was not found)
STEP.221(UUT Test seq.221) : Peak_Load_S3_Multi_S(110V-OCP1_HL_Delay time 5 PASS
ElapsedTime (S)= 8'534
Vin (V)= Refer to the previous item
Fin (Hz)= Refer to the previous item
Delay Time (ms)= 2000.00
Load Setting Time (ms)= 2000.00
Measurement Delay Time (ms)= 3000.00
Turn On Delay Time (ms)= 3000.00
Loading Loading
Name (A/Ohm/V)
------------- ----------
12V 79.500
12Vsb 0.100
PWOK 0.000
Vin_Good 0.000
SMBAlert 0.000
12V_Loading_level Dell_Time Rise Rate Fall Rate
(A) (ms) (A/us) (A/us)
------------------ --------- --------- ---------
50.000 500.000 2.5000 2.5000
79.500 500.000 2.5000 2.5000
97.785 50.200 2.5000 2.5000
79.500 500.000 2.5000 2.5000
Load Vpk Max Vpk Min Vpk High Vpk Low
Name (V) (V) (V) (V)
------------- --------- --------- --------- ---------
12V 12.810 11.590 12.254 12.188
12Vsb 12.600 11.400 12.152 12.143
PWOK 3.460 2.500 3.270 3.273
Vin_Good 3.460 2.500 3.266 3.263
SMBAlert 3.460 ********* 0.098 0.093
STEP.222(UUT Test seq.222) : Peak_Load_S3_Multi_S(110V-OCP1_HH_Delay time 5 PASS
ElapsedTime (S)= 8'502
Vin (V)= Refer to the previous item
Fin (Hz)= Refer to the previous item
Delay Time (ms)= 2000.00
Load Setting Time (ms)= 2000.00
Measurement Delay Time (ms)= 3000.00
Turn On Delay Time (ms)= 3000.00
Loading Loading
Name (A/Ohm/V)
------------- ----------
12V 79.500
12Vsb 2.500
PWOK 0.000
Vin_Good 0.000
SMBAlert 0.000
12V_Loading_level Dell_Time Rise Rate Fall Rate
(A) (ms) (A/us) (A/us)
------------------ --------- --------- ---------
50.000 500.000 2.5000 2.5000
79.500 500.000 2.5000 2.5000
97.785 50.200 2.5000 2.5000
79.500 500.000 2.5000 2.5000
Load Vpk Max Vpk Min Vpk High Vpk Low
Name (V) (V) (V) (V)
------------- --------- --------- --------- ---------
12V 12.810 11.590 12.254 12.190
12Vsb 12.600 11.400 12.034 12.016
PWOK 3.460 2.500 3.268 3.272
Vin_Good 3.460 2.500 3.263 3.261
SMBAlert 3.460 ********* 0.098 0.092
STEP.223(UUT Test seq.223) : Peak_Load_S3_Multi_S(110V-OCP2_HL_Delay time 0 PASS
ElapsedTime (S)= 8'486
Vin (V)= Refer to the previous item
Fin (Hz)= Refer to the previous item
Delay Time (ms)= 2000.00
Load Setting Time (ms)= 2000.00
Measurement Delay Time (ms)= 3000.00
Turn On Delay Time (ms)= 3000.00
Loading Loading
Name (A/Ohm/V)
------------- ----------
12V 79.500
12Vsb 0.100
PWOK 0.000
Vin_Good 0.000
SMBAlert 0.000
12V_Loading_level Dell_Time Rise Rate Fall Rate
(A) (ms) (A/us) (A/us)
------------------ --------- --------- ---------
50.000 500.000 2.5000 2.5000
79.500 500.000 2.5000 2.5000
109.710 0.120 2.5000 2.5000
79.500 500.000 2.5000 2.5000
Load Vpk Max Vpk Min Vpk High Vpk Low
Name (V) (V) (V) (V)
------------- --------- --------- --------- ---------
12V 12.960 11.000 12.251 12.168
12Vsb 12.600 11.400 12.150 12.143
PWOK 3.460 2.500 3.270 3.274
Vin_Good 3.460 2.500 3.266 3.263
SMBAlert 3.460 ********* 0.106 0.089
STEP.224(UUT Test seq.224) : Peak_Load_S3_Multi_S(110V-OCP2_HH_Delay time 0 PASS
ElapsedTime (S)= 8'471
Vin (V)= Refer to the previous item
Fin (Hz)= Refer to the previous item
Delay Time (ms)= 2000.00
Load Setting Time (ms)= 2000.00
Measurement Delay Time (ms)= 3000.00
Turn On Delay Time (ms)= 3000.00
Loading Loading
Name (A/Ohm/V)
------------- ----------
12V 79.500
12Vsb 2.500
PWOK 0.000
Vin_Good 0.000
SMBAlert 0.000
12V_Loading_level Dell_Time Rise Rate Fall Rate
(A) (ms) (A/us) (A/us)
------------------ --------- --------- ---------
50.000 500.000 2.5000 2.5000
79.500 500.000 2.5000 2.5000
109.710 0.120 2.5000 2.5000
79.500 500.000 2.5000 2.5000
Load Vpk Max Vpk Min Vpk High Vpk Low
Name (V) (V) (V) (V)
------------- --------- --------- --------- ---------
12V 12.960 11.000 12.251 12.168
12Vsb 12.600 11.400 12.034 12.017
PWOK 3.460 2.500 3.268 3.273
Vin_Good 3.460 2.500 3.263 3.263
SMBAlert 3.460 ********* 0.102 0.090
STEP.225(UUT Test seq.225) : Set Input Condition Multi_S4_4(110V_60Hz) ---- PASS
Input Voltage Type (Vac=0 ; Vdc=1) = 0
Vin = 110.000
Fin = 60.000
Vin_DC_Positive_Negative(Positive=0 ; Negative=1) = 0
STEP.226(UUT Test seq.226) : Set Dynamic_Time ---- (0'000) ---------------- PASS
ElapsedTime (S)= 0'000
Delay Time (ms)= 3000.00
Measurement Time (ms) = 1000.00
UUT Off Time (s)= 3.00
STEP.227(UUT Test seq.227) : SetAllLoad_SlewRate_S ---- (0'093) ----------- PASS
STEP.228(UUT Test seq.228) : Sync_Dynamic_80611_20200716_Multi_S(110V-OCP_1 PASS
ElapsedTime (S)= 4'867
Vin (V)= Refer to previous item
Fin (Hz)= Refer to previous item
Duration-1 (ms)= 100.0000
Duration-2 (ms) = 50.2000
Load Loading-1 Loading-2 Vstable+ Vstable-
Name (A) (A) (V) (V)
------------- --------- --------- --------- ---------
12V 1.000 1.000 -------- --------
12Vsb 2.750 3.650 -------- --------
PWOK 0.000 0.000 -------- --------
Vin_Good 0.000 0.000 -------- --------
SMBAlert 0.000 0.000 -------- --------
Load Vpk+ Max Vpk+ Min Vpk High Vpk- Max Vpk- Min Vpk Low
Name (V) (V) (V) (V) (V) (V)
------------- --------- --------- --------- --------- --------- ---------
12V 12.810 11.590 12.274 12.810 11.590 12.261
12Vsb 12.600 11.400 12.025 12.600 11.400 12.007
PWOK 3.460 2.500 3.271 3.460 2.500 3.288
Vin_Good 3.460 2.500 3.266 3.460 2.500 3.275
SMBAlert 3.460 2.500 3.249 3.460 2.500 3.253
Load Vspk+ Max Vspk+ Min Vspk High Vspk- Max Vspk- Min Vspk Low
Name (V) (V) (mV) (V) (V) (mV)
------------- ---------- ---------- ---------- ---------- ---------- ----------
12V ******** ******** -------- ******** ******** --------
12Vsb ******** ******** -------- ******** ******** --------
PWOK ******** ******** -------- ******** ******** --------
Vin_Good ******** ******** -------- ******** ******** --------
SMBAlert ******** ******** -------- ******** ******** --------
STEP.229(UUT Test seq.229) : Sync_Dynamic_80611_20200716_Multi_S(110V-OCP_1 PASS
ElapsedTime (S)= 4'821
Vin (V)= Refer to previous item
Fin (Hz)= Refer to previous item
Duration-1 (ms)= 100.0000
Duration-2 (ms) = 50.2000
Load Loading-1 Loading-2 Vstable+ Vstable-
Name (A) (A) (V) (V)
------------- --------- --------- --------- ---------
12V 79.500 79.500 -------- --------
12Vsb 2.750 3.650 -------- --------
PWOK 0.000 0.000 -------- --------
Vin_Good 0.000 0.000 -------- --------
SMBAlert 0.000 0.000 -------- --------
Load Vpk+ Max Vpk+ Min Vpk High Vpk- Max Vpk- Min Vpk Low
Name (V) (V) (V) (V) (V) (V)
------------- --------- --------- --------- --------- --------- ---------
12V 12.810 11.590 12.228 12.810 11.590 12.214
12Vsb 12.600 11.400 12.022 12.600 11.400 11.998
PWOK 3.460 2.500 3.260 3.460 2.500 3.277
Vin_Good 3.460 2.500 3.253 3.460 2.500 3.267
SMBAlert 3.460 2.500 3.253 3.460 2.500 3.259
Load Vspk+ Max Vspk+ Min Vspk High Vspk- Max Vspk- Min Vspk Low
Name (V) (V) (mV) (V) (V) (mV)
------------- ---------- ---------- ---------- ---------- ---------- ----------
12V ******** ******** -------- ******** ******** --------
12Vsb ******** ******** -------- ******** ******** --------
PWOK ******** ******** -------- ******** ******** --------
Vin_Good ******** ******** -------- ******** ******** --------
SMBAlert ******** ******** -------- ******** ******** --------
STEP.230(UUT Test seq.230) : Hold Up Timing Test_Multi or Single(100V_60Hz_ PASS
ElapsedTime (S)= 0'920
Vin (V)= 100.00
Fin (Hz)= 60.00
Delay Time (ms)= 200.00
On Phase Delay(ms)= 90.00
UUT Off Time (s)= 0.00
Trigger: 1:Trig1R(AC), 2:Trig2R(PS on), 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:Trig1F(AC), 9:Trig2F(PS on),10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1
2 1
3 1
4 1
Load Loading Start End VcmpA VcmpB
Name (A/Ohm/V) Trigger Trigger (V) (V)
------------- ---------- ------- ------- ------- -------
12V 55.650 8 12 11.590 12.810
12Vsb 1.750 8 12 11.400 12.600
PWOK 0.000 8 12 2.600 3.460
Vin_Good 0.000 8 12 2.600 3.460
SMBAlert 0.000 8 1 2.600 3.460
Load Tholdup Tholdup Tholdup
Name Max Min (ms)
------------- -------- -------- ---------
12V 1000.00 10.00 33.23
12Vsb 1000.00 70.00 78.20
PWOK 300.00 9.00 31.55
Vin_Good 4.00 0.01 2.62
SMBAlert ******** ******** 0.06
Load Ref Load Tholdup Tholdup Tholdup
Name No. Max Min (ms)
------------- ---------- -------- -------- ---------
12V 3 100.00 1.00 1.68
12Vsb 0 ******** ******** 78.20
PWOK 1 -100.00 -1.00 -1.68
Vin_Good 0 ******** ******** 2.62
SMBAlert 0 ******** ******** 0.06
STEP.231(UUT Test seq.231) : FAN Full Speed delay time Multi ---- (8'096) - PASS
STEP.232(UUT Test seq.232) : FAN Speed Normal_Multi ---- (0'093) ---------- PASS
(The Report Format of this Sequence was not found)
STEP.233(UUT Test seq.233) : Turn On Timing Test_Multi or Single(180V_47Hz_ PASS
ElaspedTime (S)= 1'887
Vin (V)= 180.00
Fin (Hz)= 47.00
On Phase Delay(ms)= 90.00
UUT Off Time (s)= 0.00
Trigger: 1:TTL1R, 2:TTL2R, 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:TTL1F, 9:TTL2F,10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1.00
2 1.00
3 1.00
4 1.00
Load Loading Start End VcmpA VcmpB
Name (A/Ohm/V) Trigger Trigger (V) (V)
------------- ---------- ------- ------- ------- -------
12V 128.700 8 5 11.590 12.810
12Vsb 2.500 8 5 11.400 12.600
PWOK 0.000 8 5 2.600 3.460
Vin_Good 0.000 8 1 2.600 3.460
SMBAlert 0.000 8 1 2.600 3.460
Load Ton Ton Ton
Name Max Min (ms)
------------- -------- -------- ---------
12V 3000.00 1.00 1075.81
12Vsb 1500.00 1.00 830.41
PWOK ******** ******** 1281.56
Vin_Good ******** ******** 0.06
SMBAlert ******** ******** 0.06
Load Ref Load Td Td Td
Name No. Max Min (ms)
------------- ------------- -------- -------- ---------
12V 3 -500.00 -100.00 -205.75
12Vsb 1 -1500.00 -50.00 -245.40
PWOK 1 500.00 100.00 205.75
Vin_Good 0 ******** ******** 0.06
SMBAlert 0 ******** ******** 0.06
STEP.234(UUT Test seq.234) : I2C Read Status Multi_S6(180V_47Hz_HH) ---- (0 PASS
Adderss :B0
Command Page00 :060200
Command Page01 :060201
Status Word :79
Status Byte :78
Status VOUT :7A
Status IOUT :7B
Status INPUT :7C
Status TEMPERATURE :7D
Status CML :7E
Status FANS :81
---------------------------------
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
----------------------------------
Word_Page_00 : 0
Word_Page_01 : 0
Status_Byte_P00 : 0
Status_Byte_P01 : 0
Status_VOUT_P00 : 0
Status_VOUT_P01 : 0
Status_IOUT_P00 : 0
Status_IOUT_P01 : 0
Status_INPUT_P00 : 0
Status_INPUT_P01 : 0
Status_TEM_P00 : 0
Status_TEM_P01 : 0
Status_CML_P00 : 0
Status_CML_P01 : 0
Status_FANS_P00 : 0
Status_FANS_P01 : 0
STEP.235(UUT Test seq.235) : PS OFF Time 80611(180V_47Hz_HH) ---- (1'544) - PASS
Vin (V)= Refer to the previous item
Fin (Hz)= Refer to the previous item
On Phase Delay(ms)= Refer to the previous item
UUT Off Time (s)= Refer to the previous item
Loading (A/Ohm/V)= Refer to the previous item
Trigger: 1:Trig1R(AC), 2:Trig2R(PS on), 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:Trig1F(AC), 9:Trig2F(PS on),10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1
2 1
3 1
4 1
Load Start End VcmpA VcmpB
Name Trigger Trigger (V) (V)
------------- ------- ------- ------- -------
12V 2 12 11.590 12.810
12Vsb 2 2 11.400 12.600
PWOK 2 12 2.600 2.600
Vin_Good 2 2 2.600 2.600
SMBAlert 2 2 2.600 2.600
Load Ton Ton Ton
Name Max Min (ms)
------------- -------- -------- ---------
12V ******** ******** 2.31
12Vsb ******** ******** --------
PWOK 50.00 0.01 0.65
Vin_Good ******** ******** --------
SMBAlert ******** ******** --------
Load Ref Load Td Td Td
Name No. Max Min (ms)
------------- ---------- -------- -------- ---------
12V 3 100.00 1.00 1.66
12Vsb 0 ******** ******** --------
PWOK 1 -100.00 -1.00 -1.66
Vin_Good 0 ******** ******** --------
SMBAlert 0 ******** ******** --------
STEP.236(UUT Test seq.236) : PS ON Delay time 80611(180V_47Hz_HH) ---- (0'8 PASS
Vin (V)= Refer to the previous item
Fin (Hz)= Refer to the previous item
On Phase Delay(ms)= Refer to the previous item
UUT Off Time (s)= Refer to the previous item
Loading (A/Ohm/V)= Refer to the previous item
Trigger: 1:Trig1R(AC), 2:Trig2R(PS on), 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:Trig1F(AC), 9:Trig2F(PS on),10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1
2 1
3 1
4 1
Load Start End VcmpA VcmpB
Name Trigger Trigger (V) (V)
------------- ------- ------- ------- -------
12V 9 5 11.590 12.810
12Vsb 9 9 11.400 12.600
PWOK 9 5 2.600 2.600
Vin_Good 9 9 2.600 2.600
SMBAlert 9 9 2.600 2.600
Load Ton Ton Ton
Name Max Min (ms)
------------- -------- -------- ---------
12V 400.00 5.00 62.48
12Vsb ******** ******** 0.17
PWOK ******** ******** 268.12
Vin_Good ******** ******** 0.17
SMBAlert ******** ******** 0.17
Load Ref Load Td Td Td
Name No. Max Min (ms)
------------- ---------- -------- -------- ---------
12V 3 -500.000 -100.000 -205.636
12Vsb 0 ********* ********* 0.167
PWOK 1 500.000 100.000 205.636
Vin_Good 0 ********* ********* 0.167
SMBAlert 0 ********* ********* 0.167
STEP.237(UUT Test seq.237) : Turn On Timing Test_Multi or Single(180V_47Hz_ PASS
ElaspedTime (S)= 2'153
Vin (V)= 180.00
Fin (Hz)= 47.00
On Phase Delay(ms)= 90.00
UUT Off Time (s)= 0.50
Trigger: 1:TTL1R, 2:TTL2R, 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:TTL1F, 9:TTL2F,10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1.00
2 1.00
3 1.00
4 1.00
Load Loading Start End VcmpA VcmpB
Name (A/Ohm/V) Trigger Trigger (V) (V)
------------- ---------- ------- ------- ------- -------
12V 128.700 5 6 1.220 11.590
12Vsb 2.500 5 6 1.200 10.800
PWOK 0.000 8 1 2.600 3.460
Vin_Good 0.000 8 1 2.600 3.460
SMBAlert 0.000 8 1 2.600 3.460
Load Ton Ton Ton
Name Max Min (ms)
------------- -------- -------- ---------
12V 70.00 5.00 51.28
12Vsb 70.00 1.00 11.89
PWOK ******** ******** 0.06
Vin_Good ******** ******** 0.06
SMBAlert ******** ******** 0.06
Load Ref Load Td Td Td
Name No. Max Min (ms)
------------- ------------- -------- -------- ---------
12V 0 ******** ******** 51.28
12Vsb 0 ******** ******** 11.89
PWOK 0 ******** ******** 0.06
Vin_Good 0 ******** ******** 0.06
SMBAlert 0 ******** ******** 0.06
STEP.238(UUT Test seq.238) : TTL & Relay Setup ---- (0'000) --------------- PASS
(The Report Format of this Sequence was not found)
STEP.239(UUT Test seq.239) : PS ON Delay time 80611(180V_47Hz_HH_Tpson_12V_ PASS
Vin (V)= Refer to the previous item
Fin (Hz)= Refer to the previous item
On Phase Delay(ms)= Refer to the previous item
UUT Off Time (s)= Refer to the previous item
Loading (A/Ohm/V)= Refer to the previous item
Trigger: 1:Trig1R(AC), 2:Trig2R(PS on), 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:Trig1F(AC), 9:Trig2F(PS on),10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1
2 1
3 1
4 1
Load Start End VcmpA VcmpB
Name Trigger Trigger (V) (V)
------------- ------- ------- ------- -------
12V 5 6 1.220 11.590
12Vsb 9 9 1.200 10.800
PWOK 9 9 2.600 2.600
Vin_Good 9 9 2.600 2.600
SMBAlert 9 9 2.600 2.600
Load Ton Ton Ton
Name Max Min (ms)
------------- -------- -------- ---------
12V 70.00 5.00 51.27
12Vsb ******** ******** 0.14
PWOK ******** ******** 0.14
Vin_Good ******** ******** 0.14
SMBAlert ******** ******** 0.14
Load Ref Load Td Td Td
Name No. Max Min (ms)
------------- ---------- -------- -------- ---------
12V 0 ********* ********* 51.268
12Vsb 0 ********* ********* 0.142
PWOK 0 ********* ********* 0.142
Vin_Good 0 ********* ********* 0.142
SMBAlert 0 ********* ********* 0.142
STEP.240(UUT Test seq.240) : Input Output Eff Noise Multi or Single(180V_47 PASS
ElapsedTime (S)= 1'622
Vin (V)= 180.00
Fin (Hz)= 47.00
Delay Time (ms)= 300.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 128.700 ******* ******* 128.697
12Vsb 0.100 ******* ******* 0.100
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
-------Load---------------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V ???.??? ???.??? ???.???
12Vsb ???.??? ???.??? ???.???
PWOK ???.??? ???.??? ???.???
Vin_Good ???.??? ???.??? ???.???
SMBAlert ???.??? ???.??? ???.???
--------34970----------------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 12.810 11.590 12.179
12VSb 12.600 11.400 12.128
PWOK 3.460 2.500 3.233
Vin_Good 3.460 2.500 3.232
SMBAlert 3.460 2.500 3.218
IBUS ******* ******* 6.357
CR 0.400 ******* -0.016
Max Min Reading
------------- ---------- ---------- ----------
Vrms (V) ******** ******** 179.3898
PF 1.0000 ******** 0.9992
THDi (%) ******** * 2.5254
Irms (A) ******** ******** 9.6749
Pin (W) ******** ******** XXXXXXXX
Pout (W) ******** ******** XXXXXXXX
Eff (%) ******** ******** 90.4593
Load Noise Range Noise B.W
Name (V) (MHz)
------------- ----------- ---------
12V 2 20.000
12Vsb 2 20.000
PWOK 2 20.000
Vin_Good 2 20.000
SMBAlert 2 20.000
Load Vpp Noise Vpp Noise Vpp Noise
Name Max(mV) Min(mV) (mV)
------------- ------------ ------------ ------------
12V 120.000 0.000 15.000
12Vsb 120.000 0.000 7.220
PWOK ********* ********* 24.170
Vin_Good ********* ********* 22.360
SMBAlert ********* ********* 26.420
STEP.241(UUT Test seq.241) : Static ACDC 34970_or_Load_Multi or Single(180V PASS
ElapsedTime (S)= 1'248
Vin (V)= 180.00
Fin (Hz)= 47.00
Delay Time (ms)= 500.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 128.700 ******* ******* 128.697
12Vsb 2.750 ******* ******* 2.750
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 12.810 11.590 12.183
12VSb 12.600 11.400 11.989
PWOK 3.460 2.500 3.230
Vin_Good 3.460 2.500 3.224
SMBAlert 3.460 2.500 3.226
IBUS ******* ******* 6.357
CR 0.400 ******* -0.017
Max Min Reading
------------- --------- --------- ---------
Pout (W) ******* ******* XXXXXXX
STEP.242(UUT Test seq.242) : Static ACDC 34970_or_Load_Multi or Single(180V PASS
ElapsedTime (S)= 1'435
Vin (V)= 180.00
Fin (Hz)= 47.00
Delay Time (ms)= 500.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 128.700 ******* ******* 0.000
12Vsb 3.650 ******* ******* 0.009
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 0.400 ******* 0.001
12VSb 12.600 ******* 11.976
PWOK 0.400 ******* 0.039
Vin_Good 3.460 2.400 3.244
SMBAlert 3.460 ******* 3.214
IBUS ******* ******* 0.192
CR 0.400 ******* 0.004
Max Min Reading
------------- --------- --------- ---------
Pout (W) ******* ******* 0.113
STEP.243(UUT Test seq.243) : Static ACDC 34970_or_Load_Multi or Single(180V PASS
ElapsedTime (S)= 1'872
Vin (V)= 180.00
Fin (Hz)= 47.00
Delay Time (ms)= 1000.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 128.700 ******* ******* 128.697
12Vsb 2.750 ******* ******* 2.750
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 12.810 11.590 12.177
12VSb 12.600 11.400 11.991
PWOK 3.460 2.500 3.226
Vin_Good 3.460 2.500 3.231
SMBAlert 3.460 2.500 3.221
IBUS ******* ******* 6.359
CR 0.400 ******* -0.017
Max Min Reading
------------- --------- --------- ---------
Pout (W) ******* ******* XXXXXXX
STEP.244(UUT Test seq.244) : Cold Redundant Master Multi _S2 ---- (0'094) - PASS
(The Report Format of this Sequence was not found)
STEP.245(UUT Test seq.245) : Static ACDC 34970_or_Load_Multi or Single(180V PASS
ElapsedTime (S)= 1'264
Vin (V)= 180.00
Fin (Hz)= 47.00
Delay Time (ms)= 500.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 128.700 ******* ******* 128.697
12Vsb 2.500 ******* ******* 2.500
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 12.810 11.590 12.184
12VSb 12.600 11.400 12.000
PWOK 3.460 2.500 3.228
Vin_Good 3.460 2.500 3.222
SMBAlert 3.460 2.500 3.222
IBUS ******* ******* 6.358
CR 3.460 2.500 3.171
Max Min Reading
------------- --------- --------- ---------
Pout (W) ******* ******* XXXXXXX
STEP.246(UUT Test seq.246) : Disable Cold Redundant Master Multi_S2 ---- (0 PASS
(The Report Format of this Sequence was not found)
STEP.247(UUT Test seq.247) : Static ACDC 34970_or_Load_Multi or Single(180V PASS
ElapsedTime (S)= 1'233
Vin (V)= 180.00
Fin (Hz)= 47.00
Delay Time (ms)= 500.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 128.700 ******* ******* 128.697
12Vsb 2.500 ******* ******* 2.500
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 12.810 11.590 12.183
12VSb 12.600 11.400 11.999
PWOK 3.460 2.500 3.227
Vin_Good 3.460 2.500 3.228
SMBAlert 3.460 2.500 3.224
IBUS ******* ******* 6.357
CR 0.400 ******* -0.017
Max Min Reading
------------- --------- --------- ---------
Pout (W) ******* ******* XXXXXXX
STEP.248(UUT Test seq.248) : Input Output Eff Noise Multi or Single(180V_47 PASS
ElapsedTime (S)= 1'575
Vin (V)= 180.00
Fin (Hz)= 47.00
Delay Time (ms)= 300.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 128.700 ******* ******* 128.697
12Vsb 2.500 ******* ******* 2.500
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
-------Load---------------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V ???.??? ???.??? ???.???
12Vsb ???.??? ???.??? ???.???
PWOK ???.??? ???.??? ???.???
Vin_Good ???.??? ???.??? ???.???
SMBAlert ???.??? ???.??? ???.???
--------34970----------------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 12.810 11.590 12.182
12VSb 12.600 11.400 12.000
PWOK 3.460 2.500 3.229
Vin_Good 3.460 2.500 3.225
SMBAlert 3.460 2.500 3.226
IBUS ******* ******* 6.359
CR 0.400 ******* -0.017
Max Min Reading
------------- ---------- ---------- ----------
Vrms (V) ******** ******** 179.3663
PF 1.0000 ******** 0.9992
THDi (%) ******** * 2.4614
Irms (A) ******** ******** 9.8808
Pin (W) ******** ******** XXXXXXXX
Pout (W) ******** ******** XXXXXXXX
Eff (%) ******** ******** 90.2298
Load Noise Range Noise B.W
Name (V) (MHz)
------------- ----------- ---------
12V 2 20.000
12Vsb 2 20.000
PWOK 2 20.000
Vin_Good 2 20.000
SMBAlert 2 20.000
Load Vpp Noise Vpp Noise Vpp Noise
Name Max(mV) Min(mV) (mV)
------------- ------------ ------------ ------------
12V 120.000 0.000 13.430
12Vsb 120.000 0.000 14.900
PWOK ********* ********* 25.390
Vin_Good ********* ********* 23.090
SMBAlert ********* ********* 27.730
STEP.249(UUT Test seq.249) : Static ACDC 34970_or_Load_Multi or Single(180V PASS
ElapsedTime (S)= 3'728
Vin (V)= 180.00
Fin (Hz)= 47.00
Delay Time (ms)= 3000.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 148.005 ******* ******* 148.002
12Vsb 2.500 ******* ******* 2.500
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 12.810 11.590 12.172
12VSb 12.600 11.400 11.996
PWOK 3.460 2.500 3.222
Vin_Good 3.460 2.500 3.228
SMBAlert 3.460 ******* 0.048
IBUS ******* ******* 7.323
CR 0.400 ******* -0.020
Max Min Reading
------------- --------- --------- ---------
Pout (W) ******* ******* XXXXXXX
STEP.250(UUT Test seq.250) : TTL & Relay Setup(PS OnOff) ---- (1'014) ----- PASS
(The Report Format of this Sequence was not found)
STEP.251(UUT Test seq.251) : Peak_Load_S3_Multi_S(180V-OCP1_HL_Delay time 5 PASS
ElapsedTime (S)= 8'658
Vin (V)= Refer to the previous item
Fin (Hz)= Refer to the previous item
Delay Time (ms)= 2000.00
Load Setting Time (ms)= 2000.00
Measurement Delay Time (ms)= 3000.00
Turn On Delay Time (ms)= 3000.00
Loading Loading
Name (A/Ohm/V)
------------- ----------
12V 128.700
12Vsb 0.100
PWOK 0.000
Vin_Good 0.000
SMBAlert 0.000
12V_Loading_level Dell_Time Rise Rate Fall Rate
(A) (ms) (A/us) (A/us)
------------------ --------- --------- ---------
100.000 500.000 2.5000 2.5000
128.700 500.000 2.5000 2.5000
167.310 50.200 2.5000 2.5000
128.700 500.000 2.5000 2.5000
Load Vpk Max Vpk Min Vpk High Vpk Low
Name (V) (V) (V) (V)
------------- --------- --------- --------- ---------
12V 12.810 11.590 12.240 12.123
12Vsb 12.600 11.400 12.147 12.136
PWOK 3.460 2.500 3.263 3.265
Vin_Good 3.460 2.500 3.257 3.252
SMBAlert 3.460 ********* 0.108 0.079
STEP.252(UUT Test seq.252) : Peak_Load_S3_Multi_S(180V-OCP1_HH_Delay time 5 PASS
ElapsedTime (S)= 8'502
Vin (V)= Refer to the previous item
Fin (Hz)= Refer to the previous item
Delay Time (ms)= 2000.00
Load Setting Time (ms)= 2000.00
Measurement Delay Time (ms)= 3000.00
Turn On Delay Time (ms)= 3000.00
Loading Loading
Name (A/Ohm/V)
------------- ----------
12V 128.700
12Vsb 2.500
PWOK 0.000
Vin_Good 0.000
SMBAlert 0.000
12V_Loading_level Dell_Time Rise Rate Fall Rate
(A) (ms) (A/us) (A/us)
------------------ --------- --------- ---------
100.000 500.000 2.5000 2.5000
128.700 500.000 2.5000 2.5000
167.310 50.200 2.5000 2.5000
128.700 500.000 2.5000 2.5000
Load Vpk Max Vpk Min Vpk High Vpk Low
Name (V) (V) (V) (V)
------------- --------- --------- --------- ---------
12V 12.810 11.590 12.236 12.127
12Vsb 12.600 11.400 12.029 12.011
PWOK 3.460 2.500 3.261 3.262
Vin_Good 3.460 2.500 3.257 3.252
SMBAlert 3.460 ********* 0.100 0.077
STEP.253(UUT Test seq.253) : Peak_Load_S3_Multi_S(180V-OCP2_HL_Delay time 0 PASS
ElapsedTime (S)= 8'471
Vin (V)= Refer to the previous item
Fin (Hz)= Refer to the previous item
Delay Time (ms)= 2000.00
Load Setting Time (ms)= 2000.00
Measurement Delay Time (ms)= 3000.00
Turn On Delay Time (ms)= 3000.00
Loading Loading
Name (A/Ohm/V)
------------- ----------
12V 128.700
12Vsb 0.100
PWOK 0.000
Vin_Good 0.000
SMBAlert 0.000
12V_Loading_level Dell_Time Rise Rate Fall Rate
(A) (ms) (A/us) (A/us)
------------------ --------- --------- ---------
100.000 500.000 2.5000 2.5000
128.700 500.000 2.5000 2.5000
258.687 0.120 2.5000 2.5000
128.700 500.000 2.5000 2.5000
Load Vpk Max Vpk Min Vpk High Vpk Low
Name (V) (V) (V) (V)
------------- --------- --------- --------- ---------
12V 12.960 11.000 12.257 11.990
12Vsb 12.600 11.400 12.152 12.138
PWOK 3.460 2.500 3.263 3.266
Vin_Good 3.460 2.500 3.259 3.257
SMBAlert 3.460 ********* 0.124 0.043
STEP.254(UUT Test seq.254) : Peak_Load_S3_Multi_S(180V-OCP2_HH_Delay time 0 PASS
ElapsedTime (S)= 8'471
Vin (V)= Refer to the previous item
Fin (Hz)= Refer to the previous item
Delay Time (ms)= 2000.00
Load Setting Time (ms)= 2000.00
Measurement Delay Time (ms)= 3000.00
Turn On Delay Time (ms)= 3000.00
Loading Loading
Name (A/Ohm/V)
------------- ----------
12V 128.700
12Vsb 2.500
PWOK 0.000
Vin_Good 0.000
SMBAlert 0.000
12V_Loading_level Dell_Time Rise Rate Fall Rate
(A) (ms) (A/us) (A/us)
------------------ --------- --------- ---------
100.000 500.000 2.5000 2.5000
128.700 500.000 2.5000 2.5000
258.687 0.120 2.5000 2.5000
128.700 500.000 2.5000 2.5000
Load Vpk Max Vpk Min Vpk High Vpk Low
Name (V) (V) (V) (V)
------------- --------- --------- --------- ---------
12V 12.960 11.000 12.263 11.994
12Vsb 12.600 11.400 12.029 12.009
PWOK 3.460 2.500 3.261 3.266
Vin_Good 3.460 2.500 3.257 3.254
SMBAlert 3.460 ********* 0.120 0.043
STEP.255(UUT Test seq.255) : Set Input Condition Multi_S4_4(180V_47Hz) ---- PASS
Input Voltage Type (Vac=0 ; Vdc=1) = 0
Vin = 180.000
Fin = 47.000
Vin_DC_Positive_Negative(Positive=0 ; Negative=1) = 0
STEP.256(UUT Test seq.256) : Set Dynamic_Time ---- (0'000) ---------------- PASS
ElapsedTime (S)= 0'000
Delay Time (ms)= 3000.00
Measurement Time (ms) = 1000.00
UUT Off Time (s)= 3.00
STEP.257(UUT Test seq.257) : SetAllLoad_SlewRate_S ---- (0'140) ----------- PASS
STEP.258(UUT Test seq.258) : Sync_Dynamic_80611_20200716_Multi_S(180V-OCP_1 PASS
ElapsedTime (S)= 4'711
Vin (V)= Refer to previous item
Fin (Hz)= Refer to previous item
Duration-1 (ms)= 100.0000
Duration-2 (ms) = 50.2000
Load Loading-1 Loading-2 Vstable+ Vstable-
Name (A) (A) (V) (V)
------------- --------- --------- --------- ---------
12V 1.000 1.000 -------- --------
12Vsb 2.750 3.650 -------- --------
PWOK 0.000 0.000 -------- --------
Vin_Good 0.000 0.000 -------- --------
SMBAlert 0.000 0.000 -------- --------
Load Vpk+ Max Vpk+ Min Vpk High Vpk- Max Vpk- Min Vpk Low
Name (V) (V) (V) (V) (V) (V)
------------- --------- --------- --------- --------- --------- ---------
12V 12.810 11.590 12.271 12.810 11.590 12.259
12Vsb 12.600 11.400 12.028 12.600 11.400 12.007
PWOK 3.460 2.500 3.271 3.460 2.500 3.286
Vin_Good 3.460 2.500 3.266 3.460 2.500 3.277
SMBAlert 3.460 2.500 3.249 3.460 2.500 3.255
Load Vspk+ Max Vspk+ Min Vspk High Vspk- Max Vspk- Min Vspk Low
Name (V) (V) (mV) (V) (V) (mV)
------------- ---------- ---------- ---------- ---------- ---------- ----------
12V ******** ******** -------- ******** ******** --------
12Vsb ******** ******** -------- ******** ******** --------
PWOK ******** ******** -------- ******** ******** --------
Vin_Good ******** ******** -------- ******** ******** --------
SMBAlert ******** ******** -------- ******** ******** --------
STEP.259(UUT Test seq.259) : Sync_Dynamic_80611_20200716_Multi_S(180V-OCP_1 PASS
ElapsedTime (S)= 4'836
Vin (V)= Refer to previous item
Fin (Hz)= Refer to previous item
Duration-1 (ms)= 100.0000
Duration-2 (ms) = 50.2000
Load Loading-1 Loading-2 Vstable+ Vstable-
Name (A) (A) (V) (V)
------------- --------- --------- --------- ---------
12V 128.700 128.700 -------- --------
12Vsb 2.750 3.650 -------- --------
PWOK 0.000 0.000 -------- --------
Vin_Good 0.000 0.000 -------- --------
SMBAlert 0.000 0.000 -------- --------
Load Vpk+ Max Vpk+ Min Vpk High Vpk- Max Vpk- Min Vpk Low
Name (V) (V) (V) (V) (V) (V)
------------- --------- --------- --------- --------- --------- ---------
12V 12.810 11.590 12.191 12.810 11.590 12.178
12Vsb 12.600 11.400 12.017 12.600 11.400 11.991
PWOK 3.460 2.500 3.253 3.460 2.500 3.270
Vin_Good 3.460 2.500 3.250 3.460 2.500 3.257
SMBAlert 3.460 2.500 3.259 3.460 2.500 3.264
Load Vspk+ Max Vspk+ Min Vspk High Vspk- Max Vspk- Min Vspk Low
Name (V) (V) (mV) (V) (V) (mV)
------------- ---------- ---------- ---------- ---------- ---------- ----------
12V ******** ******** -------- ******** ******** --------
12Vsb ******** ******** -------- ******** ******** --------
PWOK ******** ******** -------- ******** ******** --------
Vin_Good ******** ******** -------- ******** ******** --------
SMBAlert ******** ******** -------- ******** ******** --------
STEP.260(UUT Test seq.260) : Hold Up Timing Test_Multi or Single(180V_47Hz_ PASS
ElapsedTime (S)= 0'905
Vin (V)= 180.00
Fin (Hz)= 47.00
Delay Time (ms)= 200.00
On Phase Delay(ms)= 90.00
UUT Off Time (s)= 0.00
Trigger: 1:Trig1R(AC), 2:Trig2R(PS on), 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:Trig1F(AC), 9:Trig2F(PS on),10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1
2 1
3 1
4 1
Load Loading Start End VcmpA VcmpB
Name (A/Ohm/V) Trigger Trigger (V) (V)
------------- ---------- ------- ------- ------- -------
12V 90.090 8 12 11.590 12.810
12Vsb 1.750 8 12 11.400 12.600
PWOK 0.000 8 12 2.600 3.460
Vin_Good 0.000 8 12 2.600 3.460
SMBAlert 0.000 8 1 2.600 3.460
Load Tholdup Tholdup Tholdup
Name Max Min (ms)
------------- -------- -------- ---------
12V 1000.00 10.00 26.69
12Vsb 1000.00 70.00 79.04
PWOK 300.00 9.00 25.02
Vin_Good 4.00 0.01 2.68
SMBAlert ******** ******** 0.06
Load Ref Load Tholdup Tholdup Tholdup
Name No. Max Min (ms)
------------- ---------- -------- -------- ---------
12V 3 100.00 1.00 1.68
12Vsb 0 ******** ******** 79.04
PWOK 1 -100.00 -1.00 -1.68
Vin_Good 0 ******** ******** 2.68
SMBAlert 0 ******** ******** 0.06
STEP.261(UUT Test seq.261) : FAN Full Speed delay time Multi ---- (8'096) - PASS
STEP.262(UUT Test seq.262) : FAN Speed Normal_Multi ---- (0'094) ---------- PASS
(The Report Format of this Sequence was not found)
STEP.263(UUT Test seq.263) : Turn On Timing Test_Multi or Single(200V_50Hz_ PASS
ElaspedTime (S)= 1'748
Vin (V)= 200.00
Fin (Hz)= 50.00
On Phase Delay(ms)= 90.00
UUT Off Time (s)= 0.00
Trigger: 1:TTL1R, 2:TTL2R, 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:TTL1F, 9:TTL2F,10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1.00
2 1.00
3 1.00
4 1.00
Load Loading Start End VcmpA VcmpB
Name (A/Ohm/V) Trigger Trigger (V) (V)
------------- ---------- ------- ------- ------- -------
12V 145.100 8 5 11.590 12.810
12Vsb 2.500 8 5 11.400 12.600
PWOK 0.000 8 5 2.600 3.460
Vin_Good 0.000 8 1 2.600 3.460
SMBAlert 0.000 8 1 2.600 3.460
Load Ton Ton Ton
Name Max Min (ms)
------------- -------- -------- ---------
12V 3000.00 1.00 1023.15
12Vsb 1500.00 1.00 777.67
PWOK ******** ******** 1228.72
Vin_Good ******** ******** 0.06
SMBAlert ******** ******** 0.06
Load Ref Load Td Td Td
Name No. Max Min (ms)
------------- ------------- -------- -------- ---------
12V 3 -500.00 -100.00 -205.57
12Vsb 1 -1500.00 -50.00 -245.48
PWOK 1 500.00 100.00 205.57
Vin_Good 0 ******** ******** 0.06
SMBAlert 0 ******** ******** 0.06
STEP.264(UUT Test seq.264) : I2C Read Status Multi_S6(200V_50Hz_HH) ---- (0 PASS
Adderss :B0
Command Page00 :060200
Command Page01 :060201
Status Word :79
Status Byte :78
Status VOUT :7A
Status IOUT :7B
Status INPUT :7C
Status TEMPERATURE :7D
Status CML :7E
Status FANS :81
---------------------------------
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
----------------------------------
Word_Page_00 : 0
Word_Page_01 : 0
Status_Byte_P00 : 0
Status_Byte_P01 : 0
Status_VOUT_P00 : 0
Status_VOUT_P01 : 0
Status_IOUT_P00 : 0
Status_IOUT_P01 : 0
Status_INPUT_P00 : 0
Status_INPUT_P01 : 0
Status_TEM_P00 : 0
Status_TEM_P01 : 0
Status_CML_P00 : 0
Status_CML_P01 : 0
Status_FANS_P00 : 0
Status_FANS_P01 : 0
STEP.265(UUT Test seq.265) : PS OFF Time 80611(200V_50Hz_HH) ---- (1'560) - PASS
Vin (V)= Refer to the previous item
Fin (Hz)= Refer to the previous item
On Phase Delay(ms)= Refer to the previous item
UUT Off Time (s)= Refer to the previous item
Loading (A/Ohm/V)= Refer to the previous item
Trigger: 1:Trig1R(AC), 2:Trig2R(PS on), 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:Trig1F(AC), 9:Trig2F(PS on),10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1
2 1
3 1
4 1
Load Start End VcmpA VcmpB
Name Trigger Trigger (V) (V)
------------- ------- ------- ------- -------
12V 2 12 11.590 12.810
12Vsb 2 2 11.400 12.600
PWOK 2 12 2.600 2.600
Vin_Good 2 2 2.600 2.600
SMBAlert 2 2 2.600 2.600
Load Ton Ton Ton
Name Max Min (ms)
------------- -------- -------- ---------
12V ******** ******** 2.43
12Vsb ******** ******** --------
PWOK 50.00 0.01 0.77
Vin_Good ******** ******** --------
SMBAlert ******** ******** --------
Load Ref Load Td Td Td
Name No. Max Min (ms)
------------- ---------- -------- -------- ---------
12V 3 100.00 1.00 1.65
12Vsb 0 ******** ******** --------
PWOK 1 -100.00 -1.00 -1.65
Vin_Good 0 ******** ******** --------
SMBAlert 0 ******** ******** --------
STEP.266(UUT Test seq.266) : PS ON Delay time 80611(200V_50Hz_HH) ---- (0'8 PASS
Vin (V)= Refer to the previous item
Fin (Hz)= Refer to the previous item
On Phase Delay(ms)= Refer to the previous item
UUT Off Time (s)= Refer to the previous item
Loading (A/Ohm/V)= Refer to the previous item
Trigger: 1:Trig1R(AC), 2:Trig2R(PS on), 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:Trig1F(AC), 9:Trig2F(PS on),10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1
2 1
3 1
4 1
Load Start End VcmpA VcmpB
Name Trigger Trigger (V) (V)
------------- ------- ------- ------- -------
12V 9 5 11.590 12.810
12Vsb 9 9 11.400 12.600
PWOK 9 5 2.600 2.600
Vin_Good 9 9 2.600 2.600
SMBAlert 9 9 2.600 2.600
Load Ton Ton Ton
Name Max Min (ms)
------------- -------- -------- ---------
12V 400.00 5.00 62.56
12Vsb ******** ******** 0.05
PWOK ******** ******** 268.14
Vin_Good ******** ******** 0.05
SMBAlert ******** ******** 0.05
Load Ref Load Td Td Td
Name No. Max Min (ms)
------------- ---------- -------- -------- ---------
12V 3 -500.000 -100.000 -205.577
12Vsb 0 ********* ********* 0.045
PWOK 1 500.000 100.000 205.577
Vin_Good 0 ********* ********* 0.045
SMBAlert 0 ********* ********* 0.045
STEP.267(UUT Test seq.267) : Turn On Timing Test_Multi or Single(200V_50Hz_ PASS
ElaspedTime (S)= 2'215
Vin (V)= 200.00
Fin (Hz)= 50.00
On Phase Delay(ms)= 90.00
UUT Off Time (s)= 0.50
Trigger: 1:TTL1R, 2:TTL2R, 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:TTL1F, 9:TTL2F,10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1.00
2 1.00
3 1.00
4 1.00
Load Loading Start End VcmpA VcmpB
Name (A/Ohm/V) Trigger Trigger (V) (V)
------------- ---------- ------- ------- ------- -------
12V 145.100 5 6 1.220 11.590
12Vsb 2.500 5 6 1.200 10.800
PWOK 0.000 8 1 2.600 3.460
Vin_Good 0.000 8 1 2.600 3.460
SMBAlert 0.000 8 1 2.600 3.460
Load Ton Ton Ton
Name Max Min (ms)
------------- -------- -------- ---------
12V 70.00 5.00 51.26
12Vsb 70.00 1.00 11.81
PWOK ******** ******** 0.06
Vin_Good ******** ******** 0.06
SMBAlert ******** ******** 0.06
Load Ref Load Td Td Td
Name No. Max Min (ms)
------------- ------------- -------- -------- ---------
12V 0 ******** ******** 51.26
12Vsb 0 ******** ******** 11.81
PWOK 0 ******** ******** 0.06
Vin_Good 0 ******** ******** 0.06
SMBAlert 0 ******** ******** 0.06
STEP.268(UUT Test seq.268) : TTL & Relay Setup ---- (0'000) --------------- PASS
(The Report Format of this Sequence was not found)
STEP.269(UUT Test seq.269) : PS ON Delay time 80611(200V_50Hz_HH_Tpson_12V_ PASS
Vin (V)= Refer to the previous item
Fin (Hz)= Refer to the previous item
On Phase Delay(ms)= Refer to the previous item
UUT Off Time (s)= Refer to the previous item
Loading (A/Ohm/V)= Refer to the previous item
Trigger: 1:Trig1R(AC), 2:Trig2R(PS on), 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:Trig1F(AC), 9:Trig2F(PS on),10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1
2 1
3 1
4 1
Load Start End VcmpA VcmpB
Name Trigger Trigger (V) (V)
------------- ------- ------- ------- -------
12V 5 6 1.220 11.590
12Vsb 9 9 1.200 10.800
PWOK 9 9 2.600 2.600
Vin_Good 9 9 2.600 2.600
SMBAlert 9 9 2.600 2.600
Load Ton Ton Ton
Name Max Min (ms)
------------- -------- -------- ---------
12V 70.00 5.00 51.27
12Vsb ******** ******** 0.17
PWOK ******** ******** 0.17
Vin_Good ******** ******** 0.17
SMBAlert ******** ******** 0.17
Load Ref Load Td Td Td
Name No. Max Min (ms)
------------- ---------- -------- -------- ---------
12V 0 ********* ********* 51.266
12Vsb 0 ********* ********* 0.169
PWOK 0 ********* ********* 0.169
Vin_Good 0 ********* ********* 0.169
SMBAlert 0 ********* ********* 0.169
STEP.270(UUT Test seq.270) : Input Output Eff Noise Multi or Single(200V_50 PASS
ElapsedTime (S)= 1'731
Vin (V)= 200.00
Fin (Hz)= 50.00
Delay Time (ms)= 300.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 145.100 ******* ******* 145.097
12Vsb 0.100 ******* ******* 0.100
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
-------Load---------------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V ???.??? ???.??? ???.???
12Vsb ???.??? ???.??? ???.???
PWOK ???.??? ???.??? ???.???
Vin_Good ???.??? ???.??? ???.???
SMBAlert ???.??? ???.??? ???.???
--------34970----------------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 12.810 11.590 12.173
12VSb 12.600 11.400 12.126
PWOK 3.460 2.500 3.230
Vin_Good 3.460 2.500 3.224
SMBAlert 3.460 2.500 3.225
IBUS ******* ******* 7.176
CR 0.400 ******* -0.018
Max Min Reading
------------- ---------- ---------- ----------
Vrms (V) ******** ******** 199.3646
PF 1.0000 ******** 0.9990
THDi (%) ******** * 2.4479
Irms (A) ******** ******** 9.8085
Pin (W) ******** ******** XXXXXXXX
Pout (W) ******** ******** XXXXXXXX
Eff (%) ******** ******** 90.4783
Load Noise Range Noise B.W
Name (V) (MHz)
------------- ----------- ---------
12V 2 20.000
12Vsb 2 20.000
PWOK 2 20.000
Vin_Good 2 20.000
SMBAlert 2 20.000
Load Vpp Noise Vpp Noise Vpp Noise
Name Max(mV) Min(mV) (mV)
------------- ------------ ------------ ------------
12V 120.000 0.000 14.860
12Vsb 120.000 0.000 7.260
PWOK ********* ********* 24.870
Vin_Good ********* ********* 22.680
SMBAlert ********* ********* 27.510
STEP.271(UUT Test seq.271) : Static ACDC 34970_or_Load_Multi or Single(200V PASS
ElapsedTime (S)= 1'248
Vin (V)= 200.00
Fin (Hz)= 50.00
Delay Time (ms)= 500.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 145.100 ******* ******* 145.097
12Vsb 2.750 ******* ******* 2.750
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 12.810 11.590 12.174
12VSb 12.600 11.400 11.986
PWOK 3.460 2.500 3.225
Vin_Good 3.460 2.500 3.228
SMBAlert 3.460 2.500 3.219
IBUS ******* ******* 7.175
CR 0.400 ******* -0.020
Max Min Reading
------------- --------- --------- ---------
Pout (W) ******* ******* XXXXXXX
STEP.272(UUT Test seq.272) : Static ACDC 34970_or_Load_Multi or Single(200V PASS
ElapsedTime (S)= 1'435
Vin (V)= 200.00
Fin (Hz)= 50.00
Delay Time (ms)= 500.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 145.100 ******* ******* 0.000
12Vsb 3.650 ******* ******* 0.008
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 0.400 ******* 0.001
12VSb 12.600 ******* 11.977
PWOK 0.400 ******* 0.039
Vin_Good 3.460 2.400 3.241
SMBAlert 3.460 ******* 3.219
IBUS ******* ******* 0.161
CR 0.400 ******* 0.004
Max Min Reading
------------- --------- --------- ---------
Pout (W) ******* ******* 0.095
STEP.273(UUT Test seq.273) : Static ACDC 34970_or_Load_Multi or Single(200V PASS
ElapsedTime (S)= 1'934
Vin (V)= 200.00
Fin (Hz)= 50.00
Delay Time (ms)= 1000.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 145.100 ******* ******* 145.097
12Vsb 2.750 ******* ******* 2.750
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 12.810 11.590 12.171
12VSb 12.600 11.400 11.988
PWOK 3.460 2.500 3.222
Vin_Good 3.460 2.500 3.223
SMBAlert 3.460 2.500 3.226
IBUS ******* ******* 7.173
CR 0.400 ******* -0.020
Max Min Reading
------------- --------- --------- ---------
Pout (W) ******* ******* XXXXXXX
STEP.274(UUT Test seq.274) : Cold Redundant Master Multi _S2 ---- (0'093) - PASS
(The Report Format of this Sequence was not found)
STEP.275(UUT Test seq.275) : Static ACDC 34970_or_Load_Multi or Single(200V PASS
ElapsedTime (S)= 1'248
Vin (V)= 200.00
Fin (Hz)= 50.00
Delay Time (ms)= 500.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 145.100 ******* ******* 145.097
12Vsb 2.500 ******* ******* 2.500
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 12.810 11.590 12.176
12VSb 12.600 11.400 11.997
PWOK 3.460 2.500 3.223
Vin_Good 3.460 2.500 3.219
SMBAlert 3.460 2.500 3.227
IBUS ******* ******* 7.176
CR 3.460 2.500 3.168
Max Min Reading
------------- --------- --------- ---------
Pout (W) ******* ******* XXXXXXX
STEP.276(UUT Test seq.276) : Disable Cold Redundant Master Multi_S2 ---- (0 PASS
(The Report Format of this Sequence was not found)
STEP.277(UUT Test seq.277) : Static ACDC 34970_or_Load_Multi or Single(200V PASS
ElapsedTime (S)= 1'202
Vin (V)= 200.00
Fin (Hz)= 50.00
Delay Time (ms)= 500.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 145.100 ******* ******* 145.097
12Vsb 2.500 ******* ******* 2.500
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 12.810 11.590 12.176
12VSb 12.600 11.400 11.997
PWOK 3.460 2.500 3.227
Vin_Good 3.460 2.500 3.222
SMBAlert 3.460 2.500 3.224
IBUS ******* ******* 7.176
CR 0.400 ******* -0.020
Max Min Reading
------------- --------- --------- ---------
Pout (W) ******* ******* XXXXXXX
STEP.278(UUT Test seq.278) : Input Output Eff Noise Multi or Single(200V_50 PASS
ElapsedTime (S)= 1'607
Vin (V)= 200.00
Fin (Hz)= 50.00
Delay Time (ms)= 300.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 145.100 ******* ******* 145.097
12Vsb 2.500 ******* ******* 2.500
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
-------Load---------------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V ???.??? ???.??? ???.???
12Vsb ???.??? ???.??? ???.???
PWOK ???.??? ???.??? ???.???
Vin_Good ???.??? ???.??? ???.???
SMBAlert ???.??? ???.??? ???.???
--------34970----------------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 12.810 11.590 12.176
12VSb 12.600 11.400 11.996
PWOK 3.460 2.500 3.223
Vin_Good 3.460 2.500 3.228
SMBAlert 3.460 2.500 3.219
IBUS ******* ******* 7.176
CR 0.400 ******* -0.020
Max Min Reading
------------- ---------- ---------- ----------
Vrms (V) ******** ******** 199.3854
PF 1.0000 ******** 0.9990
THDi (%) ******** * 2.3877
Irms (A) ******** ******** 9.9931
Pin (W) ******** ******** XXXXXXXX
Pout (W) ******** ******** XXXXXXXX
Eff (%) ******** ******** 90.2604
Load Noise Range Noise B.W
Name (V) (MHz)
------------- ----------- ---------
12V 2 20.000
12Vsb 2 20.000
PWOK 2 20.000
Vin_Good 2 20.000
SMBAlert 2 20.000
Load Vpp Noise Vpp Noise Vpp Noise
Name Max(mV) Min(mV) (mV)
------------- ------------ ------------ ------------
12V 120.000 0.000 13.690
12Vsb 120.000 0.000 15.120
PWOK ********* ********* 25.990
Vin_Good ********* ********* 23.640
SMBAlert ********* ********* 28.030
STEP.279(UUT Test seq.279) : Static ACDC 34970_or_Load_Multi or Single(200V PASS
ElapsedTime (S)= 3'775
Vin (V)= 200.00
Fin (Hz)= 50.00
Delay Time (ms)= 3000.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 166.865 ******* ******* 166.862
12Vsb 2.500 ******* ******* 2.500
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 12.810 11.590 12.163
12VSb 12.600 11.400 11.994
PWOK 3.460 2.500 3.226
Vin_Good 3.460 2.500 3.220
SMBAlert 3.460 ******* 0.045
IBUS ******* ******* 8.274
CR 0.400 ******* -0.023
Max Min Reading
------------- --------- --------- ---------
Pout (W) ******* ******* XXXXXXX
STEP.280(UUT Test seq.280) : TTL & Relay Setup(PS OnOff) ---- (1'029) ----- PASS
(The Report Format of this Sequence was not found)
STEP.281(UUT Test seq.281) : Peak_Load_S3_Multi_S(200V-OCP1_HL_Delay time 5 PASS
ElapsedTime (S)= 8'502
Vin (V)= Refer to the previous item
Fin (Hz)= Refer to the previous item
Delay Time (ms)= 2000.00
Load Setting Time (ms)= 2000.00
Measurement Delay Time (ms)= 3000.00
Turn On Delay Time (ms)= 3000.00
Loading Loading
Name (A/Ohm/V)
------------- ----------
12V 145.100
12Vsb 0.100
PWOK 0.000
Vin_Good 0.000
SMBAlert 0.000
12V_Loading_level Dell_Time Rise Rate Fall Rate
(A) (ms) (A/us) (A/us)
------------------ --------- --------- ---------
100.000 500.000 2.5000 2.5000
145.100 500.000 2.5000 2.5000
188.630 50.200 2.5000 2.5000
145.100 500.000 2.5000 2.5000
Load Vpk Max Vpk Min Vpk High Vpk Low
Name (V) (V) (V) (V)
------------- --------- --------- --------- ---------
12V 12.810 11.590 12.233 12.099
12Vsb 12.600 11.400 12.149 12.137
PWOK 3.460 2.500 3.264 3.260
Vin_Good 3.460 2.500 3.257 3.250
SMBAlert 3.460 ********* 0.102 0.067
STEP.282(UUT Test seq.282) : Peak_Load_S3_Multi_S(200V-OCP1_HH_Delay time 5 PASS
ElapsedTime (S)= 8'471
Vin (V)= Refer to the previous item
Fin (Hz)= Refer to the previous item
Delay Time (ms)= 2000.00
Load Setting Time (ms)= 2000.00
Measurement Delay Time (ms)= 3000.00
Turn On Delay Time (ms)= 3000.00
Loading Loading
Name (A/Ohm/V)
------------- ----------
12V 145.100
12Vsb 2.500
PWOK 0.000
Vin_Good 0.000
SMBAlert 0.000
12V_Loading_level Dell_Time Rise Rate Fall Rate
(A) (ms) (A/us) (A/us)
------------------ --------- --------- ---------
100.000 500.000 2.5000 2.5000
145.100 500.000 2.5000 2.5000
188.630 50.200 2.5000 2.5000
145.100 500.000 2.5000 2.5000
Load Vpk Max Vpk Min Vpk High Vpk Low
Name (V) (V) (V) (V)
------------- --------- --------- --------- ---------
12V 12.810 11.590 12.232 12.099
12Vsb 12.600 11.400 12.027 12.011
PWOK 3.460 2.500 3.262 3.258
Vin_Good 3.460 2.500 3.256 3.247
SMBAlert 3.460 ********* 0.097 0.067
STEP.283(UUT Test seq.283) : Peak_Load_S3_Multi_S(200V-OCP2_HL_Delay time 0 PASS
ElapsedTime (S)= 8'455
Vin (V)= Refer to the previous item
Fin (Hz)= Refer to the previous item
Delay Time (ms)= 2000.00
Load Setting Time (ms)= 2000.00
Measurement Delay Time (ms)= 3000.00
Turn On Delay Time (ms)= 3000.00
Loading Loading
Name (A/Ohm/V)
------------- ----------
12V 145.100
12Vsb 0.100
PWOK 0.000
Vin_Good 0.000
SMBAlert 0.000
12V_Loading_level Dell_Time Rise Rate Fall Rate
(A) (ms) (A/us) (A/us)
------------------ --------- --------- ---------
100.000 500.000 2.5000 2.5000
145.100 500.000 2.5000 2.5000
291.651 0.120 2.5000 2.5000
145.100 500.000 2.5000 2.5000
Load Vpk Max Vpk Min Vpk High Vpk Low
Name (V) (V) (V) (V)
------------- --------- --------- --------- ---------
12V 12.960 11.000 12.269 11.962
12Vsb 12.600 11.400 12.151 12.137
PWOK 3.460 2.500 3.263 3.266
Vin_Good 3.460 2.500 3.257 3.254
SMBAlert 3.460 ********* 0.119 0.037
STEP.284(UUT Test seq.284) : Peak_Load_S3_Multi_S(200V-OCP2_HH_Delay time 0 PASS
ElapsedTime (S)= 8'471
Vin (V)= Refer to the previous item
Fin (Hz)= Refer to the previous item
Delay Time (ms)= 2000.00
Load Setting Time (ms)= 2000.00
Measurement Delay Time (ms)= 3000.00
Turn On Delay Time (ms)= 3000.00
Loading Loading
Name (A/Ohm/V)
------------- ----------
12V 145.100
12Vsb 2.500
PWOK 0.000
Vin_Good 0.000
SMBAlert 0.000
12V_Loading_level Dell_Time Rise Rate Fall Rate
(A) (ms) (A/us) (A/us)
------------------ --------- --------- ---------
100.000 500.000 2.5000 2.5000
145.100 500.000 2.5000 2.5000
291.651 0.120 2.5000 2.5000
145.100 500.000 2.5000 2.5000
Load Vpk Max Vpk Min Vpk High Vpk Low
Name (V) (V) (V) (V)
------------- --------- --------- --------- ---------
12V 12.960 11.000 12.269 11.968
12Vsb 12.600 11.400 12.025 12.001
PWOK 3.460 2.500 3.262 3.263
Vin_Good 3.460 2.500 3.257 3.252
SMBAlert 3.460 ********* 0.119 0.034
STEP.285(UUT Test seq.285) : Set Input Condition Multi_S4_4(200V_50Hz) ---- PASS
Input Voltage Type (Vac=0 ; Vdc=1) = 0
Vin = 200.000
Fin = 50.000
Vin_DC_Positive_Negative(Positive=0 ; Negative=1) = 0
STEP.286(UUT Test seq.286) : Set Dynamic_Time ---- (0'016) ---------------- PASS
ElapsedTime (S)= 0'016
Delay Time (ms)= 3000.00
Measurement Time (ms) = 1000.00
UUT Off Time (s)= 3.00
STEP.287(UUT Test seq.287) : SetAllLoad_SlewRate_S ---- (0'109) ----------- PASS
STEP.288(UUT Test seq.288) : Sync_Dynamic_80611_20200716_Multi_S(200V-OCP_1 PASS
ElapsedTime (S)= 4'711
Vin (V)= Refer to previous item
Fin (Hz)= Refer to previous item
Duration-1 (ms)= 100.0000
Duration-2 (ms) = 50.2000
Load Loading-1 Loading-2 Vstable+ Vstable-
Name (A) (A) (V) (V)
------------- --------- --------- --------- ---------
12V 1.000 1.000 -------- --------
12Vsb 2.750 3.650 -------- --------
PWOK 0.000 0.000 -------- --------
Vin_Good 0.000 0.000 -------- --------
SMBAlert 0.000 0.000 -------- --------
Load Vpk+ Max Vpk+ Min Vpk High Vpk- Max Vpk- Min Vpk Low
Name (V) (V) (V) (V) (V) (V)
------------- --------- --------- --------- --------- --------- ---------
12V 12.810 11.590 12.274 12.810 11.590 12.265
12Vsb 12.600 11.400 12.027 12.600 11.400 12.011
PWOK 3.460 2.500 3.271 3.460 2.500 3.286
Vin_Good 3.460 2.500 3.266 3.460 2.500 3.277
SMBAlert 3.460 2.500 3.251 3.460 2.500 3.256
Load Vspk+ Max Vspk+ Min Vspk High Vspk- Max Vspk- Min Vspk Low
Name (V) (V) (mV) (V) (V) (mV)
------------- ---------- ---------- ---------- ---------- ---------- ----------
12V ******** ******** -------- ******** ******** --------
12Vsb ******** ******** -------- ******** ******** --------
PWOK ******** ******** -------- ******** ******** --------
Vin_Good ******** ******** -------- ******** ******** --------
SMBAlert ******** ******** -------- ******** ******** --------
STEP.289(UUT Test seq.289) : Sync_Dynamic_80611_20200716_Multi_S(200V-OCP_1 PASS
ElapsedTime (S)= 4'821
Vin (V)= Refer to previous item
Fin (Hz)= Refer to previous item
Duration-1 (ms)= 100.0000
Duration-2 (ms) = 50.2000
Load Loading-1 Loading-2 Vstable+ Vstable-
Name (A) (A) (V) (V)
------------- --------- --------- --------- ---------
12V 145.100 145.100 -------- --------
12Vsb 2.750 3.650 -------- --------
PWOK 0.000 0.000 -------- --------
Vin_Good 0.000 0.000 -------- --------
SMBAlert 0.000 0.000 -------- --------
Load Vpk+ Max Vpk+ Min Vpk High Vpk- Max Vpk- Min Vpk Low
Name (V) (V) (V) (V) (V) (V)
------------- --------- --------- --------- --------- --------- ---------
12V 12.810 11.590 12.182 12.810 11.590 12.172
12Vsb 12.600 11.400 12.017 12.600 11.400 11.992
PWOK 3.460 2.500 3.252 3.460 2.500 3.266
Vin_Good 3.460 2.500 3.245 3.460 2.500 3.254
SMBAlert 3.460 2.500 3.257 3.460 2.500 3.262
Load Vspk+ Max Vspk+ Min Vspk High Vspk- Max Vspk- Min Vspk Low
Name (V) (V) (mV) (V) (V) (mV)
------------- ---------- ---------- ---------- ---------- ---------- ----------
12V ******** ******** -------- ******** ******** --------
12Vsb ******** ******** -------- ******** ******** --------
PWOK ******** ******** -------- ******** ******** --------
Vin_Good ******** ******** -------- ******** ******** --------
SMBAlert ******** ******** -------- ******** ******** --------
STEP.290(UUT Test seq.290) : Hold Up Timing Test_Multi or Single(200V_50Hz_ PASS
ElapsedTime (S)= 0'905
Vin (V)= 200.00
Fin (Hz)= 50.00
Delay Time (ms)= 200.00
On Phase Delay(ms)= 90.00
UUT Off Time (s)= 0.00
Trigger: 1:Trig1R(AC), 2:Trig2R(PS on), 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:Trig1F(AC), 9:Trig2F(PS on),10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1
2 1
3 1
4 1
Load Loading Start End VcmpA VcmpB
Name (A/Ohm/V) Trigger Trigger (V) (V)
------------- ---------- ------- ------- ------- -------
12V 101.570 8 12 11.590 12.810
12Vsb 1.750 8 12 11.400 12.600
PWOK 0.000 8 12 2.600 3.460
Vin_Good 0.000 8 12 2.600 3.460
SMBAlert 0.000 8 1 2.600 3.460
Load Tholdup Tholdup Tholdup
Name Max Min (ms)
------------- -------- -------- ---------
12V 1000.00 10.00 23.93
12Vsb 1000.00 70.00 78.29
PWOK 300.00 9.00 22.28
Vin_Good 4.00 0.01 2.75
SMBAlert ******** ******** 0.06
Load Ref Load Tholdup Tholdup Tholdup
Name No. Max Min (ms)
------------- ---------- -------- -------- ---------
12V 3 100.00 1.00 1.65
12Vsb 0 ******** ******** 78.29
PWOK 1 -100.00 -1.00 -1.65
Vin_Good 0 ******** ******** 2.75
SMBAlert 0 ******** ******** 0.06
STEP.291(UUT Test seq.291) : FAN Full Speed delay time Multi ---- (8'097) - PASS
STEP.292(UUT Test seq.292) : FAN Speed Normal_Multi ---- (0'094) ---------- PASS
(The Report Format of this Sequence was not found)
STEP.293(UUT Test seq.293) : Turn On Timing Test_Multi or Single(220V_50Hz_ PASS
ElaspedTime (S)= 1'747
Vin (V)= 220.00
Fin (Hz)= 50.00
On Phase Delay(ms)= 90.00
UUT Off Time (s)= 0.00
Trigger: 1:TTL1R, 2:TTL2R, 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:TTL1F, 9:TTL2F,10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1.00
2 1.00
3 1.00
4 1.00
Load Loading Start End VcmpA VcmpB
Name (A/Ohm/V) Trigger Trigger (V) (V)
------------- ---------- ------- ------- ------- -------
12V 161.500 8 5 11.590 12.810
12Vsb 2.500 8 5 11.400 12.600
PWOK 0.000 8 5 2.600 3.460
Vin_Good 0.000 8 1 2.600 3.460
SMBAlert 0.000 8 1 2.600 3.460
Load Ton Ton Ton
Name Max Min (ms)
------------- -------- -------- ---------
12V 3000.00 1.00 996.92
12Vsb 1500.00 1.00 751.19
PWOK ******** ******** 1202.59
Vin_Good ******** ******** 0.06
SMBAlert ******** ******** 0.06
Load Ref Load Td Td Td
Name No. Max Min (ms)
------------- ------------- -------- -------- ---------
12V 3 -500.00 -100.00 -205.67
12Vsb 1 -1500.00 -50.00 -245.74
PWOK 1 500.00 100.00 205.67
Vin_Good 0 ******** ******** 0.06
SMBAlert 0 ******** ******** 0.06
STEP.294(UUT Test seq.294) : I2C Read Status Multi_S6(220V_50Hz_HH) ---- (0 PASS
Adderss :B0
Command Page00 :060200
Command Page01 :060201
Status Word :79
Status Byte :78
Status VOUT :7A
Status IOUT :7B
Status INPUT :7C
Status TEMPERATURE :7D
Status CML :7E
Status FANS :81
---------------------------------
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
----------------------------------
Word_Page_00 : 0
Word_Page_01 : 0
Status_Byte_P00 : 0
Status_Byte_P01 : 0
Status_VOUT_P00 : 0
Status_VOUT_P01 : 0
Status_IOUT_P00 : 0
Status_IOUT_P01 : 0
Status_INPUT_P00 : 0
Status_INPUT_P01 : 0
Status_TEM_P00 : 0
Status_TEM_P01 : 0
Status_CML_P00 : 0
Status_CML_P01 : 0
Status_FANS_P00 : 0
Status_FANS_P01 : 0
STEP.295(UUT Test seq.295) : PS OFF Time 80611(220V_50Hz_HH) ---- (1'545) - PASS
Vin (V)= Refer to the previous item
Fin (Hz)= Refer to the previous item
On Phase Delay(ms)= Refer to the previous item
UUT Off Time (s)= Refer to the previous item
Loading (A/Ohm/V)= Refer to the previous item
Trigger: 1:Trig1R(AC), 2:Trig2R(PS on), 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:Trig1F(AC), 9:Trig2F(PS on),10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1
2 1
3 1
4 1
Load Start End VcmpA VcmpB
Name Trigger Trigger (V) (V)
------------- ------- ------- ------- -------
12V 2 12 11.590 12.810
12Vsb 2 2 11.400 12.600
PWOK 2 12 2.600 2.600
Vin_Good 2 2 2.600 2.600
SMBAlert 2 2 2.600 2.600
Load Ton Ton Ton
Name Max Min (ms)
------------- -------- -------- ---------
12V ******** ******** 2.39
12Vsb ******** ******** --------
PWOK 50.00 0.01 0.74
Vin_Good ******** ******** --------
SMBAlert ******** ******** --------
Load Ref Load Td Td Td
Name No. Max Min (ms)
------------- ---------- -------- -------- ---------
12V 3 100.00 1.00 1.65
12Vsb 0 ******** ******** --------
PWOK 1 -100.00 -1.00 -1.65
Vin_Good 0 ******** ******** --------
SMBAlert 0 ******** ******** --------
STEP.296(UUT Test seq.296) : I2C Read Status Multi_S6(StandBy) ---- (0'125) PASS
Adderss :B0
Command Page00 :060200
Command Page01 :060201
Status Word :79
Status Byte :78
Status VOUT :7A
Status IOUT :7B
Status INPUT :7C
Status TEMPERATURE :7D
Status CML :7E
Status FANS :81
---------------------------------
Word SPEC: 16392
Word SPEC: 16392
Word SPEC: 16392
Word SPEC: 16392
Word SPEC: 16392
Word SPEC: 16392
Word SPEC: 16392
Word SPEC: 16392
Word SPEC_Page1: 16392
Word SPEC_Page1: 16392
Word SPEC_Page1: 16392
Word SPEC_Page1: 16392
Word SPEC_Page1: 16392
Word SPEC_Page1: 16392
Word SPEC_Page1: 16392
Word SPEC_Page1: 16392
Byte SPEC : 64
Byte SPEC : 64
Byte SPEC : 64
Byte SPEC : 64
Byte SPEC : 64
Byte SPEC : 64
Byte SPEC : 64
Byte SPEC : 64
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
----------------------------------
Word_Page_00 : 16392
Word_Page_01 : 16392
Status_Byte_P00 : 64
Status_Byte_P01 : 64
Status_VOUT_P00 : 0
Status_VOUT_P01 : 0
Status_IOUT_P00 : 0
Status_IOUT_P01 : 0
Status_INPUT_P00 : 0
Status_INPUT_P01 : 0
Status_TEM_P00 : 0
Status_TEM_P01 : 0
Status_CML_P00 : 0
Status_CML_P01 : 0
Status_FANS_P00 : 0
Status_FANS_P01 : 0
STEP.297(UUT Test seq.297) : PS ON Delay time 80611(220V_50Hz_HH) ---- (0'9 PASS
Vin (V)= Refer to the previous item
Fin (Hz)= Refer to the previous item
On Phase Delay(ms)= Refer to the previous item
UUT Off Time (s)= Refer to the previous item
Loading (A/Ohm/V)= Refer to the previous item
Trigger: 1:Trig1R(AC), 2:Trig2R(PS on), 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:Trig1F(AC), 9:Trig2F(PS on),10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1
2 1
3 1
4 1
Load Start End VcmpA VcmpB
Name Trigger Trigger (V) (V)
------------- ------- ------- ------- -------
12V 9 5 11.590 12.810
12Vsb 9 9 11.400 12.600
PWOK 9 5 2.600 2.600
Vin_Good 9 9 2.600 2.600
SMBAlert 9 9 2.600 2.600
Load Ton Ton Ton
Name Max Min (ms)
------------- -------- -------- ---------
12V 400.00 5.00 62.72
12Vsb ******** ******** 0.17
PWOK ******** ******** 268.18
Vin_Good ******** ******** 0.17
SMBAlert ******** ******** 0.17
Load Ref Load Td Td Td
Name No. Max Min (ms)
------------- ---------- -------- -------- ---------
12V 3 -500.000 -100.000 -205.457
12Vsb 0 ********* ********* 0.170
PWOK 1 500.000 100.000 205.457
Vin_Good 0 ********* ********* 0.170
SMBAlert 0 ********* ********* 0.170
STEP.298(UUT Test seq.298) : Turn On Timing Test_Multi or Single(220V_50Hz_ PASS
ElaspedTime (S)= 2'122
Vin (V)= 220.00
Fin (Hz)= 50.00
On Phase Delay(ms)= 90.00
UUT Off Time (s)= 0.50
Trigger: 1:TTL1R, 2:TTL2R, 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:TTL1F, 9:TTL2F,10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1.00
2 1.00
3 1.00
4 1.00
Load Loading Start End VcmpA VcmpB
Name (A/Ohm/V) Trigger Trigger (V) (V)
------------- ---------- ------- ------- ------- -------
12V 161.500 5 6 1.220 11.590
12Vsb 2.500 5 6 1.200 10.800
PWOK 0.000 8 1 2.600 3.460
Vin_Good 0.000 8 1 2.600 3.460
SMBAlert 0.000 8 1 2.600 3.460
Load Ton Ton Ton
Name Max Min (ms)
------------- -------- -------- ---------
12V 70.00 5.00 51.25
12Vsb 70.00 1.00 11.74
PWOK ******** ******** 0.06
Vin_Good ******** ******** 0.06
SMBAlert ******** ******** 0.06
Load Ref Load Td Td Td
Name No. Max Min (ms)
------------- ------------- -------- -------- ---------
12V 0 ******** ******** 51.25
12Vsb 0 ******** ******** 11.74
PWOK 0 ******** ******** 0.06
Vin_Good 0 ******** ******** 0.06
SMBAlert 0 ******** ******** 0.06
STEP.299(UUT Test seq.299) : TTL & Relay Setup ---- (0'000) --------------- PASS
(The Report Format of this Sequence was not found)
STEP.300(UUT Test seq.300) : PS ON Delay time 80611(220V_50Hz_HH_Tpson_12V_ PASS
Vin (V)= Refer to the previous item
Fin (Hz)= Refer to the previous item
On Phase Delay(ms)= Refer to the previous item
UUT Off Time (s)= Refer to the previous item
Loading (A/Ohm/V)= Refer to the previous item
Trigger: 1:Trig1R(AC), 2:Trig2R(PS on), 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:Trig1F(AC), 9:Trig2F(PS on),10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1
2 1
3 1
4 1
Load Start End VcmpA VcmpB
Name Trigger Trigger (V) (V)
------------- ------- ------- ------- -------
12V 5 6 1.220 11.590
12Vsb 9 9 1.200 10.800
PWOK 9 9 2.600 2.600
Vin_Good 9 9 2.600 2.600
SMBAlert 9 9 2.600 2.600
Load Ton Ton Ton
Name Max Min (ms)
------------- -------- -------- ---------
12V 70.00 5.00 51.25
12Vsb ******** ******** 0.16
PWOK ******** ******** 0.16
Vin_Good ******** ******** 0.16
SMBAlert ******** ******** 0.16
Load Ref Load Td Td Td
Name No. Max Min (ms)
------------- ---------- -------- -------- ---------
12V 0 ********* ********* 51.247
12Vsb 0 ********* ********* 0.164
PWOK 0 ********* ********* 0.164
Vin_Good 0 ********* ********* 0.164
SMBAlert 0 ********* ********* 0.164
STEP.301(UUT Test seq.301) : Input Output Eff Noise Multi or Single(220V_50 PASS
ElapsedTime (S)= 2'340
Vin (V)= 220.00
Fin (Hz)= 50.00
Delay Time (ms)= 1000.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 161.500 ******* ******* 161.497
12Vsb 0.100 ******* ******* 0.100
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
-------Load---------------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V ???.??? ???.??? ???.???
12Vsb ???.??? ???.??? ???.???
PWOK ???.??? ???.??? ???.???
Vin_Good ???.??? ???.??? ???.???
SMBAlert ???.??? ???.??? ???.???
--------34970----------------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 12.810 11.590 12.164
12VSb 12.600 11.400 12.120
PWOK 3.460 2.500 3.228
Vin_Good 3.460 2.500 3.222
SMBAlert 3.460 2.500 3.223
IBUS ******* ******* 8.002
CR 0.400 ******* -0.020
Max Min Reading
------------- ---------- ---------- ----------
Vrms (V) ******** ******** 219.4017
PF 1.0000 ******** 0.9987
THDi (%) ******** * 2.4047
Irms (A) ******** ******** 9.9216
Pin (W) ******** ******** XXXXXXXX
Pout (W) ******** ******** XXXXXXXX
Eff (%) ******** ******** 90.4172
Load Noise Range Noise B.W
Name (V) (MHz)
------------- ----------- ---------
12V 2 20.000
12Vsb 2 20.000
PWOK 2 20.000
Vin_Good 2 20.000
SMBAlert 2 20.000
Load Vpp Noise Vpp Noise Vpp Noise
Name Max(mV) Min(mV) (mV)
------------- ------------ ------------ ------------
12V 120.000 0.000 15.600
12Vsb 120.000 0.000 7.750
PWOK ********* ********* 24.830
Vin_Good ********* ********* 23.140
SMBAlert ********* ********* 26.970
STEP.302(UUT Test seq.302) : Static ACDC 34970_or_Load_Multi or Single(220V PASS
ElapsedTime (S)= 1'217
Vin (V)= 220.00
Fin (Hz)= 50.00
Delay Time (ms)= 500.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 161.500 ******* ******* 161.497
12Vsb 2.750 ******* ******* 2.750
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 12.810 11.590 12.164
12VSb 12.600 11.400 11.984
PWOK 3.460 2.500 3.221
Vin_Good 3.460 2.500 3.227
SMBAlert 3.460 2.500 3.220
IBUS ******* ******* 8.002
CR 0.400 ******* -0.022
Max Min Reading
------------- --------- --------- ---------
Pout (W) ******* ******* XXXXXXX
STEP.303(UUT Test seq.303) : Static ACDC 34970_or_Load_Multi or Single(220V PASS
ElapsedTime (S)= 1'420
Vin (V)= 220.00
Fin (Hz)= 50.00
Delay Time (ms)= 500.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 161.500 ******* ******* 0.000
12Vsb 3.650 ******* ******* 0.009
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 0.400 ******* 0.001
12VSb 12.600 ******* 11.977
PWOK 0.400 ******* 0.039
Vin_Good 3.460 2.400 3.242
SMBAlert 3.460 ******* 3.216
IBUS ******* ******* 0.159
CR 0.400 ******* 0.004
Max Min Reading
------------- --------- --------- ---------
Pout (W) ******* ******* 0.113
STEP.304(UUT Test seq.304) : Static ACDC 34970_or_Load_Multi or Single(220V PASS
ElapsedTime (S)= 1'872
Vin (V)= 220.00
Fin (Hz)= 50.00
Delay Time (ms)= 1000.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 161.500 ******* ******* 161.497
12Vsb 2.750 ******* ******* 2.750
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 12.810 11.590 12.157
12VSb 12.600 11.400 11.988
PWOK 3.460 2.500 3.219
Vin_Good 3.460 2.500 3.222
SMBAlert 3.460 2.500 3.226
IBUS ******* ******* 7.998
CR 0.400 ******* -0.022
Max Min Reading
------------- --------- --------- ---------
Pout (W) ******* ******* XXXXXXX
STEP.305(UUT Test seq.305) : Cold Redundant Master Multi _S2 ---- (0'094) - PASS
(The Report Format of this Sequence was not found)
STEP.306(UUT Test seq.306) : Static ACDC 34970_or_Load_Multi or Single(220V PASS
ElapsedTime (S)= 1'248
Vin (V)= 220.00
Fin (Hz)= 50.00
Delay Time (ms)= 500.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 161.500 ******* ******* 161.497
12Vsb 2.500 ******* ******* 2.500
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 12.810 11.590 12.163
12VSb 12.600 11.400 11.995
PWOK 3.460 2.500 3.218
Vin_Good 3.460 2.500 3.223
SMBAlert 3.460 2.500 3.220
IBUS ******* ******* 8.003
CR 3.460 2.500 3.166
Max Min Reading
------------- --------- --------- ---------
Pout (W) ******* ******* XXXXXXX
STEP.307(UUT Test seq.307) : Disable Cold Redundant Master Multi_S2 ---- (0 PASS
(The Report Format of this Sequence was not found)
STEP.308(UUT Test seq.308) : Static ACDC 34970_or_Load_Multi or Single(220V PASS
ElapsedTime (S)= 1'263
Vin (V)= 220.00
Fin (Hz)= 50.00
Delay Time (ms)= 500.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 161.500 ******* ******* 161.497
12Vsb 2.500 ******* ******* 2.500
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 12.810 11.590 12.165
12VSb 12.600 11.400 11.995
PWOK 3.460 2.500 3.221
Vin_Good 3.460 2.500 3.224
SMBAlert 3.460 2.500 3.226
IBUS ******* ******* 8.004
CR 0.400 ******* -0.022
Max Min Reading
------------- --------- --------- ---------
Pout (W) ******* ******* XXXXXXX
STEP.309(UUT Test seq.309) : Input Output Eff Noise Multi or Single(220V_50 PASS
ElapsedTime (S)= 2'246
Vin (V)= 220.00
Fin (Hz)= 50.00
Delay Time (ms)= 1000.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 161.500 ******* ******* 161.497
12Vsb 2.500 ******* ******* 2.500
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
-------Load---------------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V ???.??? ???.??? ???.???
12Vsb ???.??? ???.??? ???.???
PWOK ???.??? ???.??? ???.???
Vin_Good ???.??? ???.??? ???.???
SMBAlert ???.??? ???.??? ???.???
--------34970----------------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 12.810 11.590 12.163
12VSb 12.600 11.400 11.995
PWOK 3.460 2.500 3.222
Vin_Good 3.460 2.500 3.226
SMBAlert 3.460 2.500 3.224
IBUS ******* ******* 8.002
CR 0.400 ******* -0.022
Max Min Reading
------------- ---------- ---------- ----------
Vrms (V) ******** ******** 219.3929
PF 1.0000 ******** 0.9987
THDi (%) ******** * 2.4246
Irms (A) ******** ******** 10.0989
Pin (W) ******** ******** XXXXXXXX
Pout (W) ******** ******** XXXXXXXX
Eff (%) ******** ******** 90.1239
Load Noise Range Noise B.W
Name (V) (MHz)
------------- ----------- ---------
12V 2 20.000
12Vsb 2 20.000
PWOK 2 20.000
Vin_Good 2 20.000
SMBAlert 2 20.000
Load Vpp Noise Vpp Noise Vpp Noise
Name Max(mV) Min(mV) (mV)
------------- ------------ ------------ ------------
12V 120.000 0.000 14.910
12Vsb 120.000 0.000 15.180
PWOK ********* ********* 24.980
Vin_Good ********* ********* 23.580
SMBAlert ********* ********* 27.990
STEP.310(UUT Test seq.310) : Static ACDC 34970_or_Load_Multi or Single(220V PASS
ElapsedTime (S)= 3'728
Vin (V)= 220.00
Fin (Hz)= 50.00
Delay Time (ms)= 3000.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 185.380 ******* ******* 185.382
12Vsb 2.500 ******* ******* 2.500
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 12.810 11.590 12.153
12VSb 12.600 11.400 11.992
PWOK 3.460 2.500 3.220
Vin_Good 3.460 2.500 3.220
SMBAlert 3.460 ******* 3.224
IBUS ******* ******* 9.016
CR 0.400 ******* -0.026
Max Min Reading
------------- --------- --------- ---------
Pout (W) ******* ******* XXXXXXX
STEP.311(UUT Test seq.311) : TTL & Relay Setup(PS OnOff) ---- (1'029) ----- PASS
(The Report Format of this Sequence was not found)
STEP.312(UUT Test seq.312) : Peak_Load_S3_Multi_S(220V-OCP1_HL_Delay time 5 PASS
ElapsedTime (S)= 8'409
Vin (V)= Refer to the previous item
Fin (Hz)= Refer to the previous item
Delay Time (ms)= 2000.00
Load Setting Time (ms)= 2000.00
Measurement Delay Time (ms)= 3000.00
Turn On Delay Time (ms)= 3000.00
Loading Loading
Name (A/Ohm/V)
------------- ----------
12V 161.500
12Vsb 0.100
PWOK 0.000
Vin_Good 0.000
SMBAlert 0.000
12V_Loading_level Dell_Time Rise Rate Fall Rate
(A) (ms) (A/us) (A/us)
------------------ --------- --------- ---------
120.000 500.000 2.5000 2.5000
161.500 500.000 2.5000 2.5000
209.950 50.200 2.5000 2.5000
161.500 500.000 2.5000 2.5000
Load Vpk Max Vpk Min Vpk High Vpk Low
Name (V) (V) (V) (V)
------------- --------- --------- --------- ---------
12V 12.810 11.590 12.235 12.086
12Vsb 12.600 11.400 12.147 12.134
PWOK 3.460 2.500 3.260 3.259
Vin_Good 3.460 2.500 3.254 3.246
SMBAlert 3.460 ********* 3.264 0.078
STEP.313(UUT Test seq.313) : Peak_Load_S3_Multi_S(220V-OCP1_HH_Delay time 5 PASS
ElapsedTime (S)= 8'486
Vin (V)= Refer to the previous item
Fin (Hz)= Refer to the previous item
Delay Time (ms)= 2000.00
Load Setting Time (ms)= 2000.00
Measurement Delay Time (ms)= 3000.00
Turn On Delay Time (ms)= 3000.00
Loading Loading
Name (A/Ohm/V)
------------- ----------
12V 161.500
12Vsb 2.500
PWOK 0.000
Vin_Good 0.000
SMBAlert 0.000
12V_Loading_level Dell_Time Rise Rate Fall Rate
(A) (ms) (A/us) (A/us)
------------------ --------- --------- ---------
120.000 500.000 2.5000 2.5000
161.500 500.000 2.5000 2.5000
209.950 50.200 2.5000 2.5000
161.500 500.000 2.5000 2.5000
Load Vpk Max Vpk Min Vpk High Vpk Low
Name (V) (V) (V) (V)
------------- --------- --------- --------- ---------
12V 12.810 11.590 12.229 12.080
12Vsb 12.600 11.400 12.025 12.007
PWOK 3.460 2.500 3.259 3.257
Vin_Good 3.460 2.500 3.253 3.244
SMBAlert 3.460 ********* 0.095 0.062
STEP.314(UUT Test seq.314) : Peak_Load_S3_Multi_S(220V-OCP2_HL_Delay time 0 PASS
ElapsedTime (S)= 8'377
Vin (V)= Refer to the previous item
Fin (Hz)= Refer to the previous item
Delay Time (ms)= 2000.00
Load Setting Time (ms)= 2000.00
Measurement Delay Time (ms)= 3000.00
Turn On Delay Time (ms)= 3000.00
Loading Loading
Name (A/Ohm/V)
------------- ----------
12V 161.500
12Vsb 0.100
PWOK 0.000
Vin_Good 0.000
SMBAlert 0.000
12V_Loading_level Dell_Time Rise Rate Fall Rate
(A) (ms) (A/us) (A/us)
------------------ --------- --------- ---------
120.000 500.000 2.5000 2.5000
161.500 500.000 2.5000 2.5000
324.615 0.120 2.5000 2.5000
161.500 500.000 2.5000 2.5000
Load Vpk Max Vpk Min Vpk High Vpk Low
Name (V) (V) (V) (V)
------------- --------- --------- --------- ---------
12V 12.960 11.000 12.245 11.932
12Vsb 12.600 11.400 12.149 12.136
PWOK 3.460 2.500 3.261 3.262
Vin_Good 3.460 2.500 3.254 3.250
SMBAlert 3.460 ********* 0.120 0.028
STEP.315(UUT Test seq.315) : Peak_Load_S3_Multi_S(220V-OCP2_HH_Delay time 0 PASS
ElapsedTime (S)= 8'471
Vin (V)= Refer to the previous item
Fin (Hz)= Refer to the previous item
Delay Time (ms)= 2000.00
Load Setting Time (ms)= 2000.00
Measurement Delay Time (ms)= 3000.00
Turn On Delay Time (ms)= 3000.00
Loading Loading
Name (A/Ohm/V)
------------- ----------
12V 161.500
12Vsb 2.500
PWOK 0.000
Vin_Good 0.000
SMBAlert 0.000
12V_Loading_level Dell_Time Rise Rate Fall Rate
(A) (ms) (A/us) (A/us)
------------------ --------- --------- ---------
120.000 500.000 2.5000 2.5000
161.500 500.000 2.5000 2.5000
324.615 0.120 2.5000 2.5000
161.500 500.000 2.5000 2.5000
Load Vpk Max Vpk Min Vpk High Vpk Low
Name (V) (V) (V) (V)
------------- --------- --------- --------- ---------
12V 12.960 11.000 12.247 11.930
12Vsb 12.600 11.400 12.025 12.004
PWOK 3.460 2.500 3.259 3.262
Vin_Good 3.460 2.500 3.253 3.250
SMBAlert 3.460 ********* 0.117 0.030
STEP.316(UUT Test seq.316) : Set Input Condition Multi_S4_4(220V_50Hz) ---- PASS
Input Voltage Type (Vac=0 ; Vdc=1) = 0
Vin = 220.000
Fin = 50.000
Vin_DC_Positive_Negative(Positive=0 ; Negative=1) = 0
STEP.317(UUT Test seq.317) : Set Dynamic_Time ---- (0'000) ---------------- PASS
ElapsedTime (S)= 0'000
Delay Time (ms)= 3000.00
Measurement Time (ms) = 1000.00
UUT Off Time (s)= 3.00
STEP.318(UUT Test seq.318) : SetAllLoad_SlewRate_S ---- (0'094) ----------- PASS
STEP.319(UUT Test seq.319) : Sync_Dynamic_80611_20200716_Multi_S(220V-OCP_1 PASS
ElapsedTime (S)= 4'711
Vin (V)= Refer to previous item
Fin (Hz)= Refer to previous item
Duration-1 (ms)= 100.0000
Duration-2 (ms) = 50.2000
Load Loading-1 Loading-2 Vstable+ Vstable-
Name (A) (A) (V) (V)
------------- --------- --------- --------- ---------
12V 1.000 1.000 -------- --------
12Vsb 2.750 3.650 -------- --------
PWOK 0.000 0.000 -------- --------
Vin_Good 0.000 0.000 -------- --------
SMBAlert 0.000 0.000 -------- --------
Load Vpk+ Max Vpk+ Min Vpk High Vpk- Max Vpk- Min Vpk Low
Name (V) (V) (V) (V) (V) (V)
------------- --------- --------- --------- --------- --------- ---------
12V 12.810 11.590 12.273 12.810 11.590 12.259
12Vsb 12.600 11.400 12.026 12.600 11.400 12.008
PWOK 3.460 2.500 3.272 3.460 2.500 3.288
Vin_Good 3.460 2.500 3.266 3.460 2.500 3.271
SMBAlert 3.460 2.500 3.251 3.460 2.500 3.256
Load Vspk+ Max Vspk+ Min Vspk High Vspk- Max Vspk- Min Vspk Low
Name (V) (V) (mV) (V) (V) (mV)
------------- ---------- ---------- ---------- ---------- ---------- ----------
12V ******** ******** -------- ******** ******** --------
12Vsb ******** ******** -------- ******** ******** --------
PWOK ******** ******** -------- ******** ******** --------
Vin_Good ******** ******** -------- ******** ******** --------
SMBAlert ******** ******** -------- ******** ******** --------
STEP.320(UUT Test seq.320) : Sync_Dynamic_80611_20200716_Multi_S(220V-OCP_1 PASS
ElapsedTime (S)= 4'711
Vin (V)= Refer to previous item
Fin (Hz)= Refer to previous item
Duration-1 (ms)= 100.0000
Duration-2 (ms) = 50.2000
Load Loading-1 Loading-2 Vstable+ Vstable-
Name (A) (A) (V) (V)
------------- --------- --------- --------- ---------
12V 161.500 161.500 -------- --------
12Vsb 2.750 3.650 -------- --------
PWOK 0.000 0.000 -------- --------
Vin_Good 0.000 0.000 -------- --------
SMBAlert 0.000 0.000 -------- --------
Load Vpk+ Max Vpk+ Min Vpk High Vpk- Max Vpk- Min Vpk Low
Name (V) (V) (V) (V) (V) (V)
------------- --------- --------- --------- --------- --------- ---------
12V 12.810 11.590 12.179 12.810 11.590 12.165
12Vsb 12.600 11.400 12.014 12.600 11.400 11.991
PWOK 3.460 2.500 3.247 3.460 2.500 3.264
Vin_Good 3.460 2.500 3.241 3.460 2.500 3.250
SMBAlert 3.460 2.500 3.259 3.460 2.500 3.268
Load Vspk+ Max Vspk+ Min Vspk High Vspk- Max Vspk- Min Vspk Low
Name (V) (V) (mV) (V) (V) (mV)
------------- ---------- ---------- ---------- ---------- ---------- ----------
12V ******** ******** -------- ******** ******** --------
12Vsb ******** ******** -------- ******** ******** --------
PWOK ******** ******** -------- ******** ******** --------
Vin_Good ******** ******** -------- ******** ******** --------
SMBAlert ******** ******** -------- ******** ******** --------
STEP.321(UUT Test seq.321) : Sync_Dynamic_80611_20200716_Multi_S(220V-Fast PASS
ElapsedTime (S)= 4'930
Vin (V)= Refer to previous item
Fin (Hz)= Refer to previous item
Duration-1 (ms)= 500.0000
Duration-2 (ms) = 5.0000
Load Loading-1 Loading-2 Vstable+ Vstable-
Name (A) (A) (V) (V)
------------- --------- --------- --------- ---------
12V 161.500 209.950 -------- --------
12Vsb 2.500 2.500 -------- --------
PWOK 0.000 0.000 -------- --------
Vin_Good 0.000 0.000 -------- --------
SMBAlert 0.000 0.000 -------- --------
Load Vpk+ Max Vpk+ Min Vpk High Vpk- Max Vpk- Min Vpk Low
Name (V) (V) (V) (V) (V) (V)
------------- --------- --------- --------- --------- --------- ---------
12V ******** ******** -------- ******** ******** ---------
12Vsb ******** ******** -------- ******** ******** ---------
PWOK ******** ******** -------- ******** ******** ---------
Vin_Good ******** ******** -------- ******** ******** ---------
SMBAlert ******** ******** -------- ******** ******** ---------
Load Vspk+ Max Vspk+ Min Vspk High Vspk- Max Vspk- Min Vspk Low
Name (V) (V) (mV) (V) (V) (mV)
------------- ---------- ---------- ---------- ---------- ---------- ----------
12V ******** ******** -------- ******** ******** --------
12Vsb ******** ******** -------- ******** ******** --------
PWOK ******** ******** -------- ******** ******** --------
Vin_Good ******** ******** -------- ******** ******** --------
SMBAlert ******** ******** -------- ******** ******** --------
STEP.322(UUT Test seq.322) : PS ON Delay time 80611(220V-Fast OCW_SMBAlert) PASS
Vin (V)= Refer to the previous item
Fin (Hz)= Refer to the previous item
On Phase Delay(ms)= Refer to the previous item
UUT Off Time (s)= Refer to the previous item
Loading (A/Ohm/V)= Refer to the previous item
Trigger: 1:Trig1R(AC), 2:Trig2R(PS on), 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:Trig1F(AC), 9:Trig2F(PS on),10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1
2 1
3 1
4 1
Load Start End VcmpA VcmpB
Name Trigger Trigger (V) (V)
------------- ------- ------- ------- -------
12V 1 1 11.590 12.810
12Vsb 1 1 11.400 12.600
PWOK 1 1 2.600 2.600
Vin_Good 1 1 2.600 2.600
SMBAlert 12 5 2.600 2.600
Load Ton Ton Ton
Name Max Min (ms)
------------- -------- -------- ---------
12V ******** ******** --------
12Vsb ******** ******** --------
PWOK ******** ******** --------
Vin_Good ******** ******** --------
SMBAlert 150.00 50.00 107.78
Load Ref Load Td Td Td
Name No. Max Min (ms)
------------- ---------- -------- -------- ---------
12V 0 ********* ********* ---------
12Vsb 0 ********* ********* ---------
PWOK 0 ********* ********* ---------
Vin_Good 0 ********* ********* ---------
SMBAlert 0 ********* ********* 107.781
STEP.323(UUT Test seq.323) : Sync_Dynamic_80611_20200716_Multi_S(220V-Fast PASS
ElapsedTime (S)= 5'054
Vin (V)= Refer to previous item
Fin (Hz)= Refer to previous item
Duration-1 (ms)= 200.0000
Duration-2 (ms) = 30.0000
Load Loading-1 Loading-2 Vstable+ Vstable-
Name (A) (A) (V) (V)
------------- --------- --------- --------- ---------
12V 161.500 209.950 -------- --------
12Vsb 2.500 2.500 -------- --------
PWOK 0.000 0.000 -------- --------
Vin_Good 0.000 0.000 -------- --------
SMBAlert 0.000 0.000 -------- --------
Load Vpk+ Max Vpk+ Min Vpk High Vpk- Max Vpk- Min Vpk Low
Name (V) (V) (V) (V) (V) (V)
------------- --------- --------- --------- --------- --------- ---------
12V 12.810 11.590 12.217 12.810 11.590 12.089
12Vsb 12.600 11.400 12.016 12.600 11.400 12.008
PWOK 3.460 2.500 3.247 3.460 2.500 3.254
Vin_Good 3.460 2.500 3.242 3.460 2.500 3.244
SMBAlert 3.460 ******** 3.250 3.460 ******** 0.086
Load Vspk+ Max Vspk+ Min Vspk High Vspk- Max Vspk- Min Vspk Low
Name (V) (V) (mV) (V) (V) (mV)
------------- ---------- ---------- ---------- ---------- ---------- ----------
12V ******** ******** -------- ******** ******** --------
12Vsb ******** ******** -------- ******** ******** --------
PWOK ******** ******** -------- ******** ******** --------
Vin_Good ******** ******** -------- ******** ******** --------
SMBAlert ******** ******** -------- ******** ******** --------
STEP.324(UUT Test seq.324) : Hold Up Timing Test_Multi or Single(220V_50Hz_ PASS
ElapsedTime (S)= 0'999
Vin (V)= 220.00
Fin (Hz)= 50.00
Delay Time (ms)= 200.00
On Phase Delay(ms)= 90.00
UUT Off Time (s)= 0.00
Trigger: 1:Trig1R(AC), 2:Trig2R(PS on), 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:Trig1F(AC), 9:Trig2F(PS on),10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1
2 1
3 1
4 1
Load Loading Start End VcmpA VcmpB
Name (A/Ohm/V) Trigger Trigger (V) (V)
------------- ---------- ------- ------- ------- -------
12V 113.050 8 12 11.590 12.810
12Vsb 1.750 8 12 11.400 12.600
PWOK 0.000 8 12 2.600 3.460
Vin_Good 0.000 8 12 2.600 3.460
SMBAlert 0.000 8 1 2.600 3.460
Load Tholdup Tholdup Tholdup
Name Max Min (ms)
------------- -------- -------- ---------
12V 1000.00 10.00 21.76
12Vsb 1000.00 70.00 78.50
PWOK 300.00 9.00 20.09
Vin_Good 4.00 0.01 2.74
SMBAlert ******** ******** 0.06
Load Ref Load Tholdup Tholdup Tholdup
Name No. Max Min (ms)
------------- ---------- -------- -------- ---------
12V 3 100.00 1.00 1.67
12Vsb 0 ******** ******** 78.50
PWOK 1 -100.00 -1.00 -1.67
Vin_Good 0 ******** ******** 2.74
SMBAlert 0 ******** ******** 0.06
STEP.325(UUT Test seq.325) : FAN Full Speed delay time Multi ---- (8'096) - PASS
STEP.326(UUT Test seq.326) : FAN Speed Normal_Multi ---- (0'109) ---------- PASS
(The Report Format of this Sequence was not found)
STEP.327(UUT Test seq.327) : Turn On Timing Test_Multi or Single(264V_63Hz_ PASS
ElaspedTime (S)= 1'654
Vin (V)= 264.00
Fin (Hz)= 63.00
On Phase Delay(ms)= 90.00
UUT Off Time (s)= 0.00
Trigger: 1:TTL1R, 2:TTL2R, 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:TTL1F, 9:TTL2F,10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1.00
2 1.00
3 1.00
4 1.00
Load Loading Start End VcmpA VcmpB
Name (A/Ohm/V) Trigger Trigger (V) (V)
------------- ---------- ------- ------- ------- -------
12V 1.000 8 5 11.590 12.810
12Vsb 0.100 8 5 11.400 12.600
PWOK 0.000 8 5 2.600 3.460
Vin_Good 0.000 8 1 2.600 3.460
SMBAlert 0.000 8 1 2.600 3.460
Load Ton Ton Ton
Name Max Min (ms)
------------- -------- -------- ---------
12V 3000.00 1.00 927.59
12Vsb 1500.00 1.00 683.05
PWOK ******** ******** 1133.53
Vin_Good ******** ******** 0.06
SMBAlert ******** ******** 0.06
Load Ref Load Td Td Td
Name No. Max Min (ms)
------------- ------------- -------- -------- ---------
12V 3 -500.00 -100.00 -205.94
12Vsb 1 -1500.00 -50.00 -244.54
PWOK 1 500.00 100.00 205.94
Vin_Good 0 ******** ******** 0.06
SMBAlert 0 ******** ******** 0.06
STEP.328(UUT Test seq.328) : PS OFF Time 80611(264V_63Hz_LL) ---- (1'591) - PASS
Vin (V)= Refer to the previous item
Fin (Hz)= Refer to the previous item
On Phase Delay(ms)= Refer to the previous item
UUT Off Time (s)= Refer to the previous item
Loading (A/Ohm/V)= Refer to the previous item
Trigger: 1:Trig1R(AC), 2:Trig2R(PS on), 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:Trig1F(AC), 9:Trig2F(PS on),10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1
2 1
3 1
4 1
Load Start End VcmpA VcmpB
Name Trigger Trigger (V) (V)
------------- ------- ------- ------- -------
12V 2 12 11.590 12.810
12Vsb 2 2 11.400 12.600
PWOK 2 12 2.600 2.600
Vin_Good 2 2 2.600 2.600
SMBAlert 2 2 2.600 2.600
Load Ton Ton Ton
Name Max Min (ms)
------------- -------- -------- ---------
12V ******** ******** 5.60
12Vsb ******** ******** --------
PWOK 50.00 0.01 0.67
Vin_Good ******** ******** --------
SMBAlert ******** ******** --------
Load Ref Load Td Td Td
Name No. Max Min (ms)
------------- ---------- -------- -------- ---------
12V 3 100.00 1.00 4.93
12Vsb 0 ******** ******** --------
PWOK 1 -100.00 -1.00 -4.93
Vin_Good 0 ******** ******** --------
SMBAlert 0 ******** ******** --------
STEP.329(UUT Test seq.329) : I2C Read Status Multi_S6(StandBy) ---- (0'140) PASS
Adderss :B0
Command Page00 :060200
Command Page01 :060201
Status Word :79
Status Byte :78
Status VOUT :7A
Status IOUT :7B
Status INPUT :7C
Status TEMPERATURE :7D
Status CML :7E
Status FANS :81
---------------------------------
Word SPEC: 16392
Word SPEC: 16392
Word SPEC: 16392
Word SPEC: 16392
Word SPEC: 16392
Word SPEC: 16392
Word SPEC: 16392
Word SPEC: 16392
Word SPEC_Page1: 16392
Word SPEC_Page1: 16392
Word SPEC_Page1: 16392
Word SPEC_Page1: 16392
Word SPEC_Page1: 16392
Word SPEC_Page1: 16392
Word SPEC_Page1: 16392
Word SPEC_Page1: 16392
Byte SPEC : 64
Byte SPEC : 64
Byte SPEC : 64
Byte SPEC : 64
Byte SPEC : 64
Byte SPEC : 64
Byte SPEC : 64
Byte SPEC : 64
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
----------------------------------
Word_Page_00 : 16392
Word_Page_01 : 16392
Status_Byte_P00 : 64
Status_Byte_P01 : 64
Status_VOUT_P00 : 0
Status_VOUT_P01 : 0
Status_IOUT_P00 : 0
Status_IOUT_P01 : 0
Status_INPUT_P00 : 0
Status_INPUT_P01 : 0
Status_TEM_P00 : 0
Status_TEM_P01 : 0
Status_CML_P00 : 0
Status_CML_P01 : 0
Status_FANS_P00 : 0
Status_FANS_P01 : 0
STEP.330(UUT Test seq.330) : Input Output Eff Noise Multi or Single(264V_63 PASS
ElapsedTime (S)= 1'950
Vin (V)= 264.00
Fin (Hz)= 63.00
Delay Time (ms)= 500.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 0.000 ******* ******* 0.000
12Vsb 0.000 ******* ******* 0.000
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
-------Load---------------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V ???.??? ???.??? ???.???
12Vsb ???.??? ???.??? ???.???
PWOK ???.??? ???.??? ???.???
Vin_Good ???.??? ???.??? ???.???
SMBAlert ???.??? ???.??? ???.???
--------34970----------------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 0.400 ******* 0.147
12VSb 12.600 11.400 12.190
PWOK 0.400 ******* 0.039
Vin_Good 3.460 2.500 3.242
SMBAlert 3.460 2.500 3.219
IBUS ******* ******* 0.131
CR 0.400 ******* 0.003
Max Min Reading
------------- ---------- ---------- ----------
Vrms (V) ******** ******** 264.2561
PF 1.0000 ******** 0.1230
THDi (%) ******** * 18.6937
Irms (A) ******** ******** 0.1136
Pin (W) ******** ******** 3.6913
Pout (W) ******** ******** 0.0000
Eff (%) ******** ******** 0.0000
Load Noise Range Noise B.W
Name (V) (MHz)
------------- ----------- ---------
12V 2 20.000
12Vsb 2 20.000
PWOK 2 20.000
Vin_Good 2 20.000
SMBAlert 2 20.000
Load Vpp Noise Vpp Noise Vpp Noise
Name Max(mV) Min(mV) (mV)
------------- ------------ ------------ ------------
12V 120.000 0.000 1.150
12Vsb 120.000 0.000 5.820
PWOK ********* ********* 15.630
Vin_Good ********* ********* 20.350
SMBAlert ********* ********* 23.010
STEP.331(UUT Test seq.331) : Input Output Eff Noise Multi or Single(264V_63 PASS
ElapsedTime (S)= 1'997
Vin (V)= 264.00
Fin (Hz)= 63.00
Delay Time (ms)= 500.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 1.000 ******* ******* 0.000
12Vsb 2.500 ******* ******* 2.500
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
-------Load---------------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V ???.??? ???.??? ???.???
12Vsb ???.??? ???.??? ???.???
PWOK ???.??? ???.??? ???.???
Vin_Good ???.??? ???.??? ???.???
SMBAlert ???.??? ???.??? ???.???
--------34970----------------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 0.400 ******* 0.001
12VSb 12.600 11.400 12.011
PWOK 0.400 ******* 0.037
Vin_Good 3.460 2.500 3.247
SMBAlert 3.460 2.500 3.212
IBUS ******* ******* 0.325
CR 0.400 ******* 0.001
Max Min Reading
------------- ---------- ---------- ----------
Vrms (V) ******** ******** 264.2424
PF 1.0000 ******** 0.6416
THDi (%) ******** * 22.8777
Irms (A) ******** ******** 0.2432
Pin (W) ******** ******** 41.2251
Pout (W) ******** ******** 30.0242
Eff (%) ******** ******** 72.8299
Load Noise Range Noise B.W
Name (V) (MHz)
------------- ----------- ---------
12V 2 20.000
12Vsb 2 20.000
PWOK 2 20.000
Vin_Good 2 20.000
SMBAlert 2 20.000
Load Vpp Noise Vpp Noise Vpp Noise
Name Max(mV) Min(mV) (mV)
------------- ------------ ------------ ------------
12V 120.000 0.000 0.230
12Vsb 120.000 0.000 2.530
PWOK ********* ********* 18.360
Vin_Good ********* ********* 24.940
SMBAlert ********* ********* 23.110
STEP.332(UUT Test seq.332) : Static ACDC 34970_or_Load_Multi or Single(12Vs PASS
ElapsedTime (S)= 1'279
Vin (V)= 264.00
Fin (Hz)= 63.00
Delay Time (ms)= 500.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 0.000 ******* ******* 0.000
12Vsb 2.750 ******* ******* 2.750
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 0.400 ******* 0.001
12VSb 12.600 11.400 12.010
PWOK 0.400 ******* 0.037
Vin_Good 3.460 2.500 3.240
SMBAlert 3.460 2.500 3.219
IBUS ******* ******* 0.308
CR 0.400 ******* 0.001
Max Min Reading
------------- --------- --------- ---------
Pout (W) ******* ******* 33.025
STEP.333(UUT Test seq.333) : Static ACDC 34970_or_Load_Multi or Single(12Vs PASS
ElapsedTime (S)= 1'279
Vin (V)= 264.00
Fin (Hz)= 63.00
Delay Time (ms)= 500.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 0.000 ******* ******* 0.000
12Vsb 3.650 ******* ******* 3.650
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 0.400 ******* 0.000
12VSb 12.600 ******* 11.974
PWOK 0.400 ******* 0.036
Vin_Good 3.460 2.400 3.243
SMBAlert 3.460 ******* 3.213
IBUS ******* ******* 0.307
CR 0.400 ******* 0.005
Max Min Reading
------------- --------- --------- ---------
Pout (W) ******* ******* 43.704
STEP.334(UUT Test seq.334) : Static ACDC 34970_or_Load_Multi or Single(12Vs PASS
ElapsedTime (S)= 1'810
Vin (V)= 264.00
Fin (Hz)= 63.00
Delay Time (ms)= 1000.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 0.000 ******* ******* 0.000
12Vsb 2.750 ******* ******* 2.750
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 0.400 ******* 0.001
12VSb 12.600 11.400 12.008
PWOK 0.400 ******* 0.037
Vin_Good 3.460 2.500 3.241
SMBAlert 3.460 2.500 3.218
IBUS ******* ******* 0.349
CR 0.400 ******* 0.001
Max Min Reading
------------- --------- --------- ---------
Pout (W) ******* ******* 33.019
STEP.335(UUT Test seq.335) : Input Output Eff Noise Multi or Single(264V_63 PASS
ElapsedTime (S)= 1'826
Vin (V)= 264.00
Fin (Hz)= 63.00
Delay Time (ms)= 500.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 1.000 ******* ******* 0.000
12Vsb 0.100 ******* ******* 0.100
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
-------Load---------------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V ???.??? ???.??? ???.???
12Vsb ???.??? ???.??? ???.???
PWOK ???.??? ???.??? ???.???
Vin_Good ???.??? ???.??? ???.???
SMBAlert ???.??? ???.??? ???.???
--------34970----------------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 0.400 ******* 0.000
12VSb 12.600 11.400 12.148
PWOK 0.400 ******* 0.039
Vin_Good 3.460 2.500 3.245
SMBAlert 3.460 2.500 3.214
IBUS ******* ******* 0.343
CR 0.400 ******* 0.003
Max Min Reading
------------- ---------- ---------- ----------
Vrms (V) ******** ******** 264.2549
PF 1.0000 ******** 0.1654
THDi (%) ******** * 21.9056
Irms (A) ******** ******** 0.1182
Pin (W) ******** ******** 5.1685
Pout (W) ******** ******** 1.2172
Eff (%) ******** ******** 23.5499
Load Noise Range Noise B.W
Name (V) (MHz)
------------- ----------- ---------
12V 2 20.000
12Vsb 2 20.000
PWOK 2 20.000
Vin_Good 2 20.000
SMBAlert 2 20.000
Load Vpp Noise Vpp Noise Vpp Noise
Name Max(mV) Min(mV) (mV)
------------- ------------ ------------ ------------
12V 120.000 0.000 0.210
12Vsb 120.000 0.000 8.470
PWOK ********* ********* 15.920
Vin_Good ********* ********* 21.250
SMBAlert ********* ********* 22.750
STEP.336(UUT Test seq.336) : PS ON Delay time 80611 ---- (0'874) ---------- PASS
Vin (V)= Refer to the previous item
Fin (Hz)= Refer to the previous item
On Phase Delay(ms)= Refer to the previous item
UUT Off Time (s)= Refer to the previous item
Loading (A/Ohm/V)= Refer to the previous item
Trigger: 1:Trig1R(AC), 2:Trig2R(PS on), 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:Trig1F(AC), 9:Trig2F(PS on),10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1
2 1
3 1
4 1
Load Start End VcmpA VcmpB
Name Trigger Trigger (V) (V)
------------- ------- ------- ------- -------
12V 9 5 11.590 12.810
12Vsb 9 9 11.400 12.600
PWOK 9 5 2.600 2.600
Vin_Good 9 9 2.600 2.600
SMBAlert 9 9 2.600 2.600
Load Ton Ton Ton
Name Max Min (ms)
------------- -------- -------- ---------
12V 400.00 5.00 62.22
12Vsb ******** ******** 0.17
PWOK ******** ******** 268.07
Vin_Good ******** ******** 0.17
SMBAlert ******** ******** 0.17
Load Ref Load Td Td Td
Name No. Max Min (ms)
------------- ---------- -------- -------- ---------
12V 3 -500.000 -100.000 -205.846
12Vsb 0 ********* ********* 0.169
PWOK 1 500.000 100.000 205.846
Vin_Good 0 ********* ********* 0.169
SMBAlert 0 ********* ********* 0.169
STEP.337(UUT Test seq.337) : Turn On Timing Test_Multi or Single(264V_63Hz_ PASS
ElaspedTime (S)= 2'028
Vin (V)= 264.00
Fin (Hz)= 63.00
On Phase Delay(ms)= 90.00
UUT Off Time (s)= 0.50
Trigger: 1:TTL1R, 2:TTL2R, 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:TTL1F, 9:TTL2F,10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1.00
2 1.00
3 1.00
4 1.00
Load Loading Start End VcmpA VcmpB
Name (A/Ohm/V) Trigger Trigger (V) (V)
------------- ---------- ------- ------- ------- -------
12V 1.000 5 6 1.220 11.590
12Vsb 0.100 5 6 1.200 10.800
PWOK 0.000 8 1 2.600 3.460
Vin_Good 0.000 8 1 2.600 3.460
SMBAlert 0.000 8 1 2.600 3.460
Load Ton Ton Ton
Name Max Min (ms)
------------- -------- -------- ---------
12V 70.00 5.00 51.29
12Vsb 70.00 1.00 12.52
PWOK ******** ******** 0.06
Vin_Good ******** ******** 0.06
SMBAlert ******** ******** 0.06
Load Ref Load Td Td Td
Name No. Max Min (ms)
------------- ------------- -------- -------- ---------
12V 0 ******** ******** 51.29
12Vsb 0 ******** ******** 12.52
PWOK 0 ******** ******** 0.06
Vin_Good 0 ******** ******** 0.06
SMBAlert 0 ******** ******** 0.06
STEP.338(UUT Test seq.338) : TTL & Relay Setup ---- (0'000) --------------- PASS
(The Report Format of this Sequence was not found)
STEP.339(UUT Test seq.339) : PS ON Delay time 80611(264V_63Hz_LL_Tpson_12V_ PASS
Vin (V)= Refer to the previous item
Fin (Hz)= Refer to the previous item
On Phase Delay(ms)= Refer to the previous item
UUT Off Time (s)= Refer to the previous item
Loading (A/Ohm/V)= Refer to the previous item
Trigger: 1:Trig1R(AC), 2:Trig2R(PS on), 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:Trig1F(AC), 9:Trig2F(PS on),10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1
2 1
3 1
4 1
Load Start End VcmpA VcmpB
Name Trigger Trigger (V) (V)
------------- ------- ------- ------- -------
12V 5 6 1.220 11.590
12Vsb 9 9 1.200 10.800
PWOK 9 9 2.600 2.600
Vin_Good 9 9 2.600 2.600
SMBAlert 9 9 2.600 2.600
Load Ton Ton Ton
Name Max Min (ms)
------------- -------- -------- ---------
12V 70.00 5.00 51.30
12Vsb ******** ******** 0.17
PWOK ******** ******** 0.17
Vin_Good ******** ******** 0.17
SMBAlert ******** ******** 0.17
Load Ref Load Td Td Td
Name No. Max Min (ms)
------------- ---------- -------- -------- ---------
12V 0 ********* ********* 51.302
12Vsb 0 ********* ********* 0.168
PWOK 0 ********* ********* 0.168
Vin_Good 0 ********* ********* 0.168
SMBAlert 0 ********* ********* 0.168
STEP.340(UUT Test seq.340) : Input Output Eff Noise Multi or Single(No Load PASS
ElapsedTime (S)= 1'856
Vin (V)= 264.00
Fin (Hz)= 63.00
Delay Time (ms)= 500.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 0.000 ******* ******* 0.000
12Vsb 0.000 ******* ******* 0.000
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
-------Load---------------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V ???.??? ???.??? ???.???
12Vsb ???.??? ???.??? ???.???
PWOK ???.??? ???.??? ???.???
Vin_Good ???.??? ???.??? ???.???
SMBAlert ???.??? ???.??? ???.???
--------34970----------------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 12.810 11.590 12.259
12VSb 12.600 11.400 12.191
PWOK 3.460 2.500 3.244
Vin_Good 3.460 2.500 3.245
SMBAlert 3.460 2.500 3.218
IBUS 0.300 -0.300 0.017
CR 0.400 ******* 0.003
Max Min Reading
------------- ---------- ---------- ----------
Vrms (V) ******** ******** 264.2557
PF 1.0000 ******** 0.1011
THDi (%) ******** * 8.3869
Irms (A) ******** ******** 0.1124
Pin (W) ******** ******** 3.0050
Pout (W) ******** ******** 0.0000
Eff (%) ******** ******** 0.0000
Load Noise Range Noise B.W
Name (V) (MHz)
------------- ----------- ---------
12V 2 20.000
12Vsb 2 20.000
PWOK 2 20.000
Vin_Good 2 20.000
SMBAlert 2 20.000
Load Vpp Noise Vpp Noise Vpp Noise
Name Max(mV) Min(mV) (mV)
------------- ------------ ------------ ------------
12V 120.000 0.000 8.330
12Vsb 120.000 0.000 6.130
PWOK ********* ********* 20.410
Vin_Good ********* ********* 19.790
SMBAlert ********* ********* 22.690
STEP.341(UUT Test seq.341) : Static ACDC 34970_or_Load_Multi or Single(12Vs PASS
ElapsedTime (S)= 1'202
Vin (V)= 264.00
Fin (Hz)= 63.00
Delay Time (ms)= 500.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 1.000 ******* ******* 0.998
12Vsb 2.750 ******* ******* 2.750
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 12.810 11.590 12.262
12VSb 12.600 11.400 12.005
PWOK 3.460 2.500 3.249
Vin_Good 3.460 2.500 3.246
SMBAlert 3.460 2.500 3.214
IBUS ******* ******* 0.059
CR 0.400 ******* 0.001
Max Min Reading
------------- --------- --------- ---------
Pout (W) ******* ******* 45.244
STEP.342(UUT Test seq.342) : Static ACDC 34970_or_Load_Multi or Single(12Vs PASS
ElapsedTime (S)= 1'404
Vin (V)= 264.00
Fin (Hz)= 63.00
Delay Time (ms)= 500.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 1.000 ******* ******* 0.000
12Vsb 3.650 ******* ******* 0.011
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 0.400 ******* 0.001
12VSb 12.600 ******* 11.978
PWOK 0.400 ******* 0.038
Vin_Good 3.460 2.400 3.246
SMBAlert 3.460 ******* 3.216
IBUS ******* ******* 0.167
CR 0.400 ******* 0.005
Max Min Reading
------------- --------- --------- ---------
Pout (W) ******* ******* 0.130
STEP.343(UUT Test seq.343) : Static ACDC 34970_or_Load_Multi or Single(12Vs PASS
ElapsedTime (S)= 1'903
Vin (V)= 264.00
Fin (Hz)= 63.00
Delay Time (ms)= 1000.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 1.000 ******* ******* 0.998
12Vsb 2.750 ******* ******* 2.750
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 12.810 11.590 12.259
12VSb 12.600 11.400 12.009
PWOK 3.460 2.500 3.248
Vin_Good 3.460 2.500 3.249
SMBAlert 3.460 2.500 3.212
IBUS ******* ******* 0.061
CR 0.400 ******* 0.001
Max Min Reading
------------- --------- --------- ---------
Pout (W) ******* ******* 45.255
STEP.344(UUT Test seq.344) : Input Output Eff Noise Multi or Single(264V_63 PASS
ElapsedTime (S)= 1'903
Vin (V)= 264.00
Fin (Hz)= 63.00
Delay Time (ms)= 500.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 1.000 ******* ******* 0.998
12Vsb 0.100 ******* ******* 0.100
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
-------Load---------------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V ???.??? ???.??? ???.???
12Vsb ???.??? ???.??? ???.???
PWOK ???.??? ???.??? ???.???
Vin_Good ???.??? ???.??? ???.???
SMBAlert ???.??? ???.??? ???.???
--------34970----------------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 12.810 11.590 12.260
12VSb 12.600 11.400 12.145
PWOK 3.460 2.500 3.245
Vin_Good 3.460 2.500 3.248
SMBAlert 3.460 2.500 3.217
IBUS ******* ******* 0.059
CR 0.400 ******* 0.003
Max Min Reading
------------- ---------- ---------- ----------
Vrms (V) ******** ******** 264.2755
PF 1.0000 ******** 0.4030
THDi (%) ******** * 28.5149
Irms (A) ******** ******** 0.1643
Pin (W) ******** ******** 17.4938
Pout (W) ******** ******** 13.4495
Eff (%) ******** ******** 76.8814
Load Noise Range Noise B.W
Name (V) (MHz)
------------- ----------- ---------
12V 2 20.000
12Vsb 2 20.000
PWOK 2 20.000
Vin_Good 2 20.000
SMBAlert 2 20.000
Load Vpp Noise Vpp Noise Vpp Noise
Name Max(mV) Min(mV) (mV)
------------- ------------ ------------ ------------
12V 120.000 0.000 9.860
12Vsb 120.000 0.000 7.990
PWOK ********* ********* 20.210
Vin_Good ********* ********* 19.540
SMBAlert ********* ********* 22.250
STEP.345(UUT Test seq.345) : Input Output Eff Noise Multi or Single(264V_63 PASS
ElapsedTime (S)= 1'887
Vin (V)= 264.00
Fin (Hz)= 63.00
Delay Time (ms)= 500.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 1.000 ******* ******* 0.998
12Vsb 2.500 ******* ******* 2.500
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
-------Load---------------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V ???.??? ???.??? ???.???
12Vsb ???.??? ???.??? ???.???
PWOK ???.??? ???.??? ???.???
Vin_Good ???.??? ???.??? ???.???
SMBAlert ???.??? ???.??? ???.???
--------34970----------------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 12.810 11.590 12.260
12VSb 12.600 11.400 12.013
PWOK 3.460 2.500 3.243
Vin_Good 3.460 2.500 3.250
SMBAlert 3.460 2.500 3.213
IBUS ******* ******* 0.058
CR 0.400 ******* 0.001
Max Min Reading
------------- ---------- ---------- ----------
Vrms (V) ******** ******** 264.2615
PF 1.0000 ******** 0.7261
THDi (%) ******** * 21.0093
Irms (A) ******** ******** 0.2980
Pin (W) ******** ******** 57.1817
Pout (W) ******** ******** 42.2608
Eff (%) ******** ******** 73.9062
Load Noise Range Noise B.W
Name (V) (MHz)
------------- ----------- ---------
12V 2 20.000
12Vsb 2 20.000
PWOK 2 20.000
Vin_Good 2 20.000
SMBAlert 2 20.000
Load Vpp Noise Vpp Noise Vpp Noise
Name Max(mV) Min(mV) (mV)
------------- ------------ ------------ ------------
12V 120.000 0.000 7.870
12Vsb 120.000 0.000 3.190
PWOK ********* ********* 20.560
Vin_Good ********* ********* 20.310
SMBAlert ********* ********* 22.670
STEP.346(UUT Test seq.346) : Cold Redundant Master Multi _S2 ---- (0'094) - PASS
(The Report Format of this Sequence was not found)
STEP.347(UUT Test seq.347) : Static ACDC 34970_or_Load_Multi or Single(264V PASS
ElapsedTime (S)= 1'264
Vin (V)= 264.00
Fin (Hz)= 63.00
Delay Time (ms)= 500.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 1.000 ******* ******* 0.998
12Vsb 0.100 ******* ******* 0.100
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 12.810 11.590 12.261
12VSb 12.600 11.400 12.145
PWOK 3.460 2.500 3.241
Vin_Good 3.460 2.500 3.245
SMBAlert 3.460 2.500 3.216
IBUS ******* ******* 0.061
CR 3.460 2.500 3.190
Max Min Reading
------------- --------- --------- ---------
Pout (W) ******* ******* 13.449
STEP.348(UUT Test seq.348) : Disable Cold Redundant Master Multi_S2 ---- (0 PASS
(The Report Format of this Sequence was not found)
STEP.349(UUT Test seq.349) : Static ACDC 34970_or_Load_Multi or Single(264V PASS
ElapsedTime (S)= 1'248
Vin (V)= 264.00
Fin (Hz)= 63.00
Delay Time (ms)= 500.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 1.000 ******* ******* 0.998
12Vsb 0.100 ******* ******* 0.100
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 12.810 11.590 12.261
12VSb 12.600 11.400 12.140
PWOK 3.460 2.500 3.246
Vin_Good 3.460 2.500 3.247
SMBAlert 3.460 2.500 3.217
IBUS ******* ******* 0.060
CR 0.400 ******* 0.003
Max Min Reading
------------- --------- --------- ---------
Pout (W) ******* ******* 13.450
STEP.350(UUT Test seq.350) : 12V OVP I2C Multi(12V_OVP_I2C) ---- (0'046) -- PASS
STEP.351(UUT Test seq.351) : Static ACDC 34970_or_Load_Multi or Single(264V PASS
ElapsedTime (S)= 1'373
Vin (V)= 264.00
Fin (Hz)= 63.00
Delay Time (ms)= 500.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 1.000 ******* ******* 0.000
12Vsb 0.100 ******* ******* 0.100
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 0.400 ******* 0.000
12VSb 12.600 11.400 12.139
PWOK 0.400 ******* 0.039
Vin_Good 3.460 2.500 3.242
SMBAlert 3.460 2.500 3.215
IBUS ******* ******* 0.131
CR 0.400 ******* 0.004
Max Min Reading
------------- --------- --------- ---------
Pout (W) ******* ******* 1.216
STEP.352(UUT Test seq.352) : I2C Read Status OR Multi_S6(12V_OV) ---- (0'10 PASS
Command Page00 :060200
Command Page01 :060201
Status Word :79
Status Byte :78
Status VOUT :7A
Status IOUT :7B
Status INPUT :7C
Status TEMPERATURE :7D
Status CML :7E
Status FANS :81
---------------------------------
Word SPEC: 25224
Word SPEC: 25224
Word SPEC: 25224
Word SPEC: 25224
Word SPEC: 25224
Word SPEC: 25224
Word SPEC: 25224
Word SPEC: 25224
Word SPEC_Page1: 25224
Word SPEC_Page1: 25224
Word SPEC_Page1: 25224
Word SPEC_Page1: 25224
Word SPEC_Page1: 25224
Word SPEC_Page1: 25224
Word SPEC_Page1: 25224
Word SPEC_Page1: 25224
Byte SPEC : 98
Byte SPEC : 98
Byte SPEC : 98
Byte SPEC : 98
Byte SPEC : 98
Byte SPEC : 98
Byte SPEC : 98
Byte SPEC : 98
VOUT SPEC : 192
VOUT SPEC : 192
VOUT SPEC : 192
VOUT SPEC : 192
VOUT SPEC : 192
VOUT SPEC : 192
VOUT SPEC : 192
VOUT SPEC : 192
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
CML SPEC : 128
CML SPEC : 128
CML SPEC : 128
CML SPEC : 128
CML SPEC : 128
CML SPEC : 128
CML SPEC : 128
CML SPEC : 128
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
Word Page0 OR : 0200
Word Page1 OR : 0200
Byte OR : 02
Input OR : 00
IOUT OR : 00
TEMP OR : 00
CML OR : 80
----------------------------------
Word_Page_00 : 25224
Word_Page_01 : 25224
Status_Byte_P00 : 98
Status_Byte_P01 : 98
Status_VOUT_P00 : 192
Status_VOUT_P01 : 192
Status_IOUT_P00 : 0
Status_IOUT_P01 : 0
Status_INPUT_P00 : 0
Status_INPUT_P01 : 0
Status_TEM_P00 : 0
Status_TEM_P01 : 0
Status_CML_P00 : 128
Status_CML_P01 : 128
Status_FANS_P00 : 0
Status_FANS_P01 : 0
STEP.353(UUT Test seq.353) : 12V OVP Disable I2C Multi ---- (0'062) ------- PASS
STEP.354(UUT Test seq.354) : TTL & Relay Setup ---- (0'624) --------------- PASS
(The Report Format of this Sequence was not found)
STEP.355(UUT Test seq.355) : Hold Up Timing Test_Multi or Single(264V_63Hz_ PASS
ElapsedTime (S)= 0'702
Vin (V)= 264.00
Fin (Hz)= 63.00
Delay Time (ms)= 0.00
On Phase Delay(ms)= 90.00
UUT Off Time (s)= 0.00
Trigger: 1:Trig1R(AC), 2:Trig2R(PS on), 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:Trig1F(AC), 9:Trig2F(PS on),10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1
2 1
3 1
4 1
Load Loading Start End VcmpA VcmpB
Name (A/Ohm/V) Trigger Trigger (V) (V)
------------- ---------- ------- ------- ------- -------
12V 1.000 8 12 11.590 12.810
12Vsb 0.100 8 12 11.400 12.600
PWOK 0.000 8 12 2.600 3.460
Vin_Good 0.000 8 12 2.600 3.460
SMBAlert 0.000 8 1 2.600 3.460
Load Tholdup Tholdup Tholdup
Name Max Min (ms)
------------- -------- -------- ---------
12V 1000.00 10.00 48.37
12Vsb 1000.00 70.00 92.45
PWOK 300.00 9.00 43.66
Vin_Good 4.00 0.01 2.77
SMBAlert ******** ******** 0.06
Load Ref Load Tholdup Tholdup Tholdup
Name No. Max Min (ms)
------------- ---------- -------- -------- ---------
12V 3 300.00 1.00 4.71
12Vsb 0 ******** ******** 92.45
PWOK 1 -300.00 -1.00 -4.71
Vin_Good 0 ******** ******** 2.77
SMBAlert 0 ******** ******** 0.06
STEP.356(UUT Test seq.356) : FAN Full Speed delay time Multi ---- (8'097) - PASS
STEP.357(UUT Test seq.357) : FAN Speed Normal_Multi ---- (0'110) ---------- PASS
(The Report Format of this Sequence was not found)
STEP.358(UUT Test seq.358) : Turn On Timing Test_Multi or Single(264V_63Hz_ PASS
ElaspedTime (S)= 1'747
Vin (V)= 264.00
Fin (Hz)= 63.00
On Phase Delay(ms)= 90.00
UUT Off Time (s)= 0.00
Trigger: 1:TTL1R, 2:TTL2R, 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:TTL1F, 9:TTL2F,10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1.00
2 1.00
3 1.00
4 1.00
Load Loading Start End VcmpA VcmpB
Name (A/Ohm/V) Trigger Trigger (V) (V)
------------- ---------- ------- ------- ------- -------
12V 161.500 8 5 11.590 12.810
12Vsb 2.500 8 5 11.400 12.600
PWOK 0.000 8 5 2.600 3.460
Vin_Good 0.000 8 1 2.600 3.460
SMBAlert 0.000 8 1 2.600 3.460
Load Ton Ton Ton
Name Max Min (ms)
------------- -------- -------- ---------
12V 3000.00 1.00 974.47
12Vsb 1500.00 1.00 728.82
PWOK ******** ******** 1179.98
Vin_Good ******** ******** 0.06
SMBAlert ******** ******** 0.06
Load Ref Load Td Td Td
Name No. Max Min (ms)
------------- ------------- -------- -------- ---------
12V 3 -500.00 -100.00 -205.51
12Vsb 1 -1500.00 -50.00 -245.65
PWOK 1 500.00 100.00 205.51
Vin_Good 0 ******** ******** 0.06
SMBAlert 0 ******** ******** 0.06
STEP.359(UUT Test seq.359) : I2C Read Status Multi_S6(264V_63Hz_HH) ---- (0 PASS
Adderss :B0
Command Page00 :060200
Command Page01 :060201
Status Word :79
Status Byte :78
Status VOUT :7A
Status IOUT :7B
Status INPUT :7C
Status TEMPERATURE :7D
Status CML :7E
Status FANS :81
---------------------------------
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
----------------------------------
Word_Page_00 : 0
Word_Page_01 : 0
Status_Byte_P00 : 0
Status_Byte_P01 : 0
Status_VOUT_P00 : 0
Status_VOUT_P01 : 0
Status_IOUT_P00 : 0
Status_IOUT_P01 : 0
Status_INPUT_P00 : 0
Status_INPUT_P01 : 0
Status_TEM_P00 : 0
Status_TEM_P01 : 0
Status_CML_P00 : 0
Status_CML_P01 : 0
Status_FANS_P00 : 0
Status_FANS_P01 : 0
STEP.360(UUT Test seq.360) : PS OFF Time 80611(264V_63Hz_HH) ---- (1'591) - PASS
Vin (V)= Refer to the previous item
Fin (Hz)= Refer to the previous item
On Phase Delay(ms)= Refer to the previous item
UUT Off Time (s)= Refer to the previous item
Loading (A/Ohm/V)= Refer to the previous item
Trigger: 1:Trig1R(AC), 2:Trig2R(PS on), 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:Trig1F(AC), 9:Trig2F(PS on),10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1
2 1
3 1
4 1
Load Start End VcmpA VcmpB
Name Trigger Trigger (V) (V)
------------- ------- ------- ------- -------
12V 2 12 11.590 12.810
12Vsb 2 2 11.400 12.600
PWOK 2 12 2.600 2.600
Vin_Good 2 2 2.600 2.600
SMBAlert 2 2 2.600 2.600
Load Ton Ton Ton
Name Max Min (ms)
------------- -------- -------- ---------
12V ******** ******** 2.38
12Vsb ******** ******** --------
PWOK 50.00 0.01 0.74
Vin_Good ******** ******** --------
SMBAlert ******** ******** --------
Load Ref Load Td Td Td
Name No. Max Min (ms)
------------- ---------- -------- -------- ---------
12V 3 100.00 1.00 1.65
12Vsb 0 ******** ******** --------
PWOK 1 -100.00 -1.00 -1.65
Vin_Good 0 ******** ******** --------
SMBAlert 0 ******** ******** --------
STEP.361(UUT Test seq.361) : I2C Read Status Multi_S6(StandBy) ---- (0'140) PASS
Adderss :B0
Command Page00 :060200
Command Page01 :060201
Status Word :79
Status Byte :78
Status VOUT :7A
Status IOUT :7B
Status INPUT :7C
Status TEMPERATURE :7D
Status CML :7E
Status FANS :81
---------------------------------
Word SPEC: 16392
Word SPEC: 16392
Word SPEC: 16392
Word SPEC: 16392
Word SPEC: 16392
Word SPEC: 16392
Word SPEC: 16392
Word SPEC: 16392
Word SPEC_Page1: 16392
Word SPEC_Page1: 16392
Word SPEC_Page1: 16392
Word SPEC_Page1: 16392
Word SPEC_Page1: 16392
Word SPEC_Page1: 16392
Word SPEC_Page1: 16392
Word SPEC_Page1: 16392
Byte SPEC : 64
Byte SPEC : 64
Byte SPEC : 64
Byte SPEC : 64
Byte SPEC : 64
Byte SPEC : 64
Byte SPEC : 64
Byte SPEC : 64
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
----------------------------------
Word_Page_00 : 16392
Word_Page_01 : 16392
Status_Byte_P00 : 64
Status_Byte_P01 : 64
Status_VOUT_P00 : 0
Status_VOUT_P01 : 0
Status_IOUT_P00 : 0
Status_IOUT_P01 : 0
Status_INPUT_P00 : 0
Status_INPUT_P01 : 0
Status_TEM_P00 : 0
Status_TEM_P01 : 0
Status_CML_P00 : 0
Status_CML_P01 : 0
Status_FANS_P00 : 0
Status_FANS_P01 : 0
STEP.362(UUT Test seq.362) : PS ON Delay time 80611(264V_63Hz_HH) ---- (0'8 PASS
Vin (V)= Refer to the previous item
Fin (Hz)= Refer to the previous item
On Phase Delay(ms)= Refer to the previous item
UUT Off Time (s)= Refer to the previous item
Loading (A/Ohm/V)= Refer to the previous item
Trigger: 1:Trig1R(AC), 2:Trig2R(PS on), 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:Trig1F(AC), 9:Trig2F(PS on),10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1
2 1
3 1
4 1
Load Start End VcmpA VcmpB
Name Trigger Trigger (V) (V)
------------- ------- ------- ------- -------
12V 9 5 11.590 12.810
12Vsb 9 9 11.400 12.600
PWOK 9 5 2.600 2.600
Vin_Good 9 9 2.600 2.600
SMBAlert 9 9 2.600 2.600
Load Ton Ton Ton
Name Max Min (ms)
------------- -------- -------- ---------
12V 400.00 5.00 62.58
12Vsb ******** ******** 0.17
PWOK ******** ******** 268.05
Vin_Good ******** ******** 0.17
SMBAlert ******** ******** 0.17
Load Ref Load Td Td Td
Name No. Max Min (ms)
------------- ---------- -------- -------- ---------
12V 3 -500.000 -100.000 -205.462
12Vsb 0 ********* ********* 0.168
PWOK 1 500.000 100.000 205.462
Vin_Good 0 ********* ********* 0.168
SMBAlert 0 ********* ********* 0.168
STEP.363(UUT Test seq.363) : Turn On Timing Test_Multi or Single(264V_63Hz_ PASS
ElaspedTime (S)= 2'106
Vin (V)= 264.00
Fin (Hz)= 63.00
On Phase Delay(ms)= 90.00
UUT Off Time (s)= 0.50
Trigger: 1:TTL1R, 2:TTL2R, 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:TTL1F, 9:TTL2F,10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1.00
2 1.00
3 1.00
4 1.00
Load Loading Start End VcmpA VcmpB
Name (A/Ohm/V) Trigger Trigger (V) (V)
------------- ---------- ------- ------- ------- -------
12V 161.500 5 6 1.220 11.590
12Vsb 2.500 5 6 1.200 10.800
PWOK 0.000 8 1 2.600 3.460
Vin_Good 0.000 8 1 2.600 3.460
SMBAlert 0.000 8 1 2.600 3.460
Load Ton Ton Ton
Name Max Min (ms)
------------- -------- -------- ---------
12V 70.00 5.00 51.26
12Vsb 70.00 1.00 11.71
PWOK ******** ******** 0.06
Vin_Good ******** ******** 0.06
SMBAlert ******** ******** 0.06
Load Ref Load Td Td Td
Name No. Max Min (ms)
------------- ------------- -------- -------- ---------
12V 0 ******** ******** 51.26
12Vsb 0 ******** ******** 11.71
PWOK 0 ******** ******** 0.06
Vin_Good 0 ******** ******** 0.06
SMBAlert 0 ******** ******** 0.06
STEP.364(UUT Test seq.364) : TTL & Relay Setup ---- (0'000) --------------- PASS
(The Report Format of this Sequence was not found)
STEP.365(UUT Test seq.365) : PS ON Delay time 80611(264V_63Hz_HH_Tpson_12V_ PASS
Vin (V)= Refer to the previous item
Fin (Hz)= Refer to the previous item
On Phase Delay(ms)= Refer to the previous item
UUT Off Time (s)= Refer to the previous item
Loading (A/Ohm/V)= Refer to the previous item
Trigger: 1:Trig1R(AC), 2:Trig2R(PS on), 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:Trig1F(AC), 9:Trig2F(PS on),10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1
2 1
3 1
4 1
Load Start End VcmpA VcmpB
Name Trigger Trigger (V) (V)
------------- ------- ------- ------- -------
12V 5 6 1.220 11.590
12Vsb 9 9 1.200 10.800
PWOK 9 9 2.600 2.600
Vin_Good 9 9 2.600 2.600
SMBAlert 9 9 2.600 2.600
Load Ton Ton Ton
Name Max Min (ms)
------------- -------- -------- ---------
12V 70.00 5.00 51.26
12Vsb ******** ******** 0.05
PWOK ******** ******** 0.05
Vin_Good ******** ******** 0.05
SMBAlert ******** ******** 0.05
Load Ref Load Td Td Td
Name No. Max Min (ms)
------------- ---------- -------- -------- ---------
12V 0 ********* ********* 51.257
12Vsb 0 ********* ********* 0.047
PWOK 0 ********* ********* 0.047
Vin_Good 0 ********* ********* 0.047
SMBAlert 0 ********* ********* 0.047
STEP.366(UUT Test seq.366) : Input Output Eff Noise Multi or Single(264V_63 PASS
ElapsedTime (S)= 2'387
Vin (V)= 264.00
Fin (Hz)= 63.00
Delay Time (ms)= 1000.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 161.500 ******* ******* 161.497
12Vsb 0.100 ******* ******* 0.100
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
-------Load---------------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V ???.??? ???.??? ???.???
12Vsb ???.??? ???.??? ???.???
PWOK ???.??? ???.??? ???.???
Vin_Good ???.??? ???.??? ???.???
SMBAlert ???.??? ???.??? ???.???
--------34970----------------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 12.810 11.590 12.165
12VSb 12.600 11.400 12.121
PWOK 3.460 2.500 3.226
Vin_Good 3.460 2.500 3.228
SMBAlert 3.460 2.500 3.220
IBUS ******* ******* 7.999
CR 0.400 ******* -0.020
Max Min Reading
------------- ---------- ---------- ----------
Vrms (V) ******** ******** 263.5244
PF 1.0000 ******** 0.9975
THDi (%) ******** * 2.2938
Irms (A) ******** ******** 8.2034
Pin (W) ******** ******** XXXXXXXX
Pout (W) ******** ******** XXXXXXXX
Eff (%) ******** ******** 91.1625
Load Noise Range Noise B.W
Name (V) (MHz)
------------- ----------- ---------
12V 2 20.000
12Vsb 2 20.000
PWOK 2 20.000
Vin_Good 2 20.000
SMBAlert 2 20.000
Load Vpp Noise Vpp Noise Vpp Noise
Name Max(mV) Min(mV) (mV)
------------- ------------ ------------ ------------
12V 120.000 0.000 16.050
12Vsb 120.000 0.000 7.280
PWOK ********* ********* 23.800
Vin_Good ********* ********* 22.020
SMBAlert ********* ********* 25.980
STEP.367(UUT Test seq.367) : Static ACDC 34970_or_Load_Multi or Single(264V PASS
ElapsedTime (S)= 1'216
Vin (V)= 264.00
Fin (Hz)= 63.00
Delay Time (ms)= 500.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 161.500 ******* ******* 161.497
12Vsb 2.750 ******* ******* 2.750
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 12.810 11.590 12.166
12VSb 12.600 11.400 11.983
PWOK 3.460 2.500 3.226
Vin_Good 3.460 2.500 3.220
SMBAlert 3.460 2.500 3.226
IBUS ******* ******* 7.998
CR 0.400 ******* -0.022
Max Min Reading
------------- --------- --------- ---------
Pout (W) ******* ******* XXXXXXX
STEP.368(UUT Test seq.368) : Static ACDC 34970_or_Load_Multi or Single(264V PASS
ElapsedTime (S)= 1'436
Vin (V)= 264.00
Fin (Hz)= 63.00
Delay Time (ms)= 500.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 161.500 ******* ******* 0.000
12Vsb 3.650 ******* ******* 0.011
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 0.400 ******* 0.001
12VSb 12.600 ******* 11.976
PWOK 0.400 ******* 0.039
Vin_Good 3.460 2.400 3.240
SMBAlert 3.460 ******* 3.218
IBUS ******* ******* 0.154
CR 0.400 ******* 0.005
Max Min Reading
------------- --------- --------- ---------
Pout (W) ******* ******* 0.134
STEP.369(UUT Test seq.369) : Static ACDC 34970_or_Load_Multi or Single(264V PASS
ElapsedTime (S)= 1'872
Vin (V)= 264.00
Fin (Hz)= 63.00
Delay Time (ms)= 1000.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 161.500 ******* ******* 161.497
12Vsb 2.750 ******* ******* 2.750
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 12.810 11.590 12.161
12VSb 12.600 11.400 11.988
PWOK 3.460 2.500 3.222
Vin_Good 3.460 2.500 3.220
SMBAlert 3.460 2.500 3.228
IBUS ******* ******* 7.999
CR 0.400 ******* -0.022
Max Min Reading
------------- --------- --------- ---------
Pout (W) ******* ******* XXXXXXX
STEP.370(UUT Test seq.370) : Cold Redundant Master Multi _S2 ---- (0'093) - PASS
(The Report Format of this Sequence was not found)
STEP.371(UUT Test seq.371) : Static ACDC 34970_or_Load_Multi or Single(264V PASS
ElapsedTime (S)= 1'232
Vin (V)= 264.00
Fin (Hz)= 63.00
Delay Time (ms)= 500.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 161.500 ******* ******* 161.497
12Vsb 2.500 ******* ******* 2.500
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 12.810 11.590 12.168
12VSb 12.600 11.400 11.996
PWOK 3.460 2.500 3.216
Vin_Good 3.460 2.500 3.223
SMBAlert 3.460 2.500 3.223
IBUS ******* ******* 8.002
CR 3.460 2.500 3.166
Max Min Reading
------------- --------- --------- ---------
Pout (W) ******* ******* XXXXXXX
STEP.372(UUT Test seq.372) : Disable Cold Redundant Master Multi_S2 ---- (0 PASS
(The Report Format of this Sequence was not found)
STEP.373(UUT Test seq.373) : Static ACDC 34970_or_Load_Multi or Single(264V PASS
ElapsedTime (S)= 1'264
Vin (V)= 264.00
Fin (Hz)= 63.00
Delay Time (ms)= 500.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 161.500 ******* ******* 161.497
12Vsb 2.500 ******* ******* 2.500
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 12.810 11.590 12.165
12VSb 12.600 11.400 11.995
PWOK 3.460 2.500 3.220
Vin_Good 3.460 2.500 3.226
SMBAlert 3.460 2.500 3.225
IBUS ******* ******* 8.002
CR 0.400 ******* -0.022
Max Min Reading
------------- --------- --------- ---------
Pout (W) ******* ******* XXXXXXX
STEP.374(UUT Test seq.374) : Input Output Eff Noise Multi or Single(HH) --- PASS
ElapsedTime (S)= 2'231
Vin (V)= 264.00
Fin (Hz)= 63.00
Delay Time (ms)= 1000.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 161.500 ******* ******* 161.497
12Vsb 2.500 ******* ******* 2.500
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
-------Load---------------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V ???.??? ???.??? ???.???
12Vsb ???.??? ???.??? ???.???
PWOK ???.??? ???.??? ???.???
Vin_Good ???.??? ???.??? ???.???
SMBAlert ???.??? ???.??? ???.???
--------34970----------------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 12.810 11.590 12.166
12VSb 12.600 11.400 11.994
PWOK 3.460 2.500 3.227
Vin_Good 3.460 2.500 3.221
SMBAlert 3.460 2.500 3.226
IBUS ******* ******* 8.004
CR 0.400 ******* -0.022
Max Min Reading
------------- ---------- ---------- ----------
Vrms (V) ******** ******** 263.5154
PF 1.0000 ******** 0.9974
THDi (%) ******** * 2.2770
Irms (A) ******** ******** 8.3503
Pin (W) ******** ******** XXXXXXXX
Pout (W) ******** ******** XXXXXXXX
Eff (%) ******** ******** 90.8856
Load Noise Range Noise B.W
Name (V) (MHz)
------------- ----------- ---------
12V 2 20.000
12Vsb 2 20.000
PWOK 2 20.000
Vin_Good 2 20.000
SMBAlert 2 20.000
Load Vpp Noise Vpp Noise Vpp Noise
Name Max(mV) Min(mV) (mV)
------------- ------------ ------------ ------------
12V 120.000 0.000 15.350
12Vsb 120.000 0.000 15.030
PWOK ********* ********* 24.650
Vin_Good ********* ********* 22.890
SMBAlert ********* ********* 27.060
STEP.375(UUT Test seq.375) : Static ACDC 34970_or_Load_Multi or Single(264V PASS
ElapsedTime (S)= 3'682
Vin (V)= 264.00
Fin (Hz)= 63.00
Delay Time (ms)= 3000.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 185.380 ******* ******* 185.382
12Vsb 2.500 ******* ******* 2.500
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 12.810 11.590 12.154
12VSb 12.600 11.400 11.992
PWOK 3.460 2.500 3.217
Vin_Good 3.460 2.500 3.220
SMBAlert 3.460 ******* 3.227
IBUS ******* ******* 9.017
CR 0.400 ******* -0.026
Max Min Reading
------------- --------- --------- ---------
Pout (W) ******* ******* XXXXXXX
STEP.376(UUT Test seq.376) : TTL & Relay Setup(PS OnOff) ---- (1'014) ----- PASS
(The Report Format of this Sequence was not found)
STEP.377(UUT Test seq.377) : Peak_Load_S3_Multi_S(264V-OCP1_HL_Delay time 5 PASS
ElapsedTime (S)= 8'502
Vin (V)= Refer to the previous item
Fin (Hz)= Refer to the previous item
Delay Time (ms)= 2000.00
Load Setting Time (ms)= 2000.00
Measurement Delay Time (ms)= 3000.00
Turn On Delay Time (ms)= 3000.00
Loading Loading
Name (A/Ohm/V)
------------- ----------
12V 161.500
12Vsb 0.100
PWOK 0.000
Vin_Good 0.000
SMBAlert 0.000
12V_Loading_level Dell_Time Rise Rate Fall Rate
(A) (ms) (A/us) (A/us)
------------------ --------- --------- ---------
120.000 500.000 2.5000 2.5000
161.500 500.000 2.5000 2.5000
209.950 50.200 2.5000 2.5000
161.500 500.000 2.5000 2.5000
Load Vpk Max Vpk Min Vpk High Vpk Low
Name (V) (V) (V) (V)
------------- --------- --------- --------- ---------
12V 12.810 11.590 12.238 12.088
12Vsb 12.600 11.400 12.147 12.134
PWOK 3.460 2.500 3.260 3.257
Vin_Good 3.460 2.500 3.254 3.246
SMBAlert 3.460 ********* 3.264 0.080
STEP.378(UUT Test seq.378) : Peak_Load_S3_Multi_S(264V-OCP1_HH_Delay time 5 PASS
ElapsedTime (S)= 8'471
Vin (V)= Refer to the previous item
Fin (Hz)= Refer to the previous item
Delay Time (ms)= 2000.00
Load Setting Time (ms)= 2000.00
Measurement Delay Time (ms)= 3000.00
Turn On Delay Time (ms)= 3000.00
Loading Loading
Name (A/Ohm/V)
------------- ----------
12V 161.500
12Vsb 2.500
PWOK 0.000
Vin_Good 0.000
SMBAlert 0.000
12V_Loading_level Dell_Time Rise Rate Fall Rate
(A) (ms) (A/us) (A/us)
------------------ --------- --------- ---------
120.000 500.000 2.5000 2.5000
161.500 500.000 2.5000 2.5000
209.950 50.200 2.5000 2.5000
161.500 500.000 2.5000 2.5000
Load Vpk Max Vpk Min Vpk High Vpk Low
Name (V) (V) (V) (V)
------------- --------- --------- --------- ---------
12V 12.810 11.590 12.230 12.080
12Vsb 12.600 11.400 12.025 12.007
PWOK 3.460 2.500 3.259 3.257
Vin_Good 3.460 2.500 3.251 3.243
SMBAlert 3.460 ********* 0.097 0.070
STEP.379(UUT Test seq.379) : Peak_Load_S3_Multi_S(264V-OCP2_HL_Delay time 0 PASS
ElapsedTime (S)= 8'502
Vin (V)= Refer to the previous item
Fin (Hz)= Refer to the previous item
Delay Time (ms)= 2000.00
Load Setting Time (ms)= 2000.00
Measurement Delay Time (ms)= 3000.00
Turn On Delay Time (ms)= 3000.00
Loading Loading
Name (A/Ohm/V)
------------- ----------
12V 161.500
12Vsb 0.100
PWOK 0.000
Vin_Good 0.000
SMBAlert 0.000
12V_Loading_level Dell_Time Rise Rate Fall Rate
(A) (ms) (A/us) (A/us)
------------------ --------- --------- ---------
120.000 500.000 2.5000 2.5000
161.500 500.000 2.5000 2.5000
324.615 0.120 2.5000 2.5000
161.500 500.000 2.5000 2.5000
Load Vpk Max Vpk Min Vpk High Vpk Low
Name (V) (V) (V) (V)
------------- --------- --------- --------- ---------
12V 12.960 11.000 12.286 11.895
12Vsb 12.600 11.400 12.151 12.137
PWOK 3.460 2.500 3.260 3.263
Vin_Good 3.460 2.500 3.254 3.252
SMBAlert 3.460 ********* 0.115 0.029
STEP.380(UUT Test seq.380) : Peak_Load_S3_Multi_S(264V-OCP2_HH_Delay time 0 PASS
ElapsedTime (S)= 8'502
Vin (V)= Refer to the previous item
Fin (Hz)= Refer to the previous item
Delay Time (ms)= 2000.00
Load Setting Time (ms)= 2000.00
Measurement Delay Time (ms)= 3000.00
Turn On Delay Time (ms)= 3000.00
Loading Loading
Name (A/Ohm/V)
------------- ----------
12V 161.500
12Vsb 2.500
PWOK 0.000
Vin_Good 0.000
SMBAlert 0.000
12V_Loading_level Dell_Time Rise Rate Fall Rate
(A) (ms) (A/us) (A/us)
------------------ --------- --------- ---------
120.000 500.000 2.5000 2.5000
161.500 500.000 2.5000 2.5000
324.615 0.120 2.5000 2.5000
161.500 500.000 2.5000 2.5000
Load Vpk Max Vpk Min Vpk High Vpk Low
Name (V) (V) (V) (V)
------------- --------- --------- --------- ---------
12V 12.960 11.000 12.250 11.926
12Vsb 12.600 11.400 12.023 12.004
PWOK 3.460 2.500 3.259 3.260
Vin_Good 3.460 2.500 3.253 3.248
SMBAlert 3.460 ********* 0.118 0.030
STEP.381(UUT Test seq.381) : Set Input Condition Multi_S4_4(264V_63Hz) ---- PASS
Input Voltage Type (Vac=0 ; Vdc=1) = 0
Vin = 264.000
Fin = 63.000
Vin_DC_Positive_Negative(Positive=0 ; Negative=1) = 0
STEP.382(UUT Test seq.382) : Set Dynamic_Time ---- (0'016) ---------------- PASS
ElapsedTime (S)= 0'016
Delay Time (ms)= 3000.00
Measurement Time (ms) = 1000.00
UUT Off Time (s)= 3.00
STEP.383(UUT Test seq.383) : SetAllLoad_SlewRate_S ---- (0'109) ----------- PASS
STEP.384(UUT Test seq.384) : Sync_Dynamic_80611_20200716_Multi_S(264V-OCP_1 PASS
ElapsedTime (S)= 4'836
Vin (V)= Refer to previous item
Fin (Hz)= Refer to previous item
Duration-1 (ms)= 100.0000
Duration-2 (ms) = 50.2000
Load Loading-1 Loading-2 Vstable+ Vstable-
Name (A) (A) (V) (V)
------------- --------- --------- --------- ---------
12V 1.000 1.000 -------- --------
12Vsb 2.750 3.650 -------- --------
PWOK 0.000 0.000 -------- --------
Vin_Good 0.000 0.000 -------- --------
SMBAlert 0.000 0.000 -------- --------
Load Vpk+ Max Vpk+ Min Vpk High Vpk- Max Vpk- Min Vpk Low
Name (V) (V) (V) (V) (V) (V)
------------- --------- --------- --------- --------- --------- ---------
12V 12.810 11.590 12.274 12.810 11.590 12.260
12Vsb 12.600 11.400 12.027 12.600 11.400 12.011
PWOK 3.460 2.500 3.270 3.460 2.500 3.287
Vin_Good 3.460 2.500 3.266 3.460 2.500 3.275
SMBAlert 3.460 2.500 3.251 3.460 2.500 3.253
Load Vspk+ Max Vspk+ Min Vspk High Vspk- Max Vspk- Min Vspk Low
Name (V) (V) (mV) (V) (V) (mV)
------------- ---------- ---------- ---------- ---------- ---------- ----------
12V ******** ******** -------- ******** ******** --------
12Vsb ******** ******** -------- ******** ******** --------
PWOK ******** ******** -------- ******** ******** --------
Vin_Good ******** ******** -------- ******** ******** --------
SMBAlert ******** ******** -------- ******** ******** --------
STEP.385(UUT Test seq.385) : Sync_Dynamic_80611_20200716_Multi_S(264V-OCP_1 PASS
ElapsedTime (S)= 4'711
Vin (V)= Refer to previous item
Fin (Hz)= Refer to previous item
Duration-1 (ms)= 100.0000
Duration-2 (ms) = 50.2000
Load Loading-1 Loading-2 Vstable+ Vstable-
Name (A) (A) (V) (V)
------------- --------- --------- --------- ---------
12V 161.500 161.500 -------- --------
12Vsb 2.750 3.650 -------- --------
PWOK 0.000 0.000 -------- --------
Vin_Good 0.000 0.000 -------- --------
SMBAlert 0.000 0.000 -------- --------
Load Vpk+ Max Vpk+ Min Vpk High Vpk- Max Vpk- Min Vpk Low
Name (V) (V) (V) (V) (V) (V)
------------- --------- --------- --------- --------- --------- ---------
12V 12.810 11.590 12.178 12.810 11.590 12.169
12Vsb 12.600 11.400 12.010 12.600 11.400 11.985
PWOK 3.460 2.500 3.250 3.460 2.500 3.263
Vin_Good 3.460 2.500 3.242 3.460 2.500 3.254
SMBAlert 3.460 2.500 3.262 3.460 2.500 3.266
Load Vspk+ Max Vspk+ Min Vspk High Vspk- Max Vspk- Min Vspk Low
Name (V) (V) (mV) (V) (V) (mV)
------------- ---------- ---------- ---------- ---------- ---------- ----------
12V ******** ******** -------- ******** ******** --------
12Vsb ******** ******** -------- ******** ******** --------
PWOK ******** ******** -------- ******** ******** --------
Vin_Good ******** ******** -------- ******** ******** --------
SMBAlert ******** ******** -------- ******** ******** --------
STEP.386(UUT Test seq.386) : Sync_Dynamic_80611_20200716_Multi_S(264V-Fast PASS
ElapsedTime (S)= 4'805
Vin (V)= Refer to previous item
Fin (Hz)= Refer to previous item
Duration-1 (ms)= 500.0000
Duration-2 (ms) = 5.0000
Load Loading-1 Loading-2 Vstable+ Vstable-
Name (A) (A) (V) (V)
------------- --------- --------- --------- ---------
12V 161.500 209.950 -------- --------
12Vsb 2.500 2.500 -------- --------
PWOK 0.000 0.000 -------- --------
Vin_Good 0.000 0.000 -------- --------
SMBAlert 0.000 0.000 -------- --------
Load Vpk+ Max Vpk+ Min Vpk High Vpk- Max Vpk- Min Vpk Low
Name (V) (V) (V) (V) (V) (V)
------------- --------- --------- --------- --------- --------- ---------
12V ******** ******** -------- ******** ******** ---------
12Vsb ******** ******** -------- ******** ******** ---------
PWOK ******** ******** -------- ******** ******** ---------
Vin_Good ******** ******** -------- ******** ******** ---------
SMBAlert ******** ******** -------- ******** ******** ---------
Load Vspk+ Max Vspk+ Min Vspk High Vspk- Max Vspk- Min Vspk Low
Name (V) (V) (mV) (V) (V) (mV)
------------- ---------- ---------- ---------- ---------- ---------- ----------
12V ******** ******** -------- ******** ******** --------
12Vsb ******** ******** -------- ******** ******** --------
PWOK ******** ******** -------- ******** ******** --------
Vin_Good ******** ******** -------- ******** ******** --------
SMBAlert ******** ******** -------- ******** ******** --------
STEP.387(UUT Test seq.387) : PS ON Delay time 80611(264V-Fast OCW_SMBAlert) PASS
Vin (V)= Refer to the previous item
Fin (Hz)= Refer to the previous item
On Phase Delay(ms)= Refer to the previous item
UUT Off Time (s)= Refer to the previous item
Loading (A/Ohm/V)= Refer to the previous item
Trigger: 1:Trig1R(AC), 2:Trig2R(PS on), 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:Trig1F(AC), 9:Trig2F(PS on),10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1
2 1
3 1
4 1
Load Start End VcmpA VcmpB
Name Trigger Trigger (V) (V)
------------- ------- ------- ------- -------
12V 1 1 11.590 12.810
12Vsb 1 1 11.400 12.600
PWOK 1 1 2.600 2.600
Vin_Good 1 1 2.600 2.600
SMBAlert 12 5 2.600 2.600
Load Ton Ton Ton
Name Max Min (ms)
------------- -------- -------- ---------
12V ******** ******** --------
12Vsb ******** ******** --------
PWOK ******** ******** --------
Vin_Good ******** ******** --------
SMBAlert 150.00 50.00 107.81
Load Ref Load Td Td Td
Name No. Max Min (ms)
------------- ---------- -------- -------- ---------
12V 0 ********* ********* ---------
12Vsb 0 ********* ********* ---------
PWOK 0 ********* ********* ---------
Vin_Good 0 ********* ********* ---------
SMBAlert 0 ********* ********* 107.812
STEP.388(UUT Test seq.388) : Sync_Dynamic_80611_20200716_Multi_S(264V-Fast PASS
ElapsedTime (S)= 4'945
Vin (V)= Refer to previous item
Fin (Hz)= Refer to previous item
Duration-1 (ms)= 200.0000
Duration-2 (ms) = 30.0000
Load Loading-1 Loading-2 Vstable+ Vstable-
Name (A) (A) (V) (V)
------------- --------- --------- --------- ---------
12V 161.500 209.950 -------- --------
12Vsb 2.500 2.500 -------- --------
PWOK 0.000 0.000 -------- --------
Vin_Good 0.000 0.000 -------- --------
SMBAlert 0.000 0.000 -------- --------
Load Vpk+ Max Vpk+ Min Vpk High Vpk- Max Vpk- Min Vpk Low
Name (V) (V) (V) (V) (V) (V)
------------- --------- --------- --------- --------- --------- ---------
12V 12.810 11.590 12.221 12.810 11.590 12.091
12Vsb 12.600 11.400 12.014 12.600 11.400 12.011
PWOK 3.460 2.500 3.247 3.460 2.500 3.258
Vin_Good 3.460 2.500 3.242 3.460 2.500 3.247
SMBAlert 3.460 ******** 3.249 3.460 ******** 0.085
Load Vspk+ Max Vspk+ Min Vspk High Vspk- Max Vspk- Min Vspk Low
Name (V) (V) (mV) (V) (V) (mV)
------------- ---------- ---------- ---------- ---------- ---------- ----------
12V ******** ******** -------- ******** ******** --------
12Vsb ******** ******** -------- ******** ******** --------
PWOK ******** ******** -------- ******** ******** --------
Vin_Good ******** ******** -------- ******** ******** --------
SMBAlert ******** ******** -------- ******** ******** --------
STEP.389(UUT Test seq.389) : Hold Up Timing Test_Multi or Single(264V_63Hz_ PASS
ElapsedTime (S)= 3'697
Vin (V)= 264.00
Fin (Hz)= 63.00
Delay Time (ms)= 3000.00
On Phase Delay(ms)= 90.00
UUT Off Time (s)= 0.00
Trigger: 1:Trig1R(AC), 2:Trig2R(PS on), 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:Trig1F(AC), 9:Trig2F(PS on),10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1
2 1
3 1
4 1
Load Loading Start End VcmpA VcmpB
Name (A/Ohm/V) Trigger Trigger (V) (V)
------------- ---------- ------- ------- ------- -------
12V 113.050 8 12 11.590 12.810
12Vsb 1.750 8 12 11.400 12.600
PWOK 0.000 8 12 2.600 3.460
Vin_Good 0.000 8 12 2.600 3.460
SMBAlert 0.000 8 1 2.600 3.460
Load Tholdup Tholdup Tholdup
Name Max Min (ms)
------------- -------- -------- ---------
12V 1000.00 10.00 21.80
12Vsb 1000.00 70.00 79.01
PWOK 300.00 9.00 20.22
Vin_Good 4.00 0.01 2.87
SMBAlert ******** ******** 0.06
Load Ref Load Tholdup Tholdup Tholdup
Name No. Max Min (ms)
------------- ---------- -------- -------- ---------
12V 3 100.00 1.00 1.58
12Vsb 0 ******** ******** 79.01
PWOK 1 -100.00 -1.00 -1.58
Vin_Good 0 ******** ******** 2.87
SMBAlert 0 ******** ******** 0.06
STEP.390(UUT Test seq.390) : FAN Full Speed delay time Multi ---- (8'096) - PASS
STEP.391(UUT Test seq.391) : FAN Speed Normal_Multi ---- (0'078) ---------- PASS
(The Report Format of this Sequence was not found)
STEP.392(UUT Test seq.392) : 61512 Ac Source ACDC Mode_Multi_S2(VDC) ---- ( PASS
(The Report Format of this Sequence was not found)
STEP.393(UUT Test seq.393) : Turn On Timing Test_Multi or Single(164VDC_LL) PASS
ElaspedTime (S)= 2'075
Vin (V)= 164.00
Fin (Hz)= 30.00
On Phase Delay(ms)= 90.00
UUT Off Time (s)= 0.00
Trigger: 1:TTL1R, 2:TTL2R, 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:TTL1F, 9:TTL2F,10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1.00
2 1.00
3 1.00
4 1.00
Load Loading Start End VcmpA VcmpB
Name (A/Ohm/V) Trigger Trigger (V) (V)
------------- ---------- ------- ------- ------- -------
12V 1.000 8 5 11.590 12.810
12Vsb 0.100 8 5 11.400 12.600
PWOK 0.000 8 5 2.600 3.460
Vin_Good 0.000 8 1 2.600 3.460
SMBAlert 0.000 8 1 2.600 3.460
Load Ton Ton Ton
Name Max Min (ms)
------------- -------- -------- ---------
12V 3000.00 1.00 1217.25
12Vsb 1500.00 1.00 972.72
PWOK ******** ******** 1423.10
Vin_Good ******** ******** 0.06
SMBAlert ******** ******** 0.06
Load Ref Load Td Td Td
Name No. Max Min (ms)
------------- ------------- -------- -------- ---------
12V 3 -500.00 -100.00 -205.85
12Vsb 1 -1500.00 -50.00 -244.53
PWOK 1 500.00 100.00 205.85
Vin_Good 0 ******** ******** 0.06
SMBAlert 0 ******** ******** 0.06
STEP.394(UUT Test seq.394) : I2C Read Status Multi_S6(164VDC_LL) ---- (0'12 PASS
Adderss :B0
Command Page00 :060200
Command Page01 :060201
Status Word :79
Status Byte :78
Status VOUT :7A
Status IOUT :7B
Status INPUT :7C
Status TEMPERATURE :7D
Status CML :7E
Status FANS :81
---------------------------------
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
----------------------------------
Word_Page_00 : 0
Word_Page_01 : 0
Status_Byte_P00 : 0
Status_Byte_P01 : 0
Status_VOUT_P00 : 0
Status_VOUT_P01 : 0
Status_IOUT_P00 : 0
Status_IOUT_P01 : 0
Status_INPUT_P00 : 0
Status_INPUT_P01 : 0
Status_TEM_P00 : 0
Status_TEM_P01 : 0
Status_CML_P00 : 0
Status_CML_P01 : 0
Status_FANS_P00 : 0
Status_FANS_P01 : 0
STEP.395(UUT Test seq.395) : PS OFF Time 80611(164VDC_LL) ---- (1'591) ---- PASS
Vin (V)= Refer to the previous item
Fin (Hz)= Refer to the previous item
On Phase Delay(ms)= Refer to the previous item
UUT Off Time (s)= Refer to the previous item
Loading (A/Ohm/V)= Refer to the previous item
Trigger: 1:Trig1R(AC), 2:Trig2R(PS on), 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:Trig1F(AC), 9:Trig2F(PS on),10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1
2 1
3 1
4 1
Load Start End VcmpA VcmpB
Name Trigger Trigger (V) (V)
------------- ------- ------- ------- -------
12V 2 12 11.590 12.810
12Vsb 2 2 11.400 12.600
PWOK 2 12 2.600 2.600
Vin_Good 2 2 2.600 2.600
SMBAlert 2 2 2.600 2.600
Load Ton Ton Ton
Name Max Min (ms)
------------- -------- -------- ---------
12V ******** ******** 5.48
12Vsb ******** ******** --------
PWOK 50.00 0.01 0.62
Vin_Good ******** ******** --------
SMBAlert ******** ******** --------
Load Ref Load Td Td Td
Name No. Max Min (ms)
------------- ---------- -------- -------- ---------
12V 3 100.00 1.00 4.86
12Vsb 0 ******** ******** --------
PWOK 1 -100.00 -1.00 -4.86
Vin_Good 0 ******** ******** --------
SMBAlert 0 ******** ******** --------
STEP.396(UUT Test seq.396) : I2C Read Status Multi_S6(StandBy) ---- (0'125) PASS
Adderss :B0
Command Page00 :060200
Command Page01 :060201
Status Word :79
Status Byte :78
Status VOUT :7A
Status IOUT :7B
Status INPUT :7C
Status TEMPERATURE :7D
Status CML :7E
Status FANS :81
---------------------------------
Word SPEC: 16392
Word SPEC: 16392
Word SPEC: 16392
Word SPEC: 16392
Word SPEC: 16392
Word SPEC: 16392
Word SPEC: 16392
Word SPEC: 16392
Word SPEC_Page1: 16392
Word SPEC_Page1: 16392
Word SPEC_Page1: 16392
Word SPEC_Page1: 16392
Word SPEC_Page1: 16392
Word SPEC_Page1: 16392
Word SPEC_Page1: 16392
Word SPEC_Page1: 16392
Byte SPEC : 64
Byte SPEC : 64
Byte SPEC : 64
Byte SPEC : 64
Byte SPEC : 64
Byte SPEC : 64
Byte SPEC : 64
Byte SPEC : 64
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
----------------------------------
Word_Page_00 : 16392
Word_Page_01 : 16392
Status_Byte_P00 : 64
Status_Byte_P01 : 64
Status_VOUT_P00 : 0
Status_VOUT_P01 : 0
Status_IOUT_P00 : 0
Status_IOUT_P01 : 0
Status_INPUT_P00 : 0
Status_INPUT_P01 : 0
Status_TEM_P00 : 0
Status_TEM_P01 : 0
Status_CML_P00 : 0
Status_CML_P01 : 0
Status_FANS_P00 : 0
Status_FANS_P01 : 0
STEP.397(UUT Test seq.397) : Check VinDC_Posi_Nega Status ---- (0'094) ---- PASS
(The Report Format of this Sequence was not found)
STEP.398(UUT Test seq.398) : Input Output Eff Noise Multi or Single(164VDC_ PASS
ElapsedTime (S)= 2'137
Vin (V)= 164.00
Fin (Hz)= 30.00
Delay Time (ms)= 500.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 0.000 ******* ******* 0.000
12Vsb 0.000 ******* ******* 0.000
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
-------Load---------------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V ???.??? ???.??? ???.???
12Vsb ???.??? ???.??? ???.???
PWOK ???.??? ???.??? ???.???
Vin_Good ???.??? ???.??? ???.???
SMBAlert ???.??? ???.??? ???.???
--------34970----------------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 0.400 ******* 0.143
12VSb 12.600 11.400 12.190
PWOK 0.400 ******* 0.039
Vin_Good 3.460 2.500 3.242
SMBAlert 3.460 2.500 3.219
IBUS ******* ******* 0.137
CR 0.400 ******* 0.003
Max Min Reading
------------- ---------- ---------- ----------
Vrms (V) ******** ******** 164.1966
PF 1.0000 ******** 0.0000
THDi (%) ******** * XXXXXXXX
Irms (A) ******** ******** 0.0000
Pin (W) ******** ******** 0.0000
Pout (W) ******** ******** 0.0000
Eff (%) ******** ******** 0.0000
Load Noise Range Noise B.W
Name (V) (MHz)
------------- ----------- ---------
12V 2 20.000
12Vsb 2 20.000
PWOK 2 20.000
Vin_Good 2 20.000
SMBAlert 2 20.000
Load Vpp Noise Vpp Noise Vpp Noise
Name Max(mV) Min(mV) (mV)
------------- ------------ ------------ ------------
12V 120.000 0.000 1.100
12Vsb 120.000 0.000 5.450
PWOK ********* ********* 14.830
Vin_Good ********* ********* 20.380
SMBAlert ********* ********* 23.140
STEP.399(UUT Test seq.399) : Input Output Eff Noise Multi or Single(164Vdc_ PASS
ElapsedTime (S)= 3'057
Vin (V)= 164.00
Fin (Hz)= 30.00
Delay Time (ms)= 500.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 1.000 ******* ******* 0.000
12Vsb 2.500 ******* ******* 2.500
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
-------Load---------------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V ???.??? ???.??? ???.???
12Vsb ???.??? ???.??? ???.???
PWOK ???.??? ???.??? ???.???
Vin_Good ???.??? ???.??? ???.???
SMBAlert ???.??? ???.??? ???.???
--------34970----------------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 0.400 ******* 0.001
12VSb 12.600 11.400 12.011
PWOK 0.400 ******* 0.037
Vin_Good 3.460 2.500 3.244
SMBAlert 3.460 2.500 3.214
IBUS ******* ******* 0.337
CR 0.400 ******* 0.001
Max Min Reading
------------- ---------- ---------- ----------
Vrms (V) ******** ******** 164.1712
PF 1.0000 ******** 0.9997
THDi (%) ******** * 956.1484
Irms (A) ******** ******** 0.2534
Pin (W) ******** ******** 41.5890
Pout (W) ******** ******** 30.0260
Eff (%) ******** ******** 72.1970
Load Noise Range Noise B.W
Name (V) (MHz)
------------- ----------- ---------
12V 2 20.000
12Vsb 2 20.000
PWOK 2 20.000
Vin_Good 2 20.000
SMBAlert 2 20.000
Load Vpp Noise Vpp Noise Vpp Noise
Name Max(mV) Min(mV) (mV)
------------- ------------ ------------ ------------
12V 120.000 0.000 0.230
12Vsb 120.000 0.000 2.430
PWOK ********* ********* 18.460
Vin_Good ********* ********* 25.100
SMBAlert ********* ********* 23.160
STEP.400(UUT Test seq.400) : Static ACDC 34970_or_Load_Multi or Single(12Vs PASS
ElapsedTime (S)= 1'248
Vin (V)= 164.00
Fin (Hz)= 30.00
Delay Time (ms)= 500.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 0.000 ******* ******* 0.000
12Vsb 2.750 ******* ******* 2.750
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 0.400 ******* 0.001
12VSb 12.600 11.400 12.011
PWOK 0.400 ******* 0.037
Vin_Good 3.460 2.500 3.242
SMBAlert 3.460 2.500 3.217
IBUS ******* ******* 0.318
CR 0.400 ******* 0.001
Max Min Reading
------------- --------- --------- ---------
Pout (W) ******* ******* 33.027
STEP.401(UUT Test seq.401) : Static ACDC 34970_or_Load_Multi or Single(12Vs PASS
ElapsedTime (S)= 1'264
Vin (V)= 164.00
Fin (Hz)= 30.00
Delay Time (ms)= 500.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 0.000 ******* ******* 0.000
12Vsb 3.650 ******* ******* 3.650
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 0.400 ******* 0.000
12VSb 12.600 ******* 11.665
PWOK 0.400 ******* 0.036
Vin_Good 3.460 2.400 3.245
SMBAlert 3.460 ******* 3.212
IBUS ******* ******* 0.312
CR 0.400 ******* 0.005
Max Min Reading
------------- --------- --------- ---------
Pout (W) ******* ******* 42.574
STEP.402(UUT Test seq.402) : Static ACDC 34970_or_Load_Multi or Single(12Vs PASS
ElapsedTime (S)= 1'747
Vin (V)= 164.00
Fin (Hz)= 30.00
Delay Time (ms)= 1000.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 0.000 ******* ******* 0.000
12Vsb 2.750 ******* ******* 2.750
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 0.400 ******* 0.001
12VSb 12.600 11.400 12.008
PWOK 0.400 ******* 0.037
Vin_Good 3.460 2.500 3.242
SMBAlert 3.460 2.500 3.214
IBUS ******* ******* 0.311
CR 0.400 ******* 0.001
Max Min Reading
------------- --------- --------- ---------
Pout (W) ******* ******* 33.021
STEP.403(UUT Test seq.403) : Input Output Eff Noise Multi or Single(164VDC_ PASS
ElapsedTime (S)= 1'919
Vin (V)= 164.00
Fin (Hz)= 30.00
Delay Time (ms)= 500.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 1.000 ******* ******* 0.000
12Vsb 0.100 ******* ******* 0.100
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
-------Load---------------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V ???.??? ???.??? ???.???
12Vsb ???.??? ???.??? ???.???
PWOK ???.??? ???.??? ???.???
Vin_Good ???.??? ???.??? ???.???
SMBAlert ???.??? ???.??? ???.???
--------34970----------------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 0.400 ******* 0.000
12VSb 12.600 11.400 12.148
PWOK 0.400 ******* 0.039
Vin_Good 3.460 2.500 3.241
SMBAlert 3.460 2.500 3.219
IBUS ******* ******* 0.293
CR 0.400 ******* 0.003
Max Min Reading
------------- ---------- ---------- ----------
Vrms (V) ******** ******** 164.1949
PF 1.0000 ******** 0.0000
THDi (%) ******** * XXXXXXXX
Irms (A) ******** ******** 0.0000
Pin (W) ******** ******** 0.0000
Pout (W) ******** ******** 1.2168
Eff (%) ******** ******** 0.0000
Load Noise Range Noise B.W
Name (V) (MHz)
------------- ----------- ---------
12V 2 20.000
12Vsb 2 20.000
PWOK 2 20.000
Vin_Good 2 20.000
SMBAlert 2 20.000
Load Vpp Noise Vpp Noise Vpp Noise
Name Max(mV) Min(mV) (mV)
------------- ------------ ------------ ------------
12V 120.000 0.000 0.100
12Vsb 120.000 0.000 8.290
PWOK ********* ********* 14.950
Vin_Good ********* ********* 20.860
SMBAlert ********* ********* 22.740
STEP.404(UUT Test seq.404) : PS ON Delay time 80611(164VDC_LL) ---- (0'874) PASS
Vin (V)= Refer to the previous item
Fin (Hz)= Refer to the previous item
On Phase Delay(ms)= Refer to the previous item
UUT Off Time (s)= Refer to the previous item
Loading (A/Ohm/V)= Refer to the previous item
Trigger: 1:Trig1R(AC), 2:Trig2R(PS on), 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:Trig1F(AC), 9:Trig2F(PS on),10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1
2 1
3 1
4 1
Load Start End VcmpA VcmpB
Name Trigger Trigger (V) (V)
------------- ------- ------- ------- -------
12V 9 5 11.590 12.810
12Vsb 9 9 11.400 12.600
PWOK 9 5 2.600 2.600
Vin_Good 9 9 2.600 2.600
SMBAlert 9 9 2.600 2.600
Load Ton Ton Ton
Name Max Min (ms)
------------- -------- -------- ---------
12V 400.00 5.00 62.19
12Vsb ******** ******** 0.17
PWOK ******** ******** 268.05
Vin_Good ******** ******** 0.17
SMBAlert ******** ******** 0.17
Load Ref Load Td Td Td
Name No. Max Min (ms)
------------- ---------- -------- -------- ---------
12V 3 -500.000 -100.000 -205.863
12Vsb 0 ********* ********* 0.171
PWOK 1 500.000 100.000 205.863
Vin_Good 0 ********* ********* 0.171
SMBAlert 0 ********* ********* 0.171
STEP.405(UUT Test seq.405) : Turn On Timing Test_Multi or Single(164VDC_LL_ PASS
ElaspedTime (S)= 1'747
Vin (V)= 164.00
Fin (Hz)= 30.00
On Phase Delay(ms)= 90.00
UUT Off Time (s)= 0.50
Trigger: 1:TTL1R, 2:TTL2R, 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:TTL1F, 9:TTL2F,10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1.00
2 1.00
3 1.00
4 1.00
Load Loading Start End VcmpA VcmpB
Name (A/Ohm/V) Trigger Trigger (V) (V)
------------- ---------- ------- ------- ------- -------
12V 1.000 5 6 1.220 11.590
12Vsb 0.100 5 6 1.200 10.800
PWOK 0.000 8 1 2.600 3.460
Vin_Good 0.000 8 1 2.600 3.460
SMBAlert 0.000 8 1 2.600 3.460
Load Ton Ton Ton
Name Max Min (ms)
------------- -------- -------- ---------
12V 70.00 5.00 51.26
12Vsb 70.00 1.00 12.50
PWOK ******** ******** 0.06
Vin_Good ******** ******** 0.06
SMBAlert ******** ******** 0.06
Load Ref Load Td Td Td
Name No. Max Min (ms)
------------- ------------- -------- -------- ---------
12V 0 ******** ******** 51.26
12Vsb 0 ******** ******** 12.50
PWOK 0 ******** ******** 0.06
Vin_Good 0 ******** ******** 0.06
SMBAlert 0 ******** ******** 0.06
STEP.406(UUT Test seq.406) : TTL & Relay Setup ---- (0'000) --------------- PASS
(The Report Format of this Sequence was not found)
STEP.407(UUT Test seq.407) : PS ON Delay time 80611(164VDC_LL_Tpson_12V_Ris PASS
Vin (V)= Refer to the previous item
Fin (Hz)= Refer to the previous item
On Phase Delay(ms)= Refer to the previous item
UUT Off Time (s)= Refer to the previous item
Loading (A/Ohm/V)= Refer to the previous item
Trigger: 1:Trig1R(AC), 2:Trig2R(PS on), 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:Trig1F(AC), 9:Trig2F(PS on),10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1
2 1
3 1
4 1
Load Start End VcmpA VcmpB
Name Trigger Trigger (V) (V)
------------- ------- ------- ------- -------
12V 5 6 1.220 11.590
12Vsb 9 9 1.200 10.800
PWOK 9 9 2.600 2.600
Vin_Good 9 9 2.600 2.600
SMBAlert 9 9 2.600 2.600
Load Ton Ton Ton
Name Max Min (ms)
------------- -------- -------- ---------
12V 70.00 5.00 51.28
12Vsb ******** ******** 0.17
PWOK ******** ******** 0.17
Vin_Good ******** ******** 0.17
SMBAlert ******** ******** 0.17
Load Ref Load Td Td Td
Name No. Max Min (ms)
------------- ---------- -------- -------- ---------
12V 0 ********* ********* 51.275
12Vsb 0 ********* ********* 0.174
PWOK 0 ********* ********* 0.173
Vin_Good 0 ********* ********* 0.174
SMBAlert 0 ********* ********* 0.174
STEP.408(UUT Test seq.408) : 12V OVP I2C Multi(OVP_I2C) ---- (0'062) ------ PASS
STEP.409(UUT Test seq.409) : Static ACDC 34970_or_Load_Multi or Single(164V PASS
ElapsedTime (S)= 1'264
Vin (V)= 164.00
Fin (Hz)= 30.00
Delay Time (ms)= 500.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 1.000 ******* ******* 0.000
12Vsb 0.100 ******* ******* 0.100
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 0.400 ******* 0.000
12VSb 12.600 11.400 12.140
PWOK 0.400 ******* 0.038
Vin_Good 3.460 2.500 3.245
SMBAlert 3.460 2.500 3.212
IBUS ******* ******* 0.314
CR 0.400 ******* 0.004
Max Min Reading
------------- --------- --------- ---------
Pout (W) ******* ******* 1.216
STEP.410(UUT Test seq.410) : I2C Read Status OR Multi_S6(12V_OV) ---- (0'10 PASS
Command Page00 :060200
Command Page01 :060201
Status Word :79
Status Byte :78
Status VOUT :7A
Status IOUT :7B
Status INPUT :7C
Status TEMPERATURE :7D
Status CML :7E
Status FANS :81
---------------------------------
Word SPEC: 25224
Word SPEC: 25224
Word SPEC: 25224
Word SPEC: 25224
Word SPEC: 25224
Word SPEC: 25224
Word SPEC: 25224
Word SPEC: 25224
Word SPEC_Page1: 25224
Word SPEC_Page1: 25224
Word SPEC_Page1: 25224
Word SPEC_Page1: 25224
Word SPEC_Page1: 25224
Word SPEC_Page1: 25224
Word SPEC_Page1: 25224
Word SPEC_Page1: 25224
Byte SPEC : 98
Byte SPEC : 98
Byte SPEC : 98
Byte SPEC : 98
Byte SPEC : 98
Byte SPEC : 98
Byte SPEC : 98
Byte SPEC : 98
VOUT SPEC : 192
VOUT SPEC : 192
VOUT SPEC : 192
VOUT SPEC : 192
VOUT SPEC : 192
VOUT SPEC : 192
VOUT SPEC : 192
VOUT SPEC : 192
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
CML SPEC : 128
CML SPEC : 128
CML SPEC : 128
CML SPEC : 128
CML SPEC : 128
CML SPEC : 128
CML SPEC : 128
CML SPEC : 128
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
Word Page0 OR : 0200
Word Page1 OR : 0200
Byte OR : 02
Input OR : 00
IOUT OR : 00
TEMP OR : 00
CML OR : 80
----------------------------------
Word_Page_00 : 25224
Word_Page_01 : 25224
Status_Byte_P00 : 98
Status_Byte_P01 : 98
Status_VOUT_P00 : 192
Status_VOUT_P01 : 192
Status_IOUT_P00 : 0
Status_IOUT_P01 : 0
Status_INPUT_P00 : 0
Status_INPUT_P01 : 0
Status_TEM_P00 : 0
Status_TEM_P01 : 0
Status_CML_P00 : 128
Status_CML_P01 : 128
Status_FANS_P00 : 0
Status_FANS_P01 : 0
STEP.411(UUT Test seq.411) : 12V OVP Disable I2C Multi ---- (0'062) ------- PASS
STEP.412(UUT Test seq.412) : TTL & Relay Setup ---- (0'624) --------------- PASS
(The Report Format of this Sequence was not found)
STEP.413(UUT Test seq.413) : Input Output Eff Noise Multi or Single(No Load PASS
ElapsedTime (S)= 1'388
Vin (V)= 164.00
Fin (Hz)= 30.00
Delay Time (ms)= 0.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 0.000 ******* ******* 0.000
12Vsb 0.000 ******* ******* 0.000
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
-------Load---------------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V ???.??? ???.??? ???.???
12Vsb ???.??? ???.??? ???.???
PWOK ???.??? ???.??? ???.???
Vin_Good ???.??? ???.??? ???.???
SMBAlert ???.??? ???.??? ???.???
--------34970----------------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 12.810 11.590 12.246
12VSb 12.600 11.400 12.192
PWOK 3.460 2.500 3.250
Vin_Good 3.460 2.500 3.250
SMBAlert 3.460 2.500 3.211
IBUS 0.300 -0.300 0.017
CR 0.400 ******* 0.003
Max Min Reading
------------- ---------- ---------- ----------
Vrms (V) ******** ******** 164.1930
PF 1.0000 ******** 0.0000
THDi (%) ******** * 71.3454
Irms (A) ******** ******** 0.0000
Pin (W) ******** ******** 0.0000
Pout (W) ******** ******** 0.0000
Eff (%) ******** ******** 0.0000
Load Noise Range Noise B.W
Name (V) (MHz)
------------- ----------- ---------
12V 2 20.000
12Vsb 2 20.000
PWOK 2 20.000
Vin_Good 2 20.000
SMBAlert 2 20.000
Load Vpp Noise Vpp Noise Vpp Noise
Name Max(mV) Min(mV) (mV)
------------- ------------ ------------ ------------
12V 120.000 0.000 8.830
12Vsb 120.000 0.000 5.470
PWOK ********* ********* 19.620
Vin_Good ********* ********* 18.630
SMBAlert ********* ********* 22.230
STEP.414(UUT Test seq.414) : Static ACDC 34970_or_Load_Multi or Single(12Vs PASS
ElapsedTime (S)= 1'201
Vin (V)= 164.00
Fin (Hz)= 30.00
Delay Time (ms)= 500.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 1.000 ******* ******* 0.998
12Vsb 2.750 ******* ******* 2.750
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 12.810 11.590 12.259
12VSb 12.600 11.400 12.005
PWOK 3.460 2.500 3.243
Vin_Good 3.460 2.500 3.249
SMBAlert 3.460 2.500 3.213
IBUS ******* ******* 0.059
CR 0.400 ******* 0.001
Max Min Reading
------------- --------- --------- ---------
Pout (W) ******* ******* 45.243
STEP.415(UUT Test seq.415) : Static ACDC 34970_or_Load_Multi or Single(12Vs PASS
ElapsedTime (S)= 1'420
Vin (V)= 164.00
Fin (Hz)= 30.00
Delay Time (ms)= 500.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 1.000 ******* ******* 0.000
12Vsb 3.650 ******* ******* 0.011
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 0.400 ******* 0.001
12VSb 12.600 ******* 11.977
PWOK 0.400 ******* 0.039
Vin_Good 3.460 2.400 3.245
SMBAlert 3.460 ******* 3.214
IBUS ******* ******* 0.124
CR 0.400 ******* 0.005
Max Min Reading
------------- --------- --------- ---------
Pout (W) ******* ******* 0.132
STEP.416(UUT Test seq.416) : Static ACDC 34970_or_Load_Multi or Single(12Vs PASS
ElapsedTime (S)= 1'935
Vin (V)= 164.00
Fin (Hz)= 30.00
Delay Time (ms)= 1000.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 1.000 ******* ******* 0.998
12Vsb 2.750 ******* ******* 2.750
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 12.810 11.590 12.257
12VSb 12.600 11.400 12.008
PWOK 3.460 2.500 3.243
Vin_Good 3.460 2.500 3.245
SMBAlert 3.460 2.500 3.218
IBUS ******* ******* 0.063
CR 0.400 ******* 0.002
Max Min Reading
------------- --------- --------- ---------
Pout (W) ******* ******* 45.249
STEP.417(UUT Test seq.417) : Input Output Eff Noise Multi or Single(164VDC_ PASS
ElapsedTime (S)= 1'810
Vin (V)= 164.00
Fin (Hz)= 30.00
Delay Time (ms)= 500.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 1.000 ******* ******* 0.998
12Vsb 0.100 ******* ******* 0.100
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
-------Load---------------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V ???.??? ???.??? ???.???
12Vsb ???.??? ???.??? ???.???
PWOK ???.??? ???.??? ???.???
Vin_Good ???.??? ???.??? ???.???
SMBAlert ???.??? ???.??? ???.???
--------34970----------------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 12.810 11.590 12.259
12VSb 12.600 11.400 12.145
PWOK 3.460 2.500 3.250
Vin_Good 3.460 2.500 3.244
SMBAlert 3.460 2.500 3.219
IBUS ******* ******* 0.062
CR 0.400 ******* 0.003
Max Min Reading
------------- ---------- ---------- ----------
Vrms (V) ******** ******** 164.1874
PF 1.0000 ******** 0.9984
THDi (%) ******** * 276.8409
Irms (A) ******** ******** 0.1081
Pin (W) ******** ******** 17.7285
Pout (W) ******** ******** 13.4465
Eff (%) ******** ******** 75.8472
Load Noise Range Noise B.W
Name (V) (MHz)
------------- ----------- ---------
12V 2 20.000
12Vsb 2 20.000
PWOK 2 20.000
Vin_Good 2 20.000
SMBAlert 2 20.000
Load Vpp Noise Vpp Noise Vpp Noise
Name Max(mV) Min(mV) (mV)
------------- ------------ ------------ ------------
12V 120.000 0.000 7.950
12Vsb 120.000 0.000 7.540
PWOK ********* ********* 19.180
Vin_Good ********* ********* 17.980
SMBAlert ********* ********* 21.720
STEP.418(UUT Test seq.418) : Input Output Eff Noise Multi or Single(164VDC_ PASS
ElapsedTime (S)= 1'747
Vin (V)= 164.00
Fin (Hz)= 30.00
Delay Time (ms)= 500.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 1.000 ******* ******* 0.998
12Vsb 2.500 ******* ******* 2.500
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
-------Load---------------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V ???.??? ???.??? ???.???
12Vsb ???.??? ???.??? ???.???
PWOK ???.??? ???.??? ???.???
Vin_Good ???.??? ???.??? ???.???
SMBAlert ???.??? ???.??? ???.???
--------34970----------------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 12.810 11.590 12.259
12VSb 12.600 11.400 12.013
PWOK 3.460 2.500 3.248
Vin_Good 3.460 2.500 3.243
SMBAlert 3.460 2.500 3.220
IBUS ******* ******* 0.060
CR 0.400 ******* 0.002
Max Min Reading
------------- ---------- ---------- ----------
Vrms (V) ******** ******** 164.1633
PF 1.0000 ******** 0.9992
THDi (%) ******** * 58.3411
Irms (A) ******** ******** 0.3406
Pin (W) ******** ******** 55.8780
Pout (W) ******** ******** 42.2601
Eff (%) ******** ******** 75.6291
Load Noise Range Noise B.W
Name (V) (MHz)
------------- ----------- ---------
12V 2 20.000
12Vsb 2 20.000
PWOK 2 20.000
Vin_Good 2 20.000
SMBAlert 2 20.000
Load Vpp Noise Vpp Noise Vpp Noise
Name Max(mV) Min(mV) (mV)
------------- ------------ ------------ ------------
12V 120.000 0.000 6.990
12Vsb 120.000 0.000 2.970
PWOK ********* ********* 19.400
Vin_Good ********* ********* 18.840
SMBAlert ********* ********* 21.480
STEP.419(UUT Test seq.419) : Cold Redundant Master Multi _S2 ---- (0'093) - PASS
(The Report Format of this Sequence was not found)
STEP.420(UUT Test seq.420) : Static ACDC 34970_or_Load_Multi or Single(164V PASS
ElapsedTime (S)= 1'217
Vin (V)= 164.00
Fin (Hz)= 30.00
Delay Time (ms)= 500.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 1.000 ******* ******* 0.998
12Vsb 0.100 ******* ******* 0.100
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 12.810 11.590 12.258
12VSb 12.600 11.400 12.144
PWOK 3.460 2.500 3.245
Vin_Good 3.460 2.500 3.241
SMBAlert 3.460 2.500 3.219
IBUS ******* ******* 0.063
CR 3.460 2.500 3.190
Max Min Reading
------------- --------- --------- ---------
Pout (W) ******* ******* 13.447
STEP.421(UUT Test seq.421) : Disable Cold Redundant Master Multi_S2 ---- (0 PASS
(The Report Format of this Sequence was not found)
STEP.422(UUT Test seq.422) : Static ACDC 34970_or_Load_Multi or Single(164V PASS
ElapsedTime (S)= 1'295
Vin (V)= 164.00
Fin (Hz)= 30.00
Delay Time (ms)= 500.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 1.000 ******* ******* 0.998
12Vsb 0.100 ******* ******* 0.100
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 12.810 11.590 12.259
12VSb 12.600 11.400 12.141
PWOK 3.460 2.500 3.246
Vin_Good 3.460 2.500 3.246
SMBAlert 3.460 2.500 3.218
IBUS ******* ******* 0.061
CR 0.400 ******* 0.003
Max Min Reading
------------- --------- --------- ---------
Pout (W) ******* ******* 13.448
STEP.423(UUT Test seq.423) : Hold Up Timing Test_Multi or Single(164VDC_LL) PASS
ElapsedTime (S)= 0'702
Vin (V)= 164.00
Fin (Hz)= 30.00
Delay Time (ms)= 0.00
On Phase Delay(ms)= 90.00
UUT Off Time (s)= 0.00
Trigger: 1:Trig1R(AC), 2:Trig2R(PS on), 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:Trig1F(AC), 9:Trig2F(PS on),10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1
2 1
3 1
4 1
Load Loading Start End VcmpA VcmpB
Name (A/Ohm/V) Trigger Trigger (V) (V)
------------- ---------- ------- ------- ------- -------
12V 1.000 8 12 11.590 12.810
12Vsb 0.100 8 12 11.400 12.600
PWOK 0.000 8 12 2.600 3.460
Vin_Good 0.000 8 12 2.600 3.460
SMBAlert 0.000 8 1 2.600 3.460
Load Tholdup Tholdup Tholdup
Name Max Min (ms)
------------- -------- -------- ---------
12V 1000.00 10.00 48.13
12Vsb 1000.00 70.00 92.03
PWOK 300.00 9.00 43.48
Vin_Good 4.00 0.01 2.60
SMBAlert ******** ******** 0.06
Load Ref Load Tholdup Tholdup Tholdup
Name No. Max Min (ms)
------------- ---------- -------- -------- ---------
12V 3 100.00 1.00 4.65
12Vsb 0 ******** ******** 92.03
PWOK 1 -100.00 -1.00 -4.65
Vin_Good 0 ******** ******** 2.60
SMBAlert 0 ******** ******** 0.06
STEP.424(UUT Test seq.424) : FAN Full Speed delay time Multi ---- (8'096) - PASS
STEP.425(UUT Test seq.425) : FAN Speed Normal_Multi ---- (0'094) ---------- PASS
(The Report Format of this Sequence was not found)
STEP.426(UUT Test seq.426) : Turn On Timing Test_Multi or Single(164VDC_HH) PASS
ElaspedTime (S)= 1'981
Vin (V)= 164.00
Fin (Hz)= 30.00
On Phase Delay(ms)= 90.00
UUT Off Time (s)= 0.00
Trigger: 1:TTL1R, 2:TTL2R, 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:TTL1F, 9:TTL2F,10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1.00
2 1.00
3 1.00
4 1.00
Load Loading Start End VcmpA VcmpB
Name (A/Ohm/V) Trigger Trigger (V) (V)
------------- ---------- ------- ------- ------- -------
12V 128.700 8 5 11.590 12.810
12Vsb 2.500 8 5 11.400 12.600
PWOK 0.000 8 5 2.600 3.460
Vin_Good 0.000 8 1 2.600 3.460
SMBAlert 0.000 8 1 2.600 3.460
Load Ton Ton Ton
Name Max Min (ms)
------------- -------- -------- ---------
12V 3000.00 1.00 1230.17
12Vsb 1500.00 1.00 984.63
PWOK ******** ******** 1435.75
Vin_Good ******** ******** 0.06
SMBAlert ******** ******** 0.06
Load Ref Load Td Td Td
Name No. Max Min (ms)
------------- ------------- -------- -------- ---------
12V 3 -500.00 -100.00 -205.58
12Vsb 1 -1500.00 -50.00 -245.54
PWOK 1 500.00 100.00 205.58
Vin_Good 0 ******** ******** 0.06
SMBAlert 0 ******** ******** 0.06
STEP.427(UUT Test seq.427) : I2C Read Status Multi_S6(164VDC_HH) ---- (0'14 PASS
Adderss :B0
Command Page00 :060200
Command Page01 :060201
Status Word :79
Status Byte :78
Status VOUT :7A
Status IOUT :7B
Status INPUT :7C
Status TEMPERATURE :7D
Status CML :7E
Status FANS :81
---------------------------------
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
----------------------------------
Word_Page_00 : 0
Word_Page_01 : 0
Status_Byte_P00 : 0
Status_Byte_P01 : 0
Status_VOUT_P00 : 0
Status_VOUT_P01 : 0
Status_IOUT_P00 : 0
Status_IOUT_P01 : 0
Status_INPUT_P00 : 0
Status_INPUT_P01 : 0
Status_TEM_P00 : 0
Status_TEM_P01 : 0
Status_CML_P00 : 0
Status_CML_P01 : 0
Status_FANS_P00 : 0
Status_FANS_P01 : 0
STEP.428(UUT Test seq.428) : PS OFF Time 80611(164VDC_HH) ---- (1'560) ---- PASS
Vin (V)= Refer to the previous item
Fin (Hz)= Refer to the previous item
On Phase Delay(ms)= Refer to the previous item
UUT Off Time (s)= Refer to the previous item
Loading (A/Ohm/V)= Refer to the previous item
Trigger: 1:Trig1R(AC), 2:Trig2R(PS on), 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:Trig1F(AC), 9:Trig2F(PS on),10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1
2 1
3 1
4 1
Load Start End VcmpA VcmpB
Name Trigger Trigger (V) (V)
------------- ------- ------- ------- -------
12V 2 12 11.590 12.810
12Vsb 2 2 11.400 12.600
PWOK 2 12 2.600 2.600
Vin_Good 2 2 2.600 2.600
SMBAlert 2 2 2.600 2.600
Load Ton Ton Ton
Name Max Min (ms)
------------- -------- -------- ---------
12V ******** ******** 2.32
12Vsb ******** ******** --------
PWOK 50.00 0.01 0.66
Vin_Good ******** ******** --------
SMBAlert ******** ******** --------
Load Ref Load Td Td Td
Name No. Max Min (ms)
------------- ---------- -------- -------- ---------
12V 3 100.00 1.00 1.66
12Vsb 0 ******** ******** --------
PWOK 1 -100.00 -1.00 -1.66
Vin_Good 0 ******** ******** --------
SMBAlert 0 ******** ******** --------
STEP.429(UUT Test seq.429) : I2C Read Status Multi_S6(StandBy) ---- (0'125) PASS
Adderss :B0
Command Page00 :060200
Command Page01 :060201
Status Word :79
Status Byte :78
Status VOUT :7A
Status IOUT :7B
Status INPUT :7C
Status TEMPERATURE :7D
Status CML :7E
Status FANS :81
---------------------------------
Word SPEC: 16392
Word SPEC: 16392
Word SPEC: 16392
Word SPEC: 16392
Word SPEC: 16392
Word SPEC: 16392
Word SPEC: 16392
Word SPEC: 16392
Word SPEC_Page1: 16392
Word SPEC_Page1: 16392
Word SPEC_Page1: 16392
Word SPEC_Page1: 16392
Word SPEC_Page1: 16392
Word SPEC_Page1: 16392
Word SPEC_Page1: 16392
Word SPEC_Page1: 16392
Byte SPEC : 64
Byte SPEC : 64
Byte SPEC : 64
Byte SPEC : 64
Byte SPEC : 64
Byte SPEC : 64
Byte SPEC : 64
Byte SPEC : 64
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
----------------------------------
Word_Page_00 : 16392
Word_Page_01 : 16392
Status_Byte_P00 : 64
Status_Byte_P01 : 64
Status_VOUT_P00 : 0
Status_VOUT_P01 : 0
Status_IOUT_P00 : 0
Status_IOUT_P01 : 0
Status_INPUT_P00 : 0
Status_INPUT_P01 : 0
Status_TEM_P00 : 0
Status_TEM_P01 : 0
Status_CML_P00 : 0
Status_CML_P01 : 0
Status_FANS_P00 : 0
Status_FANS_P01 : 0
STEP.430(UUT Test seq.430) : PS ON Delay time 80611(164VDC_HH) ---- (0'858) PASS
Vin (V)= Refer to the previous item
Fin (Hz)= Refer to the previous item
On Phase Delay(ms)= Refer to the previous item
UUT Off Time (s)= Refer to the previous item
Loading (A/Ohm/V)= Refer to the previous item
Trigger: 1:Trig1R(AC), 2:Trig2R(PS on), 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:Trig1F(AC), 9:Trig2F(PS on),10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1
2 1
3 1
4 1
Load Start End VcmpA VcmpB
Name Trigger Trigger (V) (V)
------------- ------- ------- ------- -------
12V 9 5 11.590 12.810
12Vsb 9 9 11.400 12.600
PWOK 9 5 2.600 2.600
Vin_Good 9 9 2.600 2.600
SMBAlert 9 9 2.600 2.600
Load Ton Ton Ton
Name Max Min (ms)
------------- -------- -------- ---------
12V 400.00 5.00 62.59
12Vsb ******** ******** 0.17
PWOK ******** ******** 268.08
Vin_Good ******** ******** 0.17
SMBAlert ******** ******** 0.17
Load Ref Load Td Td Td
Name No. Max Min (ms)
------------- ---------- -------- -------- ---------
12V 3 -500.000 -100.000 -205.484
12Vsb 0 ********* ********* 0.169
PWOK 1 500.000 100.000 205.484
Vin_Good 0 ********* ********* 0.169
SMBAlert 0 ********* ********* 0.169
STEP.431(UUT Test seq.431) : Turn On Timing Test_Multi or Single(164VDC_HH_ PASS
ElaspedTime (S)= 1'981
Vin (V)= 164.00
Fin (Hz)= 30.00
On Phase Delay(ms)= 90.00
UUT Off Time (s)= 0.50
Trigger: 1:TTL1R, 2:TTL2R, 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:TTL1F, 9:TTL2F,10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1.00
2 1.00
3 1.00
4 1.00
Load Loading Start End VcmpA VcmpB
Name (A/Ohm/V) Trigger Trigger (V) (V)
------------- ---------- ------- ------- ------- -------
12V 128.700 5 6 1.220 11.590
12Vsb 2.500 5 6 1.200 10.800
PWOK 0.000 8 1 2.600 3.460
Vin_Good 0.000 8 1 2.600 3.460
SMBAlert 0.000 8 1 2.600 3.460
Load Ton Ton Ton
Name Max Min (ms)
------------- -------- -------- ---------
12V 70.00 5.00 51.24
12Vsb 70.00 1.00 11.70
PWOK ******** ******** 0.06
Vin_Good ******** ******** 0.06
SMBAlert ******** ******** 0.06
Load Ref Load Td Td Td
Name No. Max Min (ms)
------------- ------------- -------- -------- ---------
12V 0 ******** ******** 51.24
12Vsb 0 ******** ******** 11.70
PWOK 0 ******** ******** 0.06
Vin_Good 0 ******** ******** 0.06
SMBAlert 0 ******** ******** 0.06
STEP.432(UUT Test seq.432) : TTL & Relay Setup ---- (0'000) --------------- PASS
(The Report Format of this Sequence was not found)
STEP.433(UUT Test seq.433) : PS ON Delay time 80611(164VDC_HH_Tpson_12V_Ris PASS
Vin (V)= Refer to the previous item
Fin (Hz)= Refer to the previous item
On Phase Delay(ms)= Refer to the previous item
UUT Off Time (s)= Refer to the previous item
Loading (A/Ohm/V)= Refer to the previous item
Trigger: 1:Trig1R(AC), 2:Trig2R(PS on), 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:Trig1F(AC), 9:Trig2F(PS on),10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1
2 1
3 1
4 1
Load Start End VcmpA VcmpB
Name Trigger Trigger (V) (V)
------------- ------- ------- ------- -------
12V 5 6 1.220 11.590
12Vsb 9 9 1.200 10.800
PWOK 9 9 2.600 2.600
Vin_Good 9 9 2.600 2.600
SMBAlert 9 9 2.600 2.600
Load Ton Ton Ton
Name Max Min (ms)
------------- -------- -------- ---------
12V 70.00 5.00 51.21
12Vsb ******** ******** 0.17
PWOK ******** ******** 0.17
Vin_Good ******** ******** 0.17
SMBAlert ******** ******** 0.17
Load Ref Load Td Td Td
Name No. Max Min (ms)
------------- ---------- -------- -------- ---------
12V 0 ********* ********* 51.215
12Vsb 0 ********* ********* 0.168
PWOK 0 ********* ********* 0.168
Vin_Good 0 ********* ********* 0.168
SMBAlert 0 ********* ********* 0.167
STEP.434(UUT Test seq.434) : Input Output Eff Noise Multi or Single(164VDC_ PASS
ElapsedTime (S)= 1'965
Vin (V)= 164.00
Fin (Hz)= 30.00
Delay Time (ms)= 500.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 64.350 ******* ******* 64.348
12Vsb 1.250 ******* ******* 1.250
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
-------Load---------------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V ???.??? ???.??? ???.???
12Vsb ???.??? ???.??? ???.???
PWOK ???.??? ???.??? ???.???
Vin_Good ???.??? ???.??? ???.???
SMBAlert ???.??? ???.??? ???.???
--------34970----------------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 12.810 11.590 12.225
12VSb 12.600 11.400 12.045
PWOK 3.460 2.500 3.239
Vin_Good 3.460 2.500 3.240
SMBAlert 3.460 2.500 3.216
IBUS ******* ******* 3.191
CR 0.400 ******* -0.007
Max Min Reading
------------- ---------- ---------- ----------
Vrms (V) ******** ******** 163.7650
PF 1.0000 ******** 1.0000
THDi (%) ******** * 204.9107
Irms (A) ******** ******** 5.4255
Pin (W) ******** ******** 888.4702
Pout (W) ******** ******** 801.6752
Eff (%) ******** ******** 90.2310
Load Noise Range Noise B.W
Name (V) (MHz)
------------- ----------- ---------
12V 2 20.000
12Vsb 2 20.000
PWOK 2 20.000
Vin_Good 2 20.000
SMBAlert 2 20.000
Load Vpp Noise Vpp Noise Vpp Noise
Name Max(mV) Min(mV) (mV)
------------- ------------ ------------ ------------
12V 120.000 0.000 12.030
12Vsb 120.000 0.000 11.410
PWOK ********* ********* 24.320
Vin_Good ********* ********* 22.870
SMBAlert ********* ********* 26.210
STEP.435(UUT Test seq.435) : Input Output Eff Noise Multi or Single(164VDC_ PASS
ElapsedTime (S)= 1'748
Vin (V)= 164.00
Fin (Hz)= 30.00
Delay Time (ms)= 500.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 128.700 ******* ******* 128.697
12Vsb 2.500 ******* ******* 2.500
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
-------Load---------------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V ???.??? ???.??? ???.???
12Vsb ???.??? ???.??? ???.???
PWOK ???.??? ???.??? ???.???
Vin_Good ???.??? ???.??? ???.???
SMBAlert ???.??? ???.??? ???.???
--------34970----------------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 12.810 11.590 12.186
12VSb 12.600 11.400 11.996
PWOK 3.460 2.500 3.225
Vin_Good 3.460 2.500 3.231
SMBAlert 3.460 2.500 3.220
IBUS ******* ******* 6.355
CR 0.400 ******* -0.017
Max Min Reading
------------- ---------- ---------- ----------
Vrms (V) ******** ******** 163.2761
PF 1.0000 ******** 0.9999
THDi (%) ******** * 117.7903
Irms (A) ******** ******** 10.9059
Pin (W) ******** ******** XXXXXXXX
Pout (W) ******** ******** XXXXXXXX
Eff (%) ******** ******** 89.7633
Load Noise Range Noise B.W
Name (V) (MHz)
------------- ----------- ---------
12V 2 20.000
12Vsb 2 20.000
PWOK 2 20.000
Vin_Good 2 20.000
SMBAlert 2 20.000
Load Vpp Noise Vpp Noise Vpp Noise
Name Max(mV) Min(mV) (mV)
------------- ------------ ------------ ------------
12V 120.000 0.000 12.620
12Vsb 120.000 0.000 14.780
PWOK ********* ********* 27.620
Vin_Good ********* ********* 24.920
SMBAlert ********* ********* 29.730
STEP.436(UUT Test seq.436) : Static ACDC 34970_or_Load_Multi or Single(164V PASS
ElapsedTime (S)= 1'201
Vin (V)= 164.00
Fin (Hz)= 30.00
Delay Time (ms)= 500.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 128.700 ******* ******* 128.697
12Vsb 2.750 ******* ******* 2.750
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 12.810 11.590 12.188
12VSb 12.600 11.400 11.993
PWOK 3.460 2.500 3.228
Vin_Good 3.460 2.500 3.225
SMBAlert 3.460 2.500 3.227
IBUS ******* ******* 6.357
CR 0.400 ******* -0.017
Max Min Reading
------------- --------- --------- ---------
Pout (W) ******* ******* XXXXXXX
STEP.437(UUT Test seq.437) : Static ACDC 34970_or_Load_Multi or Single(164V PASS
ElapsedTime (S)= 1'420
Vin (V)= 164.00
Fin (Hz)= 30.00
Delay Time (ms)= 500.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 128.700 ******* ******* 0.000
12Vsb 3.650 ******* ******* 0.011
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 0.400 ******* 0.001
12VSb 12.600 ******* 11.977
PWOK 0.400 ******* 0.039
Vin_Good 3.460 2.400 3.245
SMBAlert 3.460 ******* 3.213
IBUS ******* ******* 0.151
CR 0.400 ******* 0.005
Max Min Reading
------------- --------- --------- ---------
Pout (W) ******* ******* 0.126
STEP.438(UUT Test seq.438) : Static ACDC 34970_or_Load_Multi or Single(164V PASS
ElapsedTime (S)= 1'872
Vin (V)= 164.00
Fin (Hz)= 30.00
Delay Time (ms)= 1000.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 128.700 ******* ******* 128.697
12Vsb 2.750 ******* ******* 2.750
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 12.810 11.590 12.182
12VSb 12.600 11.400 11.991
PWOK 3.460 2.500 3.230
Vin_Good 3.460 2.500 3.231
SMBAlert 3.460 2.500 3.218
IBUS ******* ******* 6.358
CR 0.400 ******* -0.017
Max Min Reading
------------- --------- --------- ---------
Pout (W) ******* ******* XXXXXXX
STEP.439(UUT Test seq.439) : Cold Redundant Master Multi _S2 ---- (0'093) - PASS
(The Report Format of this Sequence was not found)
STEP.440(UUT Test seq.440) : Static ACDC 34970_or_Load_Multi or Single(164V PASS
ElapsedTime (S)= 1'295
Vin (V)= 164.00
Fin (Hz)= 30.00
Delay Time (ms)= 500.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 128.700 ******* ******* 128.697
12Vsb 2.500 ******* ******* 2.500
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 12.810 11.590 12.188
12VSb 12.600 11.400 12.000
PWOK 3.460 2.500 3.228
Vin_Good 3.460 2.500 3.222
SMBAlert 3.460 2.500 3.222
IBUS ******* ******* 6.358
CR 3.460 2.500 3.171
Max Min Reading
------------- --------- --------- ---------
Pout (W) ******* ******* XXXXXXX
STEP.441(UUT Test seq.441) : Disable Cold Redundant Master Multi_S2 ---- (0 PASS
(The Report Format of this Sequence was not found)
STEP.442(UUT Test seq.442) : Static ACDC 34970_or_Load_Multi or Single(164V PASS
ElapsedTime (S)= 1'248
Vin (V)= 164.00
Fin (Hz)= 30.00
Delay Time (ms)= 500.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 128.700 ******* ******* 128.697
12Vsb 2.500 ******* ******* 2.500
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 12.810 11.590 12.187
12VSb 12.600 11.400 11.998
PWOK 3.460 2.500 3.227
Vin_Good 3.460 2.500 3.231
SMBAlert 3.460 2.500 3.218
IBUS ******* ******* 6.357
CR 0.400 ******* -0.017
Max Min Reading
------------- --------- --------- ---------
Pout (W) ******* ******* XXXXXXX
STEP.443(UUT Test seq.443) : Input Output Eff Noise Multi or Single(164VDC_ PASS
ElapsedTime (S)= 1'887
Vin (V)= 164.00
Fin (Hz)= 30.00
Delay Time (ms)= 500.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 128.700 ******* ******* 128.697
12Vsb 0.100 ******* ******* 0.100
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
-------Load---------------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V ???.??? ???.??? ???.???
12Vsb ???.??? ???.??? ???.???
PWOK ???.??? ???.??? ???.???
Vin_Good ???.??? ???.??? ???.???
SMBAlert ???.??? ???.??? ???.???
--------34970----------------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 12.810 11.590 12.187
12VSb 12.600 11.400 12.128
PWOK 3.460 2.500 3.230
Vin_Good 3.460 2.500 3.228
SMBAlert 3.460 2.500 3.226
IBUS ******* ******* 6.360
CR 0.400 ******* -0.015
Max Min Reading
------------- ---------- ---------- ----------
Vrms (V) ******** ******** 163.3344
PF 1.0000 ******** 1.0000
THDi (%) ******** * 433.0768
Irms (A) ******** ******** 10.6857
Pin (W) ******** ******** XXXXXXXX
Pout (W) ******** ******** XXXXXXXX
Eff (%) ******** ******** 89.9335
Load Noise Range Noise B.W
Name (V) (MHz)
------------- ----------- ---------
12V 2 20.000
12Vsb 2 20.000
PWOK 2 20.000
Vin_Good 2 20.000
SMBAlert 2 20.000
Load Vpp Noise Vpp Noise Vpp Noise
Name Max(mV) Min(mV) (mV)
------------- ------------ ------------ ------------
12V 120.000 0.000 13.950
12Vsb 120.000 0.000 6.210
PWOK ********* ********* 25.670
Vin_Good ********* ********* 23.890
SMBAlert ********* ********* 28.770
STEP.444(UUT Test seq.444) : Hold Up Timing Test_Multi or Single(164VDC_70% PASS
ElapsedTime (S)= 0'951
Vin (V)= 164.00
Fin (Hz)= 30.00
Delay Time (ms)= 200.00
On Phase Delay(ms)= 90.00
UUT Off Time (s)= 0.00
Trigger: 1:Trig1R(AC), 2:Trig2R(PS on), 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:Trig1F(AC), 9:Trig2F(PS on),10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1
2 1
3 1
4 1
Load Loading Start End VcmpA VcmpB
Name (A/Ohm/V) Trigger Trigger (V) (V)
------------- ---------- ------- ------- ------- -------
12V 90.090 8 12 11.590 12.810
12Vsb 1.750 8 12 11.400 12.600
PWOK 0.000 8 12 2.600 3.460
Vin_Good 0.000 8 12 2.600 3.460
SMBAlert 0.000 8 1 2.600 3.460
Load Tholdup Tholdup Tholdup
Name Max Min (ms)
------------- -------- -------- ---------
12V 1000.00 10.00 26.81
12Vsb 1000.00 70.00 78.98
PWOK 300.00 9.00 25.14
Vin_Good 4.00 0.01 2.60
SMBAlert ******** ******** 0.06
Load Ref Load Tholdup Tholdup Tholdup
Name No. Max Min (ms)
------------- ---------- -------- -------- ---------
12V 3 100.00 1.00 1.67
12Vsb 0 ******** ******** 78.98
PWOK 1 -100.00 -1.00 -1.67
Vin_Good 0 ******** ******** 2.60
SMBAlert 0 ******** ******** 0.06
STEP.445(UUT Test seq.445) : FAN Full Speed delay time Multi ---- (8'096) - PASS
STEP.446(UUT Test seq.446) : FAN Speed Normal_Multi ---- (0'093) ---------- PASS
(The Report Format of this Sequence was not found)
STEP.447(UUT Test seq.447) : Turn On Timing Test_Multi or Single(200Vdc_HH) PASS
ElaspedTime (S)= 1'903
Vin (V)= 200.00
Fin (Hz)= 30.00
On Phase Delay(ms)= 90.00
UUT Off Time (s)= 0.00
Trigger: 1:TTL1R, 2:TTL2R, 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:TTL1F, 9:TTL2F,10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1.00
2 1.00
3 1.00
4 1.00
Load Loading Start End VcmpA VcmpB
Name (A/Ohm/V) Trigger Trigger (V) (V)
------------- ---------- ------- ------- ------- -------
12V 145.100 8 5 11.590 12.810
12Vsb 2.500 8 5 11.400 12.600
PWOK 0.000 8 5 2.600 3.460
Vin_Good 0.000 8 1 2.600 3.460
SMBAlert 0.000 8 1 2.600 3.460
Load Ton Ton Ton
Name Max Min (ms)
------------- -------- -------- ---------
12V 3000.00 1.00 1158.44
12Vsb 1500.00 1.00 912.87
PWOK ******** ******** 1364.02
Vin_Good ******** ******** 0.06
SMBAlert ******** ******** 0.06
Load Ref Load Td Td Td
Name No. Max Min (ms)
------------- ------------- -------- -------- ---------
12V 3 -500.00 -100.00 -205.58
12Vsb 1 -1500.00 -50.00 -245.57
PWOK 1 500.00 100.00 205.58
Vin_Good 0 ******** ******** 0.06
SMBAlert 0 ******** ******** 0.06
STEP.448(UUT Test seq.448) : I2C Read Status Multi_S6(200Vdc_HH) ---- (0'10 PASS
Adderss :B0
Command Page00 :060200
Command Page01 :060201
Status Word :79
Status Byte :78
Status VOUT :7A
Status IOUT :7B
Status INPUT :7C
Status TEMPERATURE :7D
Status CML :7E
Status FANS :81
---------------------------------
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
----------------------------------
Word_Page_00 : 0
Word_Page_01 : 0
Status_Byte_P00 : 0
Status_Byte_P01 : 0
Status_VOUT_P00 : 0
Status_VOUT_P01 : 0
Status_IOUT_P00 : 0
Status_IOUT_P01 : 0
Status_INPUT_P00 : 0
Status_INPUT_P01 : 0
Status_TEM_P00 : 0
Status_TEM_P01 : 0
Status_CML_P00 : 0
Status_CML_P01 : 0
Status_FANS_P00 : 0
Status_FANS_P01 : 0
STEP.449(UUT Test seq.449) : PS OFF Time 80611(200Vdc_HH) ---- (1'544) ---- PASS
Vin (V)= Refer to the previous item
Fin (Hz)= Refer to the previous item
On Phase Delay(ms)= Refer to the previous item
UUT Off Time (s)= Refer to the previous item
Loading (A/Ohm/V)= Refer to the previous item
Trigger: 1:Trig1R(AC), 2:Trig2R(PS on), 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:Trig1F(AC), 9:Trig2F(PS on),10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1
2 1
3 1
4 1
Load Start End VcmpA VcmpB
Name Trigger Trigger (V) (V)
------------- ------- ------- ------- -------
12V 2 12 11.590 12.810
12Vsb 2 2 11.400 12.600
PWOK 2 12 2.600 2.600
Vin_Good 2 2 2.600 2.600
SMBAlert 2 2 2.600 2.600
Load Ton Ton Ton
Name Max Min (ms)
------------- -------- -------- ---------
12V ******** ******** 2.28
12Vsb ******** ******** --------
PWOK 50.00 0.01 0.62
Vin_Good ******** ******** --------
SMBAlert ******** ******** --------
Load Ref Load Td Td Td
Name No. Max Min (ms)
------------- ---------- -------- -------- ---------
12V 3 100.00 1.00 1.65
12Vsb 0 ******** ******** --------
PWOK 1 -100.00 -1.00 -1.65
Vin_Good 0 ******** ******** --------
SMBAlert 0 ******** ******** --------
STEP.450(UUT Test seq.450) : PS ON Delay time 80611(200Vdc_HH) ---- (0'873) PASS
Vin (V)= Refer to the previous item
Fin (Hz)= Refer to the previous item
On Phase Delay(ms)= Refer to the previous item
UUT Off Time (s)= Refer to the previous item
Loading (A/Ohm/V)= Refer to the previous item
Trigger: 1:Trig1R(AC), 2:Trig2R(PS on), 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:Trig1F(AC), 9:Trig2F(PS on),10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1
2 1
3 1
4 1
Load Start End VcmpA VcmpB
Name Trigger Trigger (V) (V)
------------- ------- ------- ------- -------
12V 9 5 11.590 12.810
12Vsb 9 9 11.400 12.600
PWOK 9 5 2.600 2.600
Vin_Good 9 9 2.600 2.600
SMBAlert 9 9 2.600 2.600
Load Ton Ton Ton
Name Max Min (ms)
------------- -------- -------- ---------
12V 400.00 5.00 62.70
12Vsb ******** ******** 0.05
PWOK ******** ******** 268.13
Vin_Good ******** ******** 0.05
SMBAlert ******** ******** 0.05
Load Ref Load Td Td Td
Name No. Max Min (ms)
------------- ---------- -------- -------- ---------
12V 3 -500.000 -100.000 -205.430
12Vsb 0 ********* ********* 0.049
PWOK 1 500.000 100.000 205.430
Vin_Good 0 ********* ********* 0.049
SMBAlert 0 ********* ********* 0.049
STEP.451(UUT Test seq.451) : Turn On Timing Test_Multi or Single(200Vdc_HH_ PASS
ElaspedTime (S)= 2'043
Vin (V)= 200.00
Fin (Hz)= 30.00
On Phase Delay(ms)= 90.00
UUT Off Time (s)= 0.50
Trigger: 1:TTL1R, 2:TTL2R, 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:TTL1F, 9:TTL2F,10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1.00
2 1.00
3 1.00
4 1.00
Load Loading Start End VcmpA VcmpB
Name (A/Ohm/V) Trigger Trigger (V) (V)
------------- ---------- ------- ------- ------- -------
12V 145.100 5 6 1.220 11.590
12Vsb 2.500 5 6 1.200 10.800
PWOK 0.000 8 1 2.600 3.460
Vin_Good 0.000 8 1 2.600 3.460
SMBAlert 0.000 8 1 2.600 3.460
Load Ton Ton Ton
Name Max Min (ms)
------------- -------- -------- ---------
12V 70.00 5.00 51.28
12Vsb 70.00 1.00 11.70
PWOK ******** ******** 0.06
Vin_Good ******** ******** 0.06
SMBAlert ******** ******** 0.06
Load Ref Load Td Td Td
Name No. Max Min (ms)
------------- ------------- -------- -------- ---------
12V 0 ******** ******** 51.28
12Vsb 0 ******** ******** 11.70
PWOK 0 ******** ******** 0.06
Vin_Good 0 ******** ******** 0.06
SMBAlert 0 ******** ******** 0.06
STEP.452(UUT Test seq.452) : TTL & Relay Setup ---- (0'000) --------------- PASS
(The Report Format of this Sequence was not found)
STEP.453(UUT Test seq.453) : PS ON Delay time 80611(200Vdc_HH_Tpson_12V_Ris PASS
Vin (V)= Refer to the previous item
Fin (Hz)= Refer to the previous item
On Phase Delay(ms)= Refer to the previous item
UUT Off Time (s)= Refer to the previous item
Loading (A/Ohm/V)= Refer to the previous item
Trigger: 1:Trig1R(AC), 2:Trig2R(PS on), 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:Trig1F(AC), 9:Trig2F(PS on),10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1
2 1
3 1
4 1
Load Start End VcmpA VcmpB
Name Trigger Trigger (V) (V)
------------- ------- ------- ------- -------
12V 5 6 1.220 11.590
12Vsb 9 9 1.200 10.800
PWOK 9 9 2.600 2.600
Vin_Good 9 9 2.600 2.600
SMBAlert 9 9 2.600 2.600
Load Ton Ton Ton
Name Max Min (ms)
------------- -------- -------- ---------
12V 70.00 5.00 51.24
12Vsb ******** ******** 0.05
PWOK ******** ******** 0.05
Vin_Good ******** ******** 0.05
SMBAlert ******** ******** 0.05
Load Ref Load Td Td Td
Name No. Max Min (ms)
------------- ---------- -------- -------- ---------
12V 0 ********* ********* 51.245
12Vsb 0 ********* ********* 0.047
PWOK 0 ********* ********* 0.047
Vin_Good 0 ********* ********* 0.047
SMBAlert 0 ********* ********* 0.047
STEP.454(UUT Test seq.454) : Input Output Eff Noise Multi or Single(200Vdc_ PASS
ElapsedTime (S)= 1'607
Vin (V)= 200.00
Fin (Hz)= 30.00
Delay Time (ms)= 300.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 145.100 ******* ******* 145.097
12Vsb 0.100 ******* ******* 0.100
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
-------Load---------------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V ???.??? ???.??? ???.???
12Vsb ???.??? ???.??? ???.???
PWOK ???.??? ???.??? ???.???
Vin_Good ???.??? ???.??? ???.???
SMBAlert ???.??? ???.??? ???.???
--------34970----------------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 12.810 11.590 12.174
12VSb 12.600 11.400 12.127
PWOK 3.460 2.500 3.225
Vin_Good 3.460 2.500 3.231
SMBAlert 3.460 2.500 3.220
IBUS ******* ******* 7.175
CR 0.400 ******* -0.018
Max Min Reading
------------- ---------- ---------- ----------
Vrms (V) ******** ******** 199.3779
PF 1.0000 ******** 1.0000
THDi (%) ******** * 310.0141
Irms (A) ******** ******** 9.8077
Pin (W) ******** ******** XXXXXXXX
Pout (W) ******** ******** XXXXXXXX
Eff (%) ******** ******** 90.3981
Load Noise Range Noise B.W
Name (V) (MHz)
------------- ----------- ---------
12V 2 20.000
12Vsb 2 20.000
PWOK 2 20.000
Vin_Good 2 20.000
SMBAlert 2 20.000
Load Vpp Noise Vpp Noise Vpp Noise
Name Max(mV) Min(mV) (mV)
------------- ------------ ------------ ------------
12V 120.000 0.000 15.540
12Vsb 120.000 0.000 7.110
PWOK ********* ********* 25.760
Vin_Good ********* ********* 23.780
SMBAlert ********* ********* 28.220
STEP.455(UUT Test seq.455) : Static ACDC 34970_or_Load_Multi or Single(200V PASS
ElapsedTime (S)= 1'264
Vin (V)= 200.00
Fin (Hz)= 30.00
Delay Time (ms)= 500.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 145.100 ******* ******* 145.097
12Vsb 2.750 ******* ******* 2.750
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 12.810 11.590 12.176
12VSb 12.600 11.400 11.986
PWOK 3.460 2.500 3.228
Vin_Good 3.460 2.500 3.226
SMBAlert 3.460 2.500 3.221
IBUS ******* ******* 7.175
CR 0.400 ******* -0.019
Max Min Reading
------------- --------- --------- ---------
Pout (W) ******* ******* XXXXXXX
STEP.456(UUT Test seq.456) : Static ACDC 34970_or_Load_Multi or Single(200V PASS
ElapsedTime (S)= 1'466
Vin (V)= 200.00
Fin (Hz)= 30.00
Delay Time (ms)= 500.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 145.100 ******* ******* 0.000
12Vsb 3.650 ******* ******* 0.010
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 0.400 ******* 0.001
12VSb 12.600 ******* 11.977
PWOK 0.400 ******* 0.039
Vin_Good 3.460 2.400 3.240
SMBAlert 3.460 ******* 3.219
IBUS ******* ******* 0.154
CR 0.400 ******* 0.004
Max Min Reading
------------- --------- --------- ---------
Pout (W) ******* ******* 0.118
STEP.457(UUT Test seq.457) : Static ACDC 34970_or_Load_Multi or Single(200V PASS
ElapsedTime (S)= 1'919
Vin (V)= 200.00
Fin (Hz)= 30.00
Delay Time (ms)= 1000.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 145.100 ******* ******* 145.097
12Vsb 2.750 ******* ******* 2.750
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 12.810 11.590 12.172
12VSb 12.600 11.400 11.989
PWOK 3.460 2.500 3.228
Vin_Good 3.460 2.500 3.225
SMBAlert 3.460 2.500 3.223
IBUS ******* ******* 7.176
CR 0.400 ******* -0.019
Max Min Reading
------------- --------- --------- ---------
Pout (W) ******* ******* XXXXXXX
STEP.458(UUT Test seq.458) : Cold Redundant Master Multi _S2 ---- (0'093) - PASS
(The Report Format of this Sequence was not found)
STEP.459(UUT Test seq.459) : Static ACDC 34970_or_Load_Multi or Single(200V PASS
ElapsedTime (S)= 1'279
Vin (V)= 200.00
Fin (Hz)= 30.00
Delay Time (ms)= 500.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 145.100 ******* ******* 145.097
12Vsb 2.500 ******* ******* 2.500
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 12.810 11.590 12.176
12VSb 12.600 11.400 11.997
PWOK 3.460 2.500 3.223
Vin_Good 3.460 2.500 3.219
SMBAlert 3.460 2.500 3.226
IBUS ******* ******* 7.174
CR 3.460 2.500 3.168
Max Min Reading
------------- --------- --------- ---------
Pout (W) ******* ******* XXXXXXX
STEP.460(UUT Test seq.460) : Disable Cold Redundant Master Multi_S2 ---- (0 PASS
(The Report Format of this Sequence was not found)
STEP.461(UUT Test seq.461) : Static ACDC 34970_or_Load_Multi or Single(200V PASS
ElapsedTime (S)= 1'248
Vin (V)= 200.00
Fin (Hz)= 30.00
Delay Time (ms)= 500.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 145.100 ******* ******* 145.097
12Vsb 2.500 ******* ******* 2.500
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 12.810 11.590 12.176
12VSb 12.600 11.400 11.997
PWOK 3.460 2.500 3.229
Vin_Good 3.460 2.500 3.223
SMBAlert 3.460 2.500 3.224
IBUS ******* ******* 7.176
CR 0.400 ******* -0.019
Max Min Reading
------------- --------- --------- ---------
Pout (W) ******* ******* XXXXXXX
STEP.462(UUT Test seq.462) : Input Output Eff Noise Multi or Single(200Vdc_ PASS
ElapsedTime (S)= 1'560
Vin (V)= 200.00
Fin (Hz)= 30.00
Delay Time (ms)= 300.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 145.100 ******* ******* 145.097
12Vsb 2.500 ******* ******* 2.500
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
-------Load---------------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V ???.??? ???.??? ???.???
12Vsb ???.??? ???.??? ???.???
PWOK ???.??? ???.??? ???.???
Vin_Good ???.??? ???.??? ???.???
SMBAlert ???.??? ???.??? ???.???
--------34970----------------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 12.810 11.590 12.177
12VSb 12.600 11.400 11.996
PWOK 3.460 2.500 3.227
Vin_Good 3.460 2.500 3.223
SMBAlert 3.460 2.500 3.228
IBUS ******* ******* 7.177
CR 0.400 ******* -0.019
Max Min Reading
------------- ---------- ---------- ----------
Vrms (V) ******** ******** 199.4253
PF 1.0000 ******** 1.0000
THDi (%) ******** * XXXXXXXX
Irms (A) ******** ******** 9.9893
Pin (W) ******** ******** XXXXXXXX
Pout (W) ******** ******** XXXXXXXX
Eff (%) ******** ******** 90.2006
Load Noise Range Noise B.W
Name (V) (MHz)
------------- ----------- ---------
12V 2 20.000
12Vsb 2 20.000
PWOK 2 20.000
Vin_Good 2 20.000
SMBAlert 2 20.000
Load Vpp Noise Vpp Noise Vpp Noise
Name Max(mV) Min(mV) (mV)
------------- ------------ ------------ ------------
12V 120.000 0.000 14.020
12Vsb 120.000 0.000 14.590
PWOK ********* ********* 26.300
Vin_Good ********* ********* 23.930
SMBAlert ********* ********* 28.060
STEP.463(UUT Test seq.463) : Hold Up Timing Test_Multi or Single(200Vdc_70% PASS
ElapsedTime (S)= 0'905
Vin (V)= 200.00
Fin (Hz)= 30.00
Delay Time (ms)= 200.00
On Phase Delay(ms)= 90.00
UUT Off Time (s)= 0.00
Trigger: 1:Trig1R(AC), 2:Trig2R(PS on), 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:Trig1F(AC), 9:Trig2F(PS on),10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1
2 1
3 1
4 1
Load Loading Start End VcmpA VcmpB
Name (A/Ohm/V) Trigger Trigger (V) (V)
------------- ---------- ------- ------- ------- -------
12V 101.570 8 12 11.590 12.810
12Vsb 1.750 8 12 11.400 12.600
PWOK 0.000 8 12 2.600 3.460
Vin_Good 0.000 8 12 2.600 3.460
SMBAlert 0.000 8 1 2.600 3.460
Load Tholdup Tholdup Tholdup
Name Max Min (ms)
------------- -------- -------- ---------
12V 1000.00 10.00 24.11
12Vsb 1000.00 70.00 78.66
PWOK 300.00 9.00 22.43
Vin_Good 4.00 0.01 2.69
SMBAlert ******** ******** 0.06
Load Ref Load Tholdup Tholdup Tholdup
Name No. Max Min (ms)
------------- ---------- -------- -------- ---------
12V 3 100.00 1.00 1.68
12Vsb 0 ******** ******** 78.66
PWOK 1 -100.00 -1.00 -1.68
Vin_Good 0 ******** ******** 2.69
SMBAlert 0 ******** ******** 0.06
STEP.464(UUT Test seq.464) : FAN Full Speed delay time Multi ---- (8'190) - PASS
STEP.465(UUT Test seq.465) : FAN Speed Normal_Multi ---- (0'093) ---------- PASS
(The Report Format of this Sequence was not found)
STEP.466(UUT Test seq.466) : Turn On Timing Test_Multi or Single(220VDC_HH) PASS
ElaspedTime (S)= 1'904
Vin (V)= 220.00
Fin (Hz)= 30.00
On Phase Delay(ms)= 90.00
UUT Off Time (s)= 0.00
Trigger: 1:TTL1R, 2:TTL2R, 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:TTL1F, 9:TTL2F,10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1.00
2 1.00
3 1.00
4 1.00
Load Loading Start End VcmpA VcmpB
Name (A/Ohm/V) Trigger Trigger (V) (V)
------------- ---------- ------- ------- ------- -------
12V 161.500 8 5 11.590 12.810
12Vsb 2.500 8 5 11.400 12.600
PWOK 0.000 8 5 2.600 3.460
Vin_Good 0.000 8 1 2.600 3.460
SMBAlert 0.000 8 1 2.600 3.460
Load Ton Ton Ton
Name Max Min (ms)
------------- -------- -------- ---------
12V 3000.00 1.00 1117.93
12Vsb 1500.00 1.00 872.30
PWOK ******** ******** 1323.34
Vin_Good ******** ******** 0.06
SMBAlert ******** ******** 0.06
Load Ref Load Td Td Td
Name No. Max Min (ms)
------------- ------------- -------- -------- ---------
12V 3 -500.00 -100.00 -205.41
12Vsb 1 -1500.00 -50.00 -245.63
PWOK 1 500.00 100.00 205.41
Vin_Good 0 ******** ******** 0.06
SMBAlert 0 ******** ******** 0.06
STEP.467(UUT Test seq.467) : I2C Read Status Multi_S6(220VDC_HH) ---- (0'10 PASS
Adderss :B0
Command Page00 :060200
Command Page01 :060201
Status Word :79
Status Byte :78
Status VOUT :7A
Status IOUT :7B
Status INPUT :7C
Status TEMPERATURE :7D
Status CML :7E
Status FANS :81
---------------------------------
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
----------------------------------
Word_Page_00 : 0
Word_Page_01 : 0
Status_Byte_P00 : 0
Status_Byte_P01 : 0
Status_VOUT_P00 : 0
Status_VOUT_P01 : 0
Status_IOUT_P00 : 0
Status_IOUT_P01 : 0
Status_INPUT_P00 : 0
Status_INPUT_P01 : 0
Status_TEM_P00 : 0
Status_TEM_P01 : 0
Status_CML_P00 : 0
Status_CML_P01 : 0
Status_FANS_P00 : 0
Status_FANS_P01 : 0
STEP.468(UUT Test seq.468) : PS OFF Time 80611(220VDC_HH) ---- (1'575) ---- PASS
Vin (V)= Refer to the previous item
Fin (Hz)= Refer to the previous item
On Phase Delay(ms)= Refer to the previous item
UUT Off Time (s)= Refer to the previous item
Loading (A/Ohm/V)= Refer to the previous item
Trigger: 1:Trig1R(AC), 2:Trig2R(PS on), 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:Trig1F(AC), 9:Trig2F(PS on),10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1
2 1
3 1
4 1
Load Start End VcmpA VcmpB
Name Trigger Trigger (V) (V)
------------- ------- ------- ------- -------
12V 2 12 11.590 12.810
12Vsb 2 2 11.400 12.600
PWOK 2 12 2.600 2.600
Vin_Good 2 2 2.600 2.600
SMBAlert 2 2 2.600 2.600
Load Ton Ton Ton
Name Max Min (ms)
------------- -------- -------- ---------
12V ******** ******** 2.39
12Vsb ******** ******** --------
PWOK 50.00 0.01 0.74
Vin_Good ******** ******** --------
SMBAlert ******** ******** --------
Load Ref Load Td Td Td
Name No. Max Min (ms)
------------- ---------- -------- -------- ---------
12V 3 100.00 1.00 1.65
12Vsb 0 ******** ******** --------
PWOK 1 -100.00 -1.00 -1.65
Vin_Good 0 ******** ******** --------
SMBAlert 0 ******** ******** --------
STEP.469(UUT Test seq.469) : I2C Read Status Multi_S6(StandBy) ---- (0'124) PASS
Adderss :B0
Command Page00 :060200
Command Page01 :060201
Status Word :79
Status Byte :78
Status VOUT :7A
Status IOUT :7B
Status INPUT :7C
Status TEMPERATURE :7D
Status CML :7E
Status FANS :81
---------------------------------
Word SPEC: 16392
Word SPEC: 16392
Word SPEC: 16392
Word SPEC: 16392
Word SPEC: 16392
Word SPEC: 16392
Word SPEC: 16392
Word SPEC: 16392
Word SPEC_Page1: 16392
Word SPEC_Page1: 16392
Word SPEC_Page1: 16392
Word SPEC_Page1: 16392
Word SPEC_Page1: 16392
Word SPEC_Page1: 16392
Word SPEC_Page1: 16392
Word SPEC_Page1: 16392
Byte SPEC : 64
Byte SPEC : 64
Byte SPEC : 64
Byte SPEC : 64
Byte SPEC : 64
Byte SPEC : 64
Byte SPEC : 64
Byte SPEC : 64
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
----------------------------------
Word_Page_00 : 16392
Word_Page_01 : 16392
Status_Byte_P00 : 64
Status_Byte_P01 : 64
Status_VOUT_P00 : 0
Status_VOUT_P01 : 0
Status_IOUT_P00 : 0
Status_IOUT_P01 : 0
Status_INPUT_P00 : 0
Status_INPUT_P01 : 0
Status_TEM_P00 : 0
Status_TEM_P01 : 0
Status_CML_P00 : 0
Status_CML_P01 : 0
Status_FANS_P00 : 0
Status_FANS_P01 : 0
STEP.470(UUT Test seq.470) : PS ON Delay time 80611(220VDC_HH) ---- (0'858) PASS
Vin (V)= Refer to the previous item
Fin (Hz)= Refer to the previous item
On Phase Delay(ms)= Refer to the previous item
UUT Off Time (s)= Refer to the previous item
Loading (A/Ohm/V)= Refer to the previous item
Trigger: 1:Trig1R(AC), 2:Trig2R(PS on), 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:Trig1F(AC), 9:Trig2F(PS on),10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1
2 1
3 1
4 1
Load Start End VcmpA VcmpB
Name Trigger Trigger (V) (V)
------------- ------- ------- ------- -------
12V 9 5 11.590 12.810
12Vsb 9 9 11.400 12.600
PWOK 9 5 2.600 2.600
Vin_Good 9 9 2.600 2.600
SMBAlert 9 9 2.600 2.600
Load Ton Ton Ton
Name Max Min (ms)
------------- -------- -------- ---------
12V 400.00 5.00 62.79
12Vsb ******** ******** 0.17
PWOK ******** ******** 268.23
Vin_Good ******** ******** 0.17
SMBAlert ******** ******** 0.17
Load Ref Load Td Td Td
Name No. Max Min (ms)
------------- ---------- -------- -------- ---------
12V 3 -500.000 -100.000 -205.435
12Vsb 0 ********* ********* 0.168
PWOK 1 500.000 100.000 205.435
Vin_Good 0 ********* ********* 0.168
SMBAlert 0 ********* ********* 0.168
STEP.471(UUT Test seq.471) : Turn On Timing Test_Multi or Single(220VDC_HH_ PASS
ElaspedTime (S)= 2'043
Vin (V)= 220.00
Fin (Hz)= 30.00
On Phase Delay(ms)= 90.00
UUT Off Time (s)= 0.50
Trigger: 1:TTL1R, 2:TTL2R, 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:TTL1F, 9:TTL2F,10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1.00
2 1.00
3 1.00
4 1.00
Load Loading Start End VcmpA VcmpB
Name (A/Ohm/V) Trigger Trigger (V) (V)
------------- ---------- ------- ------- ------- -------
12V 161.500 5 6 1.220 11.590
12Vsb 2.500 5 6 1.200 10.800
PWOK 0.000 8 1 2.600 3.460
Vin_Good 0.000 8 1 2.600 3.460
SMBAlert 0.000 8 1 2.600 3.460
Load Ton Ton Ton
Name Max Min (ms)
------------- -------- -------- ---------
12V 70.00 5.00 51.24
12Vsb 70.00 1.00 11.68
PWOK ******** ******** 0.06
Vin_Good ******** ******** 0.06
SMBAlert ******** ******** 0.06
Load Ref Load Td Td Td
Name No. Max Min (ms)
------------- ------------- -------- -------- ---------
12V 0 ******** ******** 51.24
12Vsb 0 ******** ******** 11.68
PWOK 0 ******** ******** 0.06
Vin_Good 0 ******** ******** 0.06
SMBAlert 0 ******** ******** 0.06
STEP.472(UUT Test seq.472) : TTL & Relay Setup ---- (0'000) --------------- PASS
(The Report Format of this Sequence was not found)
STEP.473(UUT Test seq.473) : PS ON Delay time 80611(220VDC_HH_Tpson_12V_Ris PASS
Vin (V)= Refer to the previous item
Fin (Hz)= Refer to the previous item
On Phase Delay(ms)= Refer to the previous item
UUT Off Time (s)= Refer to the previous item
Loading (A/Ohm/V)= Refer to the previous item
Trigger: 1:Trig1R(AC), 2:Trig2R(PS on), 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:Trig1F(AC), 9:Trig2F(PS on),10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1
2 1
3 1
4 1
Load Start End VcmpA VcmpB
Name Trigger Trigger (V) (V)
------------- ------- ------- ------- -------
12V 5 6 1.220 11.590
12Vsb 9 9 1.200 10.800
PWOK 9 9 2.600 2.600
Vin_Good 9 9 2.600 2.600
SMBAlert 9 9 2.600 2.600
Load Ton Ton Ton
Name Max Min (ms)
------------- -------- -------- ---------
12V 70.00 5.00 51.23
12Vsb ******** ******** 0.05
PWOK ******** ******** 0.05
Vin_Good ******** ******** 0.05
SMBAlert ******** ******** 0.05
Load Ref Load Td Td Td
Name No. Max Min (ms)
------------- ---------- -------- -------- ---------
12V 0 ********* ********* 51.226
12Vsb 0 ********* ********* 0.052
PWOK 0 ********* ********* 0.052
Vin_Good 0 ********* ********* 0.052
SMBAlert 0 ********* ********* 0.052
STEP.474(UUT Test seq.474) : Input Output Eff Noise Multi or Single(220VDC_ PASS
ElapsedTime (S)= 1'779
Vin (V)= 220.00
Fin (Hz)= 30.00
Delay Time (ms)= 500.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 161.500 ******* ******* 161.497
12Vsb 0.100 ******* ******* 0.100
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
-------Load---------------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V ???.??? ???.??? ???.???
12Vsb ???.??? ???.??? ???.???
PWOK ???.??? ???.??? ???.???
Vin_Good ???.??? ???.??? ???.???
SMBAlert ???.??? ???.??? ???.???
--------34970----------------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 12.810 11.590 12.167
12VSb 12.600 11.400 12.125
PWOK 3.460 2.500 3.228
Vin_Good 3.460 2.500 3.223
SMBAlert 3.460 2.500 3.224
IBUS ******* ******* 8.001
CR 0.400 ******* -0.020
Max Min Reading
------------- ---------- ---------- ----------
Vrms (V) ******** ******** 219.4187
PF 1.0000 ******** 1.0000
THDi (%) ******** * 236.6085
Irms (A) ******** ******** 9.9188
Pin (W) ******** ******** XXXXXXXX
Pout (W) ******** ******** XXXXXXXX
Eff (%) ******** ******** 90.3405
Load Noise Range Noise B.W
Name (V) (MHz)
------------- ----------- ---------
12V 2 20.000
12Vsb 2 20.000
PWOK 2 20.000
Vin_Good 2 20.000
SMBAlert 2 20.000
Load Vpp Noise Vpp Noise Vpp Noise
Name Max(mV) Min(mV) (mV)
------------- ------------ ------------ ------------
12V 120.000 0.000 15.700
12Vsb 120.000 0.000 7.390
PWOK ********* ********* 24.250
Vin_Good ********* ********* 23.070
SMBAlert ********* ********* 27.170
STEP.475(UUT Test seq.475) : Static ACDC 34970_or_Load_Multi or Single(220V PASS
ElapsedTime (S)= 1'248
Vin (V)= 220.00
Fin (Hz)= 30.00
Delay Time (ms)= 500.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 161.500 ******* ******* 161.497
12Vsb 2.750 ******* ******* 2.750
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 12.810 11.590 12.166
12VSb 12.600 11.400 11.983
PWOK 3.460 2.500 3.220
Vin_Good 3.460 2.500 3.225
SMBAlert 3.460 2.500 3.225
IBUS ******* ******* 8.001
CR 0.400 ******* -0.022
Max Min Reading
------------- --------- --------- ---------
Pout (W) ******* ******* XXXXXXX
STEP.476(UUT Test seq.476) : Static ACDC 34970_or_Load_Multi or Single(220V PASS
ElapsedTime (S)= 1'420
Vin (V)= 220.00
Fin (Hz)= 30.00
Delay Time (ms)= 500.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 161.500 ******* ******* 0.000
12Vsb 3.650 ******* ******* 0.013
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 0.400 ******* 0.001
12VSb 12.600 ******* 11.978
PWOK 0.400 ******* 0.038
Vin_Good 3.460 2.400 3.247
SMBAlert 3.460 ******* 3.211
IBUS ******* ******* 0.170
CR 0.400 ******* 0.005
Max Min Reading
------------- --------- --------- ---------
Pout (W) ******* ******* 0.157
STEP.477(UUT Test seq.477) : Static ACDC 34970_or_Load_Multi or Single(220V PASS
ElapsedTime (S)= 1'935
Vin (V)= 220.00
Fin (Hz)= 30.00
Delay Time (ms)= 1000.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 161.500 ******* ******* 161.497
12Vsb 2.750 ******* ******* 2.750
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 12.810 11.590 12.160
12VSb 12.600 11.400 11.988
PWOK 3.460 2.500 3.224
Vin_Good 3.460 2.500 3.227
SMBAlert 3.460 2.500 3.220
IBUS ******* ******* 8.001
CR 0.400 ******* -0.022
Max Min Reading
------------- --------- --------- ---------
Pout (W) ******* ******* XXXXXXX
STEP.478(UUT Test seq.478) : Cold Redundant Master Multi _S2 ---- (0'094) - PASS
(The Report Format of this Sequence was not found)
STEP.479(UUT Test seq.479) : Static ACDC 34970_or_Load_Multi or Single(220V PASS
ElapsedTime (S)= 1'295
Vin (V)= 220.00
Fin (Hz)= 30.00
Delay Time (ms)= 500.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 161.500 ******* ******* 161.497
12Vsb 2.500 ******* ******* 2.500
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 12.810 11.590 12.168
12VSb 12.600 11.400 11.995
PWOK 3.460 2.500 3.222
Vin_Good 3.460 2.500 3.219
SMBAlert 3.460 2.500 3.223
IBUS ******* ******* 8.001
CR 3.460 2.500 3.166
Max Min Reading
------------- --------- --------- ---------
Pout (W) ******* ******* XXXXXXX
STEP.480(UUT Test seq.480) : Disable Cold Redundant Master Multi_S2 ---- (0 PASS
(The Report Format of this Sequence was not found)
STEP.481(UUT Test seq.481) : Static ACDC 34970_or_Load_Multi or Single(220V PASS
ElapsedTime (S)= 1'248
Vin (V)= 220.00
Fin (Hz)= 30.00
Delay Time (ms)= 500.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 161.500 ******* ******* 161.497
12Vsb 2.500 ******* ******* 2.500
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 12.810 11.590 12.168
12VSb 12.600 11.400 11.995
PWOK 3.460 2.500 3.223
Vin_Good 3.460 2.500 3.221
SMBAlert 3.460 2.500 3.228
IBUS ******* ******* 8.002
CR 0.400 ******* -0.022
Max Min Reading
------------- --------- --------- ---------
Pout (W) ******* ******* XXXXXXX
STEP.482(UUT Test seq.482) : Input Output Eff Noise Multi or Single(220VDC_ PASS
ElapsedTime (S)= 1'794
Vin (V)= 220.00
Fin (Hz)= 30.00
Delay Time (ms)= 500.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 161.500 ******* ******* 161.497
12Vsb 2.500 ******* ******* 2.500
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
-------Load---------------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V ???.??? ???.??? ???.???
12Vsb ???.??? ???.??? ???.???
PWOK ???.??? ???.??? ???.???
Vin_Good ???.??? ???.??? ???.???
SMBAlert ???.??? ???.??? ???.???
--------34970----------------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 12.810 11.590 12.167
12VSb 12.600 11.400 11.994
PWOK 3.460 2.500 3.225
Vin_Good 3.460 2.500 3.222
SMBAlert 3.460 2.500 3.224
IBUS ******* ******* 8.003
CR 0.400 ******* -0.022
Max Min Reading
------------- ---------- ---------- ----------
Vrms (V) ******** ******** 219.4211
PF 1.0000 ******** 1.0000
THDi (%) ******** * XXXXXXXX
Irms (A) ******** ******** 10.0923
Pin (W) ******** ******** XXXXXXXX
Pout (W) ******** ******** XXXXXXXX
Eff (%) ******** ******** 90.0863
Load Noise Range Noise B.W
Name (V) (MHz)
------------- ----------- ---------
12V 2 20.000
12Vsb 2 20.000
PWOK 2 20.000
Vin_Good 2 20.000
SMBAlert 2 20.000
Load Vpp Noise Vpp Noise Vpp Noise
Name Max(mV) Min(mV) (mV)
------------- ------------ ------------ ------------
12V 120.000 0.000 14.400
12Vsb 120.000 0.000 14.990
PWOK ********* ********* 25.600
Vin_Good ********* ********* 23.420
SMBAlert ********* ********* 27.280
STEP.483(UUT Test seq.483) : Hold Up Timing Test_Multi or Single(220VDC_70% PASS
ElapsedTime (S)= 0'921
Vin (V)= 220.00
Fin (Hz)= 30.00
Delay Time (ms)= 200.00
On Phase Delay(ms)= 90.00
UUT Off Time (s)= 0.00
Trigger: 1:Trig1R(AC), 2:Trig2R(PS on), 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:Trig1F(AC), 9:Trig2F(PS on),10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1
2 1
3 1
4 1
Load Loading Start End VcmpA VcmpB
Name (A/Ohm/V) Trigger Trigger (V) (V)
------------- ---------- ------- ------- ------- -------
12V 113.050 8 12 11.590 12.810
12Vsb 1.750 8 12 11.400 12.600
PWOK 0.000 8 12 2.600 3.460
Vin_Good 0.000 8 12 2.600 3.460
SMBAlert 0.000 8 1 2.600 3.460
Load Tholdup Tholdup Tholdup
Name Max Min (ms)
------------- -------- -------- ---------
12V 1000.00 10.00 21.93
12Vsb 1000.00 70.00 78.94
PWOK 300.00 9.00 20.35
Vin_Good 4.00 0.01 2.80
SMBAlert ******** ******** 0.06
Load Ref Load Tholdup Tholdup Tholdup
Name No. Max Min (ms)
------------- ---------- -------- -------- ---------
12V 3 100.00 1.00 1.58
12Vsb 0 ******** ******** 78.94
PWOK 1 -100.00 -1.00 -1.58
Vin_Good 0 ******** ******** 2.80
SMBAlert 0 ******** ******** 0.06
STEP.484(UUT Test seq.484) : FAN Full Speed delay time Multi ---- (8'096) - PASS
STEP.485(UUT Test seq.485) : FAN Speed Normal_Multi ---- (0'093) ---------- PASS
(The Report Format of this Sequence was not found)
STEP.486(UUT Test seq.486) : Turn On Timing Test_Multi or Single(300VDC_LL) PASS
ElaspedTime (S)= 1'763
Vin (V)= 300.00
Fin (Hz)= 30.00
On Phase Delay(ms)= 90.00
UUT Off Time (s)= 0.00
Trigger: 1:TTL1R, 2:TTL2R, 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:TTL1F, 9:TTL2F,10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1.00
2 1.00
3 1.00
4 1.00
Load Loading Start End VcmpA VcmpB
Name (A/Ohm/V) Trigger Trigger (V) (V)
------------- ---------- ------- ------- ------- -------
12V 1.000 8 5 11.590 12.810
12Vsb 0.100 8 5 11.400 12.600
PWOK 0.000 8 5 2.600 3.460
Vin_Good 0.000 8 1 2.600 3.460
SMBAlert 0.000 8 1 2.600 3.460
Load Ton Ton Ton
Name Max Min (ms)
------------- -------- -------- ---------
12V 3000.00 1.00 947.60
12Vsb 1500.00 1.00 703.04
PWOK ******** ******** 1153.45
Vin_Good ******** ******** 0.06
SMBAlert ******** ******** 0.06
Load Ref Load Td Td Td
Name No. Max Min (ms)
------------- ------------- -------- -------- ---------
12V 3 -500.00 -100.00 -205.86
12Vsb 1 -1500.00 -50.00 -244.56
PWOK 1 500.00 100.00 205.86
Vin_Good 0 ******** ******** 0.06
SMBAlert 0 ******** ******** 0.06
STEP.487(UUT Test seq.487) : I2C Read Status Multi_S6(300VDC_LL) ---- (0'10 PASS
Adderss :B0
Command Page00 :060200
Command Page01 :060201
Status Word :79
Status Byte :78
Status VOUT :7A
Status IOUT :7B
Status INPUT :7C
Status TEMPERATURE :7D
Status CML :7E
Status FANS :81
---------------------------------
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
----------------------------------
Word_Page_00 : 0
Word_Page_01 : 0
Status_Byte_P00 : 0
Status_Byte_P01 : 0
Status_VOUT_P00 : 0
Status_VOUT_P01 : 0
Status_IOUT_P00 : 0
Status_IOUT_P01 : 0
Status_INPUT_P00 : 0
Status_INPUT_P01 : 0
Status_TEM_P00 : 0
Status_TEM_P01 : 0
Status_CML_P00 : 0
Status_CML_P01 : 0
Status_FANS_P00 : 0
Status_FANS_P01 : 0
STEP.488(UUT Test seq.488) : PS OFF Time 80611(300VDC_LL) ---- (1'544) ---- PASS
Vin (V)= Refer to the previous item
Fin (Hz)= Refer to the previous item
On Phase Delay(ms)= Refer to the previous item
UUT Off Time (s)= Refer to the previous item
Loading (A/Ohm/V)= Refer to the previous item
Trigger: 1:Trig1R(AC), 2:Trig2R(PS on), 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:Trig1F(AC), 9:Trig2F(PS on),10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1
2 1
3 1
4 1
Load Start End VcmpA VcmpB
Name Trigger Trigger (V) (V)
------------- ------- ------- ------- -------
12V 2 12 11.590 12.810
12Vsb 2 2 11.400 12.600
PWOK 2 12 2.600 2.600
Vin_Good 2 2 2.600 2.600
SMBAlert 2 2 2.600 2.600
Load Ton Ton Ton
Name Max Min (ms)
------------- -------- -------- ---------
12V ******** ******** 5.68
12Vsb ******** ******** --------
PWOK 50.00 0.01 0.71
Vin_Good ******** ******** --------
SMBAlert ******** ******** --------
Load Ref Load Td Td Td
Name No. Max Min (ms)
------------- ---------- -------- -------- ---------
12V 3 100.00 1.00 4.96
12Vsb 0 ******** ******** --------
PWOK 1 -100.00 -1.00 -4.96
Vin_Good 0 ******** ******** --------
SMBAlert 0 ******** ******** --------
STEP.489(UUT Test seq.489) : I2C Read Status Multi_S6(StandBy) ---- (0'125) PASS
Adderss :B0
Command Page00 :060200
Command Page01 :060201
Status Word :79
Status Byte :78
Status VOUT :7A
Status IOUT :7B
Status INPUT :7C
Status TEMPERATURE :7D
Status CML :7E
Status FANS :81
---------------------------------
Word SPEC: 16392
Word SPEC: 16392
Word SPEC: 16392
Word SPEC: 16392
Word SPEC: 16392
Word SPEC: 16392
Word SPEC: 16392
Word SPEC: 16392
Word SPEC_Page1: 16392
Word SPEC_Page1: 16392
Word SPEC_Page1: 16392
Word SPEC_Page1: 16392
Word SPEC_Page1: 16392
Word SPEC_Page1: 16392
Word SPEC_Page1: 16392
Word SPEC_Page1: 16392
Byte SPEC : 64
Byte SPEC : 64
Byte SPEC : 64
Byte SPEC : 64
Byte SPEC : 64
Byte SPEC : 64
Byte SPEC : 64
Byte SPEC : 64
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
----------------------------------
Word_Page_00 : 16392
Word_Page_01 : 16392
Status_Byte_P00 : 64
Status_Byte_P01 : 64
Status_VOUT_P00 : 0
Status_VOUT_P01 : 0
Status_IOUT_P00 : 0
Status_IOUT_P01 : 0
Status_INPUT_P00 : 0
Status_INPUT_P01 : 0
Status_TEM_P00 : 0
Status_TEM_P01 : 0
Status_CML_P00 : 0
Status_CML_P01 : 0
Status_FANS_P00 : 0
Status_FANS_P01 : 0
STEP.490(UUT Test seq.490) : Input Output Eff Noise Multi or Single(No Load PASS
ElapsedTime (S)= 2'028
Vin (V)= 300.00
Fin (Hz)= 30.00
Delay Time (ms)= 500.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 0.000 ******* ******* 0.000
12Vsb 0.000 ******* ******* 0.000
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
-------Load---------------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V ???.??? ???.??? ???.???
12Vsb ???.??? ???.??? ???.???
PWOK ???.??? ???.??? ???.???
Vin_Good ???.??? ???.??? ???.???
SMBAlert ???.??? ???.??? ???.???
--------34970----------------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 0.400 ******* 0.152
12VSb 12.600 11.400 12.189
PWOK 0.400 ******* 0.038
Vin_Good 3.460 2.500 3.247
SMBAlert 3.460 2.500 3.212
IBUS ******* ******* 0.164
CR 0.400 ******* 0.003
Max Min Reading
------------- ---------- ---------- ----------
Vrms (V) ******** ******** 300.3211
PF 1.0000 ******** 0.0000
THDi (%) ******** * XXXXXXXX
Irms (A) ******** ******** 0.0000
Pin (W) ******** ******** 0.0000
Pout (W) ******** ******** 0.0000
Eff (%) ******** ******** 0.0000
Load Noise Range Noise B.W
Name (V) (MHz)
------------- ----------- ---------
12V 2 20.000
12Vsb 2 20.000
PWOK 2 20.000
Vin_Good 2 20.000
SMBAlert 2 20.000
Load Vpp Noise Vpp Noise Vpp Noise
Name Max(mV) Min(mV) (mV)
------------- ------------ ------------ ------------
12V 120.000 0.000 0.890
12Vsb 120.000 0.000 5.140
PWOK ********* ********* 12.960
Vin_Good ********* ********* 19.160
SMBAlert ********* ********* 20.580
STEP.491(UUT Test seq.491) : Input Output Eff Noise Multi or Single(300Vdc_ PASS
ElapsedTime (S)= 1'841
Vin (V)= 300.00
Fin (Hz)= 30.00
Delay Time (ms)= 500.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 1.000 ******* ******* 0.000
12Vsb 2.500 ******* ******* 2.500
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
-------Load---------------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V ???.??? ???.??? ???.???
12Vsb ???.??? ???.??? ???.???
PWOK ???.??? ???.??? ???.???
Vin_Good ???.??? ???.??? ???.???
SMBAlert ???.??? ???.??? ???.???
--------34970----------------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 0.400 ******* 0.001
12VSb 12.600 11.400 12.013
PWOK 0.400 ******* 0.037
Vin_Good 3.460 2.500 3.240
SMBAlert 3.460 2.500 3.219
IBUS ******* ******* 0.299
CR 0.400 ******* 0.001
Max Min Reading
------------- ---------- ---------- ----------
Vrms (V) ******** ******** 300.3096
PF 1.0000 ******** 0.9992
THDi (%) ******** * 264.8223
Irms (A) ******** ******** 0.1364
Pin (W) ******** ******** 40.9324
Pout (W) ******** ******** 30.0297
Eff (%) ******** ******** 73.3643
Load Noise Range Noise B.W
Name (V) (MHz)
------------- ----------- ---------
12V 2 20.000
12Vsb 2 20.000
PWOK 2 20.000
Vin_Good 2 20.000
SMBAlert 2 20.000
Load Vpp Noise Vpp Noise Vpp Noise
Name Max(mV) Min(mV) (mV)
------------- ------------ ------------ ------------
12V 120.000 0.000 0.040
12Vsb 120.000 0.000 2.250
PWOK ********* ********* 16.590
Vin_Good ********* ********* 23.790
SMBAlert ********* ********* 20.950
STEP.492(UUT Test seq.492) : Static ACDC 34970_or_Load_Multi or Single(12Vs PASS
ElapsedTime (S)= 1'263
Vin (V)= 300.00
Fin (Hz)= 30.00
Delay Time (ms)= 500.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 0.000 ******* ******* 0.000
12Vsb 2.750 ******* ******* 2.750
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 0.400 ******* 0.001
12VSb 12.600 11.400 12.009
PWOK 0.400 ******* 0.037
Vin_Good 3.460 2.500 3.239
SMBAlert 3.460 2.500 3.220
IBUS ******* ******* 0.302
CR 0.400 ******* 0.001
Max Min Reading
------------- --------- --------- ---------
Pout (W) ******* ******* 33.023
STEP.493(UUT Test seq.493) : Static ACDC 34970_or_Load_Multi or Single(12Vs PASS
ElapsedTime (S)= 1'341
Vin (V)= 300.00
Fin (Hz)= 30.00
Delay Time (ms)= 500.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 0.000 ******* ******* 0.000
12Vsb 3.650 ******* ******* 0.041
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 0.400 ******* 0.000
12VSb 12.600 ******* 11.970
PWOK 0.400 ******* 0.036
Vin_Good 3.460 2.400 3.240
SMBAlert 3.460 ******* 3.219
IBUS ******* ******* 0.299
CR 0.400 ******* 0.005
Max Min Reading
------------- --------- --------- ---------
Pout (W) ******* ******* 0.490
STEP.494(UUT Test seq.494) : Static ACDC 34970_or_Load_Multi or Single(12Vs PASS
ElapsedTime (S)= 1'825
Vin (V)= 300.00
Fin (Hz)= 30.00
Delay Time (ms)= 1000.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 0.000 ******* ******* 0.000
12Vsb 2.750 ******* ******* 2.750
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 0.400 ******* 0.001
12VSb 12.600 11.400 12.009
PWOK 0.400 ******* 0.037
Vin_Good 3.460 2.500 3.242
SMBAlert 3.460 2.500 3.217
IBUS ******* ******* 0.325
CR 0.400 ******* 0.001
Max Min Reading
------------- --------- --------- ---------
Pout (W) ******* ******* 33.023
STEP.495(UUT Test seq.495) : Input Output Eff Noise Multi or Single(300Vdc_ PASS
ElapsedTime (S)= 1'825
Vin (V)= 300.00
Fin (Hz)= 30.00
Delay Time (ms)= 500.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 1.000 ******* ******* 0.000
12Vsb 0.100 ******* ******* 0.100
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
-------Load---------------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V ???.??? ???.??? ???.???
12Vsb ???.??? ???.??? ???.???
PWOK ???.??? ???.??? ???.???
Vin_Good ???.??? ???.??? ???.???
SMBAlert ???.??? ???.??? ???.???
--------34970----------------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 0.400 ******* 0.000
12VSb 12.600 11.400 12.145
PWOK 0.400 ******* 0.039
Vin_Good 3.460 2.500 3.242
SMBAlert 3.460 2.500 3.218
IBUS ******* ******* 0.313
CR 0.400 ******* 0.003
Max Min Reading
------------- ---------- ---------- ----------
Vrms (V) ******** ******** 300.3184
PF 1.0000 ******** 0.0000
THDi (%) ******** * XXXXXXXX
Irms (A) ******** ******** 0.0000
Pin (W) ******** ******** 0.0000
Pout (W) ******** ******** 1.2167
Eff (%) ******** ******** 0.0000
Load Noise Range Noise B.W
Name (V) (MHz)
------------- ----------- ---------
12V 2 20.000
12Vsb 2 20.000
PWOK 2 20.000
Vin_Good 2 20.000
SMBAlert 2 20.000
Load Vpp Noise Vpp Noise Vpp Noise
Name Max(mV) Min(mV) (mV)
------------- ------------ ------------ ------------
12V 120.000 0.000 0.030
12Vsb 120.000 0.000 8.230
PWOK ********* ********* 13.010
Vin_Good ********* ********* 20.050
SMBAlert ********* ********* 20.410
STEP.496(UUT Test seq.496) : PS ON Delay time 80611(300VDC_LL) ---- (0'983) PASS
Vin (V)= Refer to the previous item
Fin (Hz)= Refer to the previous item
On Phase Delay(ms)= Refer to the previous item
UUT Off Time (s)= Refer to the previous item
Loading (A/Ohm/V)= Refer to the previous item
Trigger: 1:Trig1R(AC), 2:Trig2R(PS on), 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:Trig1F(AC), 9:Trig2F(PS on),10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1
2 1
3 1
4 1
Load Start End VcmpA VcmpB
Name Trigger Trigger (V) (V)
------------- ------- ------- ------- -------
12V 9 5 11.590 12.810
12Vsb 9 9 11.400 12.600
PWOK 9 5 2.600 2.600
Vin_Good 9 9 2.600 2.600
SMBAlert 9 9 2.600 2.600
Load Ton Ton Ton
Name Max Min (ms)
------------- -------- -------- ---------
12V 400.00 5.00 62.18
12Vsb ******** ******** 0.17
PWOK ******** ******** 268.03
Vin_Good ******** ******** 0.17
SMBAlert ******** ******** 0.17
Load Ref Load Td Td Td
Name No. Max Min (ms)
------------- ---------- -------- -------- ---------
12V 3 -500.000 -100.000 -205.844
12Vsb 0 ********* ********* 0.172
PWOK 1 500.000 100.000 205.844
Vin_Good 0 ********* ********* 0.172
SMBAlert 0 ********* ********* 0.172
STEP.497(UUT Test seq.497) : Turn On Timing Test_Multi or Single(300VDC_LL_ PASS
ElaspedTime (S)= 1'747
Vin (V)= 300.00
Fin (Hz)= 30.00
On Phase Delay(ms)= 90.00
UUT Off Time (s)= 0.50
Trigger: 1:TTL1R, 2:TTL2R, 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:TTL1F, 9:TTL2F,10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1.00
2 1.00
3 1.00
4 1.00
Load Loading Start End VcmpA VcmpB
Name (A/Ohm/V) Trigger Trigger (V) (V)
------------- ---------- ------- ------- ------- -------
12V 1.000 5 6 1.220 11.590
12Vsb 0.100 5 6 1.200 10.800
PWOK 0.000 8 1 2.600 3.460
Vin_Good 0.000 8 1 2.600 3.460
SMBAlert 0.000 8 1 2.600 3.460
Load Ton Ton Ton
Name Max Min (ms)
------------- -------- -------- ---------
12V 70.00 5.00 51.32
12Vsb 70.00 1.00 12.51
PWOK ******** ******** 0.06
Vin_Good ******** ******** 0.06
SMBAlert ******** ******** 0.06
Load Ref Load Td Td Td
Name No. Max Min (ms)
------------- ------------- -------- -------- ---------
12V 0 ******** ******** 51.32
12Vsb 0 ******** ******** 12.51
PWOK 0 ******** ******** 0.06
Vin_Good 0 ******** ******** 0.06
SMBAlert 0 ******** ******** 0.06
STEP.498(UUT Test seq.498) : TTL & Relay Setup ---- (0'016) --------------- PASS
(The Report Format of this Sequence was not found)
STEP.499(UUT Test seq.499) : PS ON Delay time 80611(300VDC_LL_Tpson_12V_Ris PASS
Vin (V)= Refer to the previous item
Fin (Hz)= Refer to the previous item
On Phase Delay(ms)= Refer to the previous item
UUT Off Time (s)= Refer to the previous item
Loading (A/Ohm/V)= Refer to the previous item
Trigger: 1:Trig1R(AC), 2:Trig2R(PS on), 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:Trig1F(AC), 9:Trig2F(PS on),10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1
2 1
3 1
4 1
Load Start End VcmpA VcmpB
Name Trigger Trigger (V) (V)
------------- ------- ------- ------- -------
12V 5 6 1.220 11.590
12Vsb 9 9 1.200 10.800
PWOK 9 9 2.600 2.600
Vin_Good 9 9 2.600 2.600
SMBAlert 9 9 2.600 2.600
Load Ton Ton Ton
Name Max Min (ms)
------------- -------- -------- ---------
12V 70.00 5.00 51.26
12Vsb ******** ******** 0.17
PWOK ******** ******** 0.17
Vin_Good ******** ******** 0.17
SMBAlert ******** ******** 0.17
Load Ref Load Td Td Td
Name No. Max Min (ms)
------------- ---------- -------- -------- ---------
12V 0 ********* ********* 51.257
12Vsb 0 ********* ********* 0.171
PWOK 0 ********* ********* 0.171
Vin_Good 0 ********* ********* 0.171
SMBAlert 0 ********* ********* 0.171
STEP.500(UUT Test seq.500) : 12V OVP I2C Multi(OVP_I2C) ---- (0'063) ------ PASS
STEP.501(UUT Test seq.501) : Static ACDC 34970_or_Load_Multi or Single(300V PASS
ElapsedTime (S)= 1'248
Vin (V)= 300.00
Fin (Hz)= 30.00
Delay Time (ms)= 500.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 1.000 ******* ******* 0.000
12Vsb 0.100 ******* ******* 0.100
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 0.400 ******* 0.000
12VSb 12.600 11.400 12.139
PWOK 0.400 ******* 0.039
Vin_Good 3.460 2.500 3.240
SMBAlert 3.460 2.500 3.219
IBUS ******* ******* 0.295
CR 0.400 ******* 0.004
Max Min Reading
------------- --------- --------- ---------
Pout (W) ******* ******* 1.216
STEP.502(UUT Test seq.502) : I2C Read Status OR Multi_S6(12V_OV) ---- (0'10 PASS
Command Page00 :060200
Command Page01 :060201
Status Word :79
Status Byte :78
Status VOUT :7A
Status IOUT :7B
Status INPUT :7C
Status TEMPERATURE :7D
Status CML :7E
Status FANS :81
---------------------------------
Word SPEC: 25224
Word SPEC: 25224
Word SPEC: 25224
Word SPEC: 25224
Word SPEC: 25224
Word SPEC: 25224
Word SPEC: 25224
Word SPEC: 25224
Word SPEC_Page1: 25224
Word SPEC_Page1: 25224
Word SPEC_Page1: 25224
Word SPEC_Page1: 25224
Word SPEC_Page1: 25224
Word SPEC_Page1: 25224
Word SPEC_Page1: 25224
Word SPEC_Page1: 25224
Byte SPEC : 98
Byte SPEC : 98
Byte SPEC : 98
Byte SPEC : 98
Byte SPEC : 98
Byte SPEC : 98
Byte SPEC : 98
Byte SPEC : 98
VOUT SPEC : 192
VOUT SPEC : 192
VOUT SPEC : 192
VOUT SPEC : 192
VOUT SPEC : 192
VOUT SPEC : 192
VOUT SPEC : 192
VOUT SPEC : 192
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
CML SPEC : 128
CML SPEC : 128
CML SPEC : 128
CML SPEC : 128
CML SPEC : 128
CML SPEC : 128
CML SPEC : 128
CML SPEC : 128
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
Word Page0 OR : 0200
Word Page1 OR : 0200
Byte OR : 02
Input OR : 00
IOUT OR : 00
TEMP OR : 00
CML OR : 80
----------------------------------
Word_Page_00 : 25224
Word_Page_01 : 25224
Status_Byte_P00 : 98
Status_Byte_P01 : 98
Status_VOUT_P00 : 192
Status_VOUT_P01 : 192
Status_IOUT_P00 : 0
Status_IOUT_P01 : 0
Status_INPUT_P00 : 0
Status_INPUT_P01 : 0
Status_TEM_P00 : 0
Status_TEM_P01 : 0
Status_CML_P00 : 128
Status_CML_P01 : 128
Status_FANS_P00 : 0
Status_FANS_P01 : 0
STEP.503(UUT Test seq.503) : 12V OVP Disable I2C Multi ---- (0'063) ------- PASS
STEP.504(UUT Test seq.504) : TTL & Relay Setup ---- (0'405) --------------- PASS
(The Report Format of this Sequence was not found)
STEP.505(UUT Test seq.505) : Input Output Eff Noise Multi or Single(No Load PASS
ElapsedTime (S)= 2'527
Vin (V)= 300.00
Fin (Hz)= 30.00
Delay Time (ms)= 1000.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 0.000 ******* ******* 0.000
12Vsb 0.000 ******* ******* 0.000
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
-------Load---------------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V ???.??? ???.??? ???.???
12Vsb ???.??? ???.??? ???.???
PWOK ???.??? ???.??? ???.???
Vin_Good ???.??? ???.??? ???.???
SMBAlert ???.??? ???.??? ???.???
--------34970----------------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 12.810 11.590 12.259
12VSb 12.600 11.400 12.191
PWOK 3.460 2.500 3.248
Vin_Good 3.460 2.500 3.244
SMBAlert 3.460 2.500 3.218
IBUS 0.300 -0.300 0.017
CR 0.400 ******* 0.003
Max Min Reading
------------- ---------- ---------- ----------
Vrms (V) ******** ******** 300.3358
PF 1.0000 ******** 0.0000
THDi (%) ******** * XXXXXXXX
Irms (A) ******** ******** 0.0000
Pin (W) ******** ******** 0.0000
Pout (W) ******** ******** 0.0000
Eff (%) ******** ******** 0.0000
Load Noise Range Noise B.W
Name (V) (MHz)
------------- ----------- ---------
12V 2 20.000
12Vsb 2 20.000
PWOK 2 20.000
Vin_Good 2 20.000
SMBAlert 2 20.000
Load Vpp Noise Vpp Noise Vpp Noise
Name Max(mV) Min(mV) (mV)
------------- ------------ ------------ ------------
12V 120.000 0.000 9.270
12Vsb 120.000 0.000 5.740
PWOK ********* ********* 18.220
Vin_Good ********* ********* 17.930
SMBAlert ********* ********* 20.450
STEP.506(UUT Test seq.506) : Static ACDC 34970_or_Load_Multi or Single(12Vs PASS
ElapsedTime (S)= 1'248
Vin (V)= 300.00
Fin (Hz)= 30.00
Delay Time (ms)= 500.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 1.000 ******* ******* 0.998
12Vsb 2.750 ******* ******* 2.750
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 12.810 11.590 12.261
12VSb 12.600 11.400 12.004
PWOK 3.460 2.500 3.244
Vin_Good 3.460 2.500 3.246
SMBAlert 3.460 2.500 3.217
IBUS ******* ******* 0.059
CR 0.400 ******* 0.001
Max Min Reading
------------- --------- --------- ---------
Pout (W) ******* ******* 45.241
STEP.507(UUT Test seq.507) : Static ACDC 34970_or_Load_Multi or Single(12Vs PASS
ElapsedTime (S)= 1'388
Vin (V)= 300.00
Fin (Hz)= 30.00
Delay Time (ms)= 500.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 1.000 ******* ******* 0.000
12Vsb 3.650 ******* ******* 0.013
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 0.400 ******* 0.001
12VSb 12.600 ******* 11.978
PWOK 0.400 ******* 0.039
Vin_Good 3.460 2.400 3.245
SMBAlert 3.460 ******* 3.213
IBUS ******* ******* 0.112
CR 0.400 ******* 0.005
Max Min Reading
------------- --------- --------- ---------
Pout (W) ******* ******* 0.151
STEP.508(UUT Test seq.508) : Static ACDC 34970_or_Load_Multi or Single(12Vs PASS
ElapsedTime (S)= 1'935
Vin (V)= 300.00
Fin (Hz)= 30.00
Delay Time (ms)= 1000.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 1.000 ******* ******* 0.998
12Vsb 2.750 ******* ******* 2.750
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 12.810 11.590 12.259
12VSb 12.600 11.400 12.008
PWOK 3.460 2.500 3.247
Vin_Good 3.460 2.500 3.250
SMBAlert 3.460 2.500 3.211
IBUS ******* ******* 0.062
CR 0.400 ******* 0.002
Max Min Reading
------------- --------- --------- ---------
Pout (W) ******* ******* 45.251
STEP.509(UUT Test seq.509) : Input Output Eff Noise Multi or Single(300VDC_ PASS
ElapsedTime (S)= 2'121
Vin (V)= 300.00
Fin (Hz)= 30.00
Delay Time (ms)= 800.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 1.000 ******* ******* 0.998
12Vsb 0.100 ******* ******* 0.100
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
-------Load---------------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V ???.??? ???.??? ???.???
12Vsb ???.??? ???.??? ???.???
PWOK ???.??? ???.??? ???.???
Vin_Good ???.??? ???.??? ???.???
SMBAlert ???.??? ???.??? ???.???
--------34970----------------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 12.810 11.590 12.260
12VSb 12.600 11.400 12.142
PWOK 3.460 2.500 3.247
Vin_Good 3.460 2.500 3.246
SMBAlert 3.460 2.500 3.218
IBUS ******* ******* 0.062
CR 0.400 ******* 0.003
Max Min Reading
------------- ---------- ---------- ----------
Vrms (V) ******** ******** 300.3283
PF 1.0000 ******** 0.0000
THDi (%) ******** * 299.6263
Irms (A) ******** ******** 0.0000
Pin (W) ******** ******** 0.0000
Pout (W) ******** ******** 13.4502
Eff (%) ******** ******** 0.0000
Load Noise Range Noise B.W
Name (V) (MHz)
------------- ----------- ---------
12V 2 20.000
12Vsb 2 20.000
PWOK 2 20.000
Vin_Good 2 20.000
SMBAlert 2 20.000
Load Vpp Noise Vpp Noise Vpp Noise
Name Max(mV) Min(mV) (mV)
------------- ------------ ------------ ------------
12V 120.000 0.000 8.700
12Vsb 120.000 0.000 7.790
PWOK ********* ********* 17.740
Vin_Good ********* ********* 17.550
SMBAlert ********* ********* 20.160
STEP.510(UUT Test seq.510) : Input Output Eff Noise Multi or Single(300VDC_ PASS
ElapsedTime (S)= 2'043
Vin (V)= 300.00
Fin (Hz)= 30.00
Delay Time (ms)= 800.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 1.000 ******* ******* 0.998
12Vsb 2.500 ******* ******* 2.500
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
-------Load---------------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V ???.??? ???.??? ???.???
12Vsb ???.??? ???.??? ???.???
PWOK ???.??? ???.??? ???.???
Vin_Good ???.??? ???.??? ???.???
SMBAlert ???.??? ???.??? ???.???
--------34970----------------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 12.810 11.590 12.261
12VSb 12.600 11.400 12.014
PWOK 3.460 2.500 3.248
Vin_Good 3.460 2.500 3.244
SMBAlert 3.460 2.500 3.219
IBUS ******* ******* 0.061
CR 0.400 ******* 0.002
Max Min Reading
------------- ---------- ---------- ----------
Vrms (V) ******** ******** 300.3155
PF 1.0000 ******** 0.9994
THDi (%) ******** * 407.5441
Irms (A) ******** ******** 0.1874
Pin (W) ******** ******** 56.2388
Pout (W) ******** ******** 42.2645
Eff (%) ******** ******** 75.1519
Load Noise Range Noise B.W
Name (V) (MHz)
------------- ----------- ---------
12V 2 20.000
12Vsb 2 20.000
PWOK 2 20.000
Vin_Good 2 20.000
SMBAlert 2 20.000
Load Vpp Noise Vpp Noise Vpp Noise
Name Max(mV) Min(mV) (mV)
------------- ------------ ------------ ------------
12V 120.000 0.000 5.690
12Vsb 120.000 0.000 2.930
PWOK ********* ********* 18.040
Vin_Good ********* ********* 18.100
SMBAlert ********* ********* 19.710
STEP.511(UUT Test seq.511) : Cold Redundant Master Multi _S2 ---- (0'110) - PASS
(The Report Format of this Sequence was not found)
STEP.512(UUT Test seq.512) : Static ACDC 34970_or_Load_Multi or Single(300V PASS
ElapsedTime (S)= 1'294
Vin (V)= 300.00
Fin (Hz)= 30.00
Delay Time (ms)= 500.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 1.000 ******* ******* 0.998
12Vsb 0.100 ******* ******* 0.100
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 12.810 11.590 12.262
12VSb 12.600 11.400 12.145
PWOK 3.460 2.500 3.243
Vin_Good 3.460 2.500 3.246
SMBAlert 3.460 2.500 3.212
IBUS ******* ******* 0.061
CR 3.460 2.500 3.190
Max Min Reading
------------- --------- --------- ---------
Pout (W) ******* ******* 13.450
STEP.513(UUT Test seq.513) : Disable Cold Redundant Master Multi_S2 ---- (0 PASS
(The Report Format of this Sequence was not found)
STEP.514(UUT Test seq.514) : Static ACDC 34970_or_Load_Multi or Single(300V PASS
ElapsedTime (S)= 1'232
Vin (V)= 300.00
Fin (Hz)= 30.00
Delay Time (ms)= 500.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 1.000 ******* ******* 0.998
12Vsb 0.100 ******* ******* 0.100
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 12.810 11.590 12.261
12VSb 12.600 11.400 12.139
PWOK 3.460 2.500 3.245
Vin_Good 3.460 2.500 3.249
SMBAlert 3.460 2.500 3.216
IBUS ******* ******* 0.061
CR 0.400 ******* 0.003
Max Min Reading
------------- --------- --------- ---------
Pout (W) ******* ******* 13.449
STEP.515(UUT Test seq.515) : Hold Up Timing Test_Multi or Single(300VDC_LL) PASS
ElapsedTime (S)= 0'718
Vin (V)= 300.00
Fin (Hz)= 30.00
Delay Time (ms)= 0.00
On Phase Delay(ms)= 90.00
UUT Off Time (s)= 0.00
Trigger: 1:Trig1R(AC), 2:Trig2R(PS on), 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:Trig1F(AC), 9:Trig2F(PS on),10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1
2 1
3 1
4 1
Load Loading Start End VcmpA VcmpB
Name (A/Ohm/V) Trigger Trigger (V) (V)
------------- ---------- ------- ------- ------- -------
12V 1.000 8 12 11.590 12.810
12Vsb 0.100 8 12 11.400 12.600
PWOK 0.000 8 12 2.600 3.460
Vin_Good 0.000 8 12 2.600 3.460
SMBAlert 0.000 8 1 2.600 3.460
Load Tholdup Tholdup Tholdup
Name Max Min (ms)
------------- -------- -------- ---------
12V 1000.00 10.00 47.56
12Vsb 1000.00 70.00 92.14
PWOK 300.00 9.00 42.84
Vin_Good 4.00 0.01 2.78
SMBAlert ******** ******** 0.06
Load Ref Load Tholdup Tholdup Tholdup
Name No. Max Min (ms)
------------- ---------- -------- -------- ---------
12V 3 300.00 1.00 4.72
12Vsb 0 ******** ******** 92.14
PWOK 1 -300.00 -1.00 -4.72
Vin_Good 0 ******** ******** 2.78
SMBAlert 0 ******** ******** 0.06
STEP.516(UUT Test seq.516) : FAN Full Speed delay time Multi ---- (8'096) - PASS
STEP.517(UUT Test seq.517) : FAN Speed Normal_Multi ---- (0'078) ---------- PASS
(The Report Format of this Sequence was not found)
STEP.518(UUT Test seq.518) : 61512 Ac Source ACDC Mode_Multi_S2(300VDC_HH) PASS
(The Report Format of this Sequence was not found)
STEP.519(UUT Test seq.519) : Turn On Timing Test_Multi or Single(300VDC_HH) PASS
ElaspedTime (S)= 1'795
Vin (V)= 300.00
Fin (Hz)= 30.00
On Phase Delay(ms)= 90.00
UUT Off Time (s)= 0.00
Trigger: 1:TTL1R, 2:TTL2R, 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:TTL1F, 9:TTL2F,10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1.00
2 1.00
3 1.00
4 1.00
Load Loading Start End VcmpA VcmpB
Name (A/Ohm/V) Trigger Trigger (V) (V)
------------- ---------- ------- ------- ------- -------
12V 161.500 8 5 11.590 12.810
12Vsb 2.500 8 5 11.400 12.600
PWOK 0.000 8 5 2.600 3.460
Vin_Good 0.000 8 1 2.600 3.460
SMBAlert 0.000 8 1 2.600 3.460
Load Ton Ton Ton
Name Max Min (ms)
------------- -------- -------- ---------
12V 3000.00 1.00 952.16
12Vsb 1500.00 1.00 706.50
PWOK ******** ******** 1157.70
Vin_Good ******** ******** 0.06
SMBAlert ******** ******** 0.06
Load Ref Load Td Td Td
Name No. Max Min (ms)
------------- ------------- -------- -------- ---------
12V 3 -500.00 -100.00 -205.54
12Vsb 1 -1500.00 -50.00 -245.67
PWOK 1 500.00 100.00 205.54
Vin_Good 0 ******** ******** 0.06
SMBAlert 0 ******** ******** 0.06
STEP.520(UUT Test seq.520) : I2C Read Status Multi_S6(300VDC_HH) ---- (0'12 PASS
Adderss :B0
Command Page00 :060200
Command Page01 :060201
Status Word :79
Status Byte :78
Status VOUT :7A
Status IOUT :7B
Status INPUT :7C
Status TEMPERATURE :7D
Status CML :7E
Status FANS :81
---------------------------------
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
----------------------------------
Word_Page_00 : 0
Word_Page_01 : 0
Status_Byte_P00 : 0
Status_Byte_P01 : 0
Status_VOUT_P00 : 0
Status_VOUT_P01 : 0
Status_IOUT_P00 : 0
Status_IOUT_P01 : 0
Status_INPUT_P00 : 0
Status_INPUT_P01 : 0
Status_TEM_P00 : 0
Status_TEM_P01 : 0
Status_CML_P00 : 0
Status_CML_P01 : 0
Status_FANS_P00 : 0
Status_FANS_P01 : 0
STEP.521(UUT Test seq.521) : PS OFF Time 80611(300VDC_HH) ---- (1'653) ---- PASS
Vin (V)= Refer to the previous item
Fin (Hz)= Refer to the previous item
On Phase Delay(ms)= Refer to the previous item
UUT Off Time (s)= Refer to the previous item
Loading (A/Ohm/V)= Refer to the previous item
Trigger: 1:Trig1R(AC), 2:Trig2R(PS on), 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:Trig1F(AC), 9:Trig2F(PS on),10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1
2 1
3 1
4 1
Load Start End VcmpA VcmpB
Name Trigger Trigger (V) (V)
------------- ------- ------- ------- -------
12V 2 12 11.590 12.810
12Vsb 2 2 11.400 12.600
PWOK 2 12 2.600 2.600
Vin_Good 2 2 2.600 2.600
SMBAlert 2 2 2.600 2.600
Load Ton Ton Ton
Name Max Min (ms)
------------- -------- -------- ---------
12V ******** ******** 2.38
12Vsb ******** ******** --------
PWOK 50.00 0.01 0.73
Vin_Good ******** ******** --------
SMBAlert ******** ******** --------
Load Ref Load Td Td Td
Name No. Max Min (ms)
------------- ---------- -------- -------- ---------
12V 3 100.00 1.00 1.65
12Vsb 0 ******** ******** --------
PWOK 1 -100.00 -1.00 -1.65
Vin_Good 0 ******** ******** --------
SMBAlert 0 ******** ******** --------
STEP.522(UUT Test seq.522) : I2C Read Status Multi_S6(StandBy) ---- (0'109) PASS
Adderss :B0
Command Page00 :060200
Command Page01 :060201
Status Word :79
Status Byte :78
Status VOUT :7A
Status IOUT :7B
Status INPUT :7C
Status TEMPERATURE :7D
Status CML :7E
Status FANS :81
---------------------------------
Word SPEC: 16392
Word SPEC: 16392
Word SPEC: 16392
Word SPEC: 16392
Word SPEC: 16392
Word SPEC: 16392
Word SPEC: 16392
Word SPEC: 16392
Word SPEC_Page1: 16392
Word SPEC_Page1: 16392
Word SPEC_Page1: 16392
Word SPEC_Page1: 16392
Word SPEC_Page1: 16392
Word SPEC_Page1: 16392
Word SPEC_Page1: 16392
Word SPEC_Page1: 16392
Byte SPEC : 64
Byte SPEC : 64
Byte SPEC : 64
Byte SPEC : 64
Byte SPEC : 64
Byte SPEC : 64
Byte SPEC : 64
Byte SPEC : 64
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
----------------------------------
Word_Page_00 : 16392
Word_Page_01 : 16392
Status_Byte_P00 : 64
Status_Byte_P01 : 64
Status_VOUT_P00 : 0
Status_VOUT_P01 : 0
Status_IOUT_P00 : 0
Status_IOUT_P01 : 0
Status_INPUT_P00 : 0
Status_INPUT_P01 : 0
Status_TEM_P00 : 0
Status_TEM_P01 : 0
Status_CML_P00 : 0
Status_CML_P01 : 0
Status_FANS_P00 : 0
Status_FANS_P01 : 0
STEP.523(UUT Test seq.523) : PS ON Delay time 80611(300VDC_HH) ---- (0'982) PASS
Vin (V)= Refer to the previous item
Fin (Hz)= Refer to the previous item
On Phase Delay(ms)= Refer to the previous item
UUT Off Time (s)= Refer to the previous item
Loading (A/Ohm/V)= Refer to the previous item
Trigger: 1:Trig1R(AC), 2:Trig2R(PS on), 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:Trig1F(AC), 9:Trig2F(PS on),10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1
2 1
3 1
4 1
Load Start End VcmpA VcmpB
Name Trigger Trigger (V) (V)
------------- ------- ------- ------- -------
12V 9 5 11.590 12.810
12Vsb 9 9 11.400 12.600
PWOK 9 5 2.600 2.600
Vin_Good 9 9 2.600 2.600
SMBAlert 9 9 2.600 2.600
Load Ton Ton Ton
Name Max Min (ms)
------------- -------- -------- ---------
12V 400.00 5.00 62.72
12Vsb ******** ******** 0.17
PWOK ******** ******** 268.21
Vin_Good ******** ******** 0.17
SMBAlert ******** ******** 0.17
Load Ref Load Td Td Td
Name No. Max Min (ms)
------------- ---------- -------- -------- ---------
12V 3 -500.000 -100.000 -205.491
12Vsb 0 ********* ********* 0.172
PWOK 1 500.000 100.000 205.491
Vin_Good 0 ********* ********* 0.171
SMBAlert 0 ********* ********* 0.171
STEP.524(UUT Test seq.524) : Turn On Timing Test_Multi or Single(300VDC_HH_ PASS
ElaspedTime (S)= 1'887
Vin (V)= 300.00
Fin (Hz)= 30.00
On Phase Delay(ms)= 90.00
UUT Off Time (s)= 0.50
Trigger: 1:TTL1R, 2:TTL2R, 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:TTL1F, 9:TTL2F,10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1.00
2 1.00
3 1.00
4 1.00
Load Loading Start End VcmpA VcmpB
Name (A/Ohm/V) Trigger Trigger (V) (V)
------------- ---------- ------- ------- ------- -------
12V 161.500 5 6 1.220 11.590
12Vsb 2.500 5 6 1.200 10.800
PWOK 0.000 8 1 2.600 3.460
Vin_Good 0.000 8 1 2.600 3.460
SMBAlert 0.000 8 1 2.600 3.460
Load Ton Ton Ton
Name Max Min (ms)
------------- -------- -------- ---------
12V 70.00 5.00 51.23
12Vsb 70.00 1.00 11.68
PWOK ******** ******** 0.06
Vin_Good ******** ******** 0.06
SMBAlert ******** ******** 0.06
Load Ref Load Td Td Td
Name No. Max Min (ms)
------------- ------------- -------- -------- ---------
12V 0 ******** ******** 51.23
12Vsb 0 ******** ******** 11.68
PWOK 0 ******** ******** 0.06
Vin_Good 0 ******** ******** 0.06
SMBAlert 0 ******** ******** 0.06
STEP.525(UUT Test seq.525) : TTL & Relay Setup ---- (0'000) --------------- PASS
(The Report Format of this Sequence was not found)
STEP.526(UUT Test seq.526) : PS ON Delay time 80611(300VDC_HH_Tpson_12V_Ris PASS
Vin (V)= Refer to the previous item
Fin (Hz)= Refer to the previous item
On Phase Delay(ms)= Refer to the previous item
UUT Off Time (s)= Refer to the previous item
Loading (A/Ohm/V)= Refer to the previous item
Trigger: 1:Trig1R(AC), 2:Trig2R(PS on), 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:Trig1F(AC), 9:Trig2F(PS on),10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1
2 1
3 1
4 1
Load Start End VcmpA VcmpB
Name Trigger Trigger (V) (V)
------------- ------- ------- ------- -------
12V 5 6 1.220 11.590
12Vsb 9 9 1.200 10.800
PWOK 9 9 2.600 2.600
Vin_Good 9 9 2.600 2.600
SMBAlert 9 9 2.600 2.600
Load Ton Ton Ton
Name Max Min (ms)
------------- -------- -------- ---------
12V 70.00 5.00 51.26
12Vsb ******** ******** 0.05
PWOK ******** ******** 0.05
Vin_Good ******** ******** 0.05
SMBAlert ******** ******** 0.05
Load Ref Load Td Td Td
Name No. Max Min (ms)
------------- ---------- -------- -------- ---------
12V 0 ********* ********* 51.261
12Vsb 0 ********* ********* 0.049
PWOK 0 ********* ********* 0.049
Vin_Good 0 ********* ********* 0.049
SMBAlert 0 ********* ********* 0.049
STEP.527(UUT Test seq.527) : Input Output Eff Noise Multi or Single(300VDC_ PASS
ElapsedTime (S)= 1'826
Vin (V)= 300.00
Fin (Hz)= 30.00
Delay Time (ms)= 500.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 80.750 ******* ******* 80.748
12Vsb 1.250 ******* ******* 1.250
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
-------Load---------------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V ???.??? ???.??? ???.???
12Vsb ???.??? ???.??? ???.???
PWOK ???.??? ???.??? ???.???
Vin_Good ???.??? ???.??? ???.???
SMBAlert ???.??? ???.??? ???.???
--------34970----------------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 12.810 11.590 12.216
12VSb 12.600 11.400 12.044
PWOK 3.460 2.500 3.233
Vin_Good 3.460 2.500 3.238
SMBAlert 3.460 2.500 3.219
IBUS ******* ******* 3.996
CR 0.400 ******* -0.009
Max Min Reading
------------- ---------- ---------- ----------
Vrms (V) ******** ******** 300.0468
PF 1.0000 ******** 1.0000
THDi (%) ******** * 133.1653
Irms (A) ******** ******** 3.6066
Pin (W) ******** ******** XXXXXXXX
Pout (W) ******** ******** XXXXXXXX
Eff (%) ******** ******** 92.5441
Load Noise Range Noise B.W
Name (V) (MHz)
------------- ----------- ---------
12V 2 20.000
12Vsb 2 20.000
PWOK 2 20.000
Vin_Good 2 20.000
SMBAlert 2 20.000
Load Vpp Noise Vpp Noise Vpp Noise
Name Max(mV) Min(mV) (mV)
------------- ------------ ------------ ------------
12V 120.000 0.000 12.220
12Vsb 120.000 0.000 9.060
PWOK ********* ********* 22.350
Vin_Good ********* ********* 21.780
SMBAlert ********* ********* 23.870
STEP.528(UUT Test seq.528) : Input Output Eff Noise Multi or Single(300VDC_ PASS
ElapsedTime (S)= 1'794
Vin (V)= 300.00
Fin (Hz)= 30.00
Delay Time (ms)= 500.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 161.500 ******* ******* 161.497
12Vsb 0.100 ******* ******* 0.100
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
-------Load---------------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V ???.??? ???.??? ???.???
12Vsb ???.??? ???.??? ???.???
PWOK ???.??? ???.??? ???.???
Vin_Good ???.??? ???.??? ???.???
SMBAlert ???.??? ???.??? ???.???
--------34970----------------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 12.810 11.590 12.167
12VSb 12.600 11.400 12.121
PWOK 3.460 2.500 3.228
Vin_Good 3.460 2.500 3.224
SMBAlert 3.460 2.500 3.223
IBUS ******* ******* 8.002
CR 0.400 ******* -0.020
Max Min Reading
------------- ---------- ---------- ----------
Vrms (V) ******** ******** 299.7185
PF 1.0000 ******** 1.0000
THDi (%) ******** * 128.4777
Irms (A) ******** ******** 7.1715
Pin (W) ******** ******** XXXXXXXX
Pout (W) ******** ******** XXXXXXXX
Eff (%) ******** ******** 91.4715
Load Noise Range Noise B.W
Name (V) (MHz)
------------- ----------- ---------
12V 2 20.000
12Vsb 2 20.000
PWOK 2 20.000
Vin_Good 2 20.000
SMBAlert 2 20.000
Load Vpp Noise Vpp Noise Vpp Noise
Name Max(mV) Min(mV) (mV)
------------- ------------ ------------ ------------
12V 120.000 0.000 14.720
12Vsb 120.000 0.000 6.180
PWOK ********* ********* 22.660
Vin_Good ********* ********* 21.830
SMBAlert ********* ********* 24.330
STEP.529(UUT Test seq.529) : Cold Redundant Master Multi _S2 ---- (0'094) - PASS
(The Report Format of this Sequence was not found)
STEP.530(UUT Test seq.530) : Static ACDC 34970_or_Load_Multi or Single(300V PASS
ElapsedTime (S)= 1'233
Vin (V)= 300.00
Fin (Hz)= 30.00
Delay Time (ms)= 500.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 161.500 ******* ******* 161.497
12Vsb 2.500 ******* ******* 2.500
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 12.810 11.590 12.167
12VSb 12.600 11.400 11.991
PWOK 3.460 2.500 3.216
Vin_Good 3.460 2.500 3.223
SMBAlert 3.460 2.500 3.223
IBUS ******* ******* 8.002
CR 3.460 2.500 3.166
Max Min Reading
------------- --------- --------- ---------
Pout (W) ******* ******* XXXXXXX
STEP.531(UUT Test seq.531) : Disable Cold Redundant Master Multi_S2 ---- (0 PASS
(The Report Format of this Sequence was not found)
STEP.532(UUT Test seq.532) : Static ACDC 34970_or_Load_Multi or Single(300V PASS
ElapsedTime (S)= 1'248
Vin (V)= 300.00
Fin (Hz)= 30.00
Delay Time (ms)= 500.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 161.500 ******* ******* 161.497
12Vsb 2.500 ******* ******* 2.500
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 12.810 11.590 12.165
12VSb 12.600 11.400 11.994
PWOK 3.460 2.500 3.226
Vin_Good 3.460 2.500 3.220
SMBAlert 3.460 2.500 3.226
IBUS ******* ******* 7.999
CR 0.400 ******* -0.022
Max Min Reading
------------- --------- --------- ---------
Pout (W) ******* ******* XXXXXXX
STEP.533(UUT Test seq.533) : Input Output Eff Noise Multi or Single(300VDC_ PASS
ElapsedTime (S)= 1'763
Vin (V)= 300.00
Fin (Hz)= 30.00
Delay Time (ms)= 500.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 161.500 ******* ******* 161.497
12Vsb 2.500 ******* ******* 2.500
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
-------Load---------------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V ???.??? ???.??? ???.???
12Vsb ???.??? ???.??? ???.???
PWOK ???.??? ???.??? ???.???
Vin_Good ???.??? ???.??? ???.???
SMBAlert ???.??? ???.??? ???.???
--------34970----------------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 12.810 11.590 12.166
12VSb 12.600 11.400 11.994
PWOK 3.460 2.500 3.220
Vin_Good 3.460 2.500 3.225
SMBAlert 3.460 2.500 3.225
IBUS ******* ******* 8.003
CR 0.400 ******* -0.022
Max Min Reading
------------- ---------- ---------- ----------
Vrms (V) ******** ******** 299.7196
PF 1.0000 ******** 1.0000
THDi (%) ******** * XXXXXXXX
Irms (A) ******** ******** 7.2950
Pin (W) ******** ******** XXXXXXXX
Pout (W) ******** ******** XXXXXXXX
Eff (%) ******** ******** 91.2345
Load Noise Range Noise B.W
Name (V) (MHz)
------------- ----------- ---------
12V 2 20.000
12Vsb 2 20.000
PWOK 2 20.000
Vin_Good 2 20.000
SMBAlert 2 20.000
Load Vpp Noise Vpp Noise Vpp Noise
Name Max(mV) Min(mV) (mV)
------------- ------------ ------------ ------------
12V 120.000 0.000 14.040
12Vsb 120.000 0.000 15.350
PWOK ********* ********* 24.220
Vin_Good ********* ********* 22.770
SMBAlert ********* ********* 25.450
STEP.534(UUT Test seq.534) : Static ACDC 34970_or_Load_Multi or Single(300V PASS
ElapsedTime (S)= 1'232
Vin (V)= 300.00
Fin (Hz)= 30.00
Delay Time (ms)= 500.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 161.500 ******* ******* 161.497
12Vsb 2.750 ******* ******* 2.750
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 12.810 11.590 12.165
12VSb 12.600 11.400 11.988
PWOK 3.460 2.500 3.226
Vin_Good 3.460 2.500 3.224
SMBAlert 3.460 2.500 3.222
IBUS ******* ******* 8.003
CR 0.400 ******* -0.022
Max Min Reading
------------- --------- --------- ---------
Pout (W) ******* ******* XXXXXXX
STEP.535(UUT Test seq.535) : Static ACDC 34970_or_Load_Multi or Single(300V PASS
ElapsedTime (S)= 1'420
Vin (V)= 300.00
Fin (Hz)= 30.00
Delay Time (ms)= 500.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 161.500 ******* ******* 0.000
12Vsb 3.650 ******* ******* 0.012
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 0.400 ******* 0.001
12VSb 12.600 ******* 11.978
PWOK 0.400 ******* 0.039
Vin_Good 3.460 2.400 3.240
SMBAlert 3.460 ******* 3.215
IBUS ******* ******* 0.148
CR 0.400 ******* 0.005
Max Min Reading
------------- --------- --------- ---------
Pout (W) ******* ******* 0.148
STEP.536(UUT Test seq.536) : Static ACDC 34970_or_Load_Multi or Single(300V PASS
ElapsedTime (S)= 1'887
Vin (V)= 300.00
Fin (Hz)= 30.00
Delay Time (ms)= 1000.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 161.500 ******* ******* 161.497
12Vsb 2.750 ******* ******* 2.750
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 12.810 11.590 12.159
12VSb 12.600 11.400 11.987
PWOK 3.460 2.500 3.222
Vin_Good 3.460 2.500 3.220
SMBAlert 3.460 2.500 3.228
IBUS ******* ******* 8.001
CR 0.400 ******* -0.022
Max Min Reading
------------- --------- --------- ---------
Pout (W) ******* ******* XXXXXXX
STEP.537(UUT Test seq.537) : Hold Up Timing Test_Multi or Single(300VDC_70% PASS
ElapsedTime (S)= 3'713
Vin (V)= 300.00
Fin (Hz)= 30.00
Delay Time (ms)= 3000.00
On Phase Delay(ms)= 90.00
UUT Off Time (s)= 0.00
Trigger: 1:Trig1R(AC), 2:Trig2R(PS on), 3:TTL3R, 4:TTL4R, 5:CMPAR, 6:CMPBR, 7:SWR,
8:Trig1F(AC), 9:Trig2F(PS on),10:TTL3F,11:TTL4F,12:CMPAF,13:CMPBF,14:SWF
TTL Trigger
Index Level
------- ---------
1 1
2 1
3 1
4 1
Load Loading Start End VcmpA VcmpB
Name (A/Ohm/V) Trigger Trigger (V) (V)
------------- ---------- ------- ------- ------- -------
12V 113.050 8 12 11.590 12.810
12Vsb 1.750 8 12 11.400 12.600
PWOK 0.000 8 12 2.600 3.460
Vin_Good 0.000 8 12 2.600 3.460
SMBAlert 0.000 8 1 2.600 3.460
Load Tholdup Tholdup Tholdup
Name Max Min (ms)
------------- -------- -------- ---------
12V 1000.00 10.00 21.78
12Vsb 1000.00 70.00 78.93
PWOK 300.00 9.00 20.12
Vin_Good 4.00 0.01 2.77
SMBAlert ******** ******** 0.06
Load Ref Load Tholdup Tholdup Tholdup
Name No. Max Min (ms)
------------- ---------- -------- -------- ---------
12V 3 100.00 1.00 1.66
12Vsb 0 ******** ******** 78.93
PWOK 1 -100.00 -1.00 -1.66
Vin_Good 0 ******** ******** 2.77
SMBAlert 0 ******** ******** 0.06
STEP.538(UUT Test seq.538) : FAN Full Speed delay time Multi ---- (5'101) - PASS
STEP.539(UUT Test seq.539) : FAN Speed Normal_Multi ---- (0'094) ---------- PASS
(The Report Format of this Sequence was not found)
STEP.540(UUT Test seq.540) : 61512 Ac Source ACDC Mode_Multi_S2 ---- (0'172 PASS
(The Report Format of this Sequence was not found)
STEP.541(UUT Test seq.541) : Input Source Distortion_Multi or Single ---- ( PASS
STEP.542(UUT Test seq.542) : Static ACDC 34970_or_Load_Multi or Single(---- PASS
ElapsedTime (S)= 3'776
Vin (V)= 100.00
Fin (Hz)= 60.00
Delay Time (ms)= 3000.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 71.300 ******* ******* 71.298
12Vsb 2.500 ******* ******* 2.500
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 12.810 11.590 12.219
12VSb 12.600 11.400 12.005
PWOK 3.460 2.500 3.235
Vin_Good 3.460 2.500 3.240
SMBAlert 3.460 2.500 3.215
IBUS ******* ******* 3.531
CR 0.400 ******* -0.009
Max Min Reading
------------- --------- --------- ---------
Pout (W) ******* ******* 901.222
STEP.543(UUT Test seq.543) : Input Source Distortion_Multi or Single ---- ( PASS
STEP.544(UUT Test seq.544) : Static ACDC 34970_or_Load_Multi or Single(---- PASS
ElapsedTime (S)= 1'794
Vin (V)= 100.00
Fin (Hz)= 60.00
Delay Time (ms)= 1000.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 1.000 ******* ******* 0.998
12Vsb 0.100 ******* ******* 0.100
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 12.810 11.590 12.259
12VSb 12.600 11.400 12.138
PWOK 3.460 2.500 3.246
Vin_Good 3.460 2.500 3.251
SMBAlert 3.460 2.500 3.212
IBUS ******* ******* 0.060
CR 0.400 ******* 0.003
Max Min Reading
------------- --------- --------- ---------
Pout (W) ******* ******* 13.446
STEP.545(UUT Test seq.545) : Input Source Distortion_Multi or Single ---- ( PASS
STEP.546(UUT Test seq.546) : Static ACDC 34970_or_Load_Multi or Single(---- PASS
ElapsedTime (S)= 1'716
Vin (V)= 200.00
Fin (Hz)= 50.00
Delay Time (ms)= 1000.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 1.000 ******* ******* 0.998
12Vsb 0.100 ******* ******* 0.100
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 12.810 11.590 12.259
12VSb 12.600 11.400 12.135
PWOK 3.460 2.500 3.244
Vin_Good 3.460 2.500 3.249
SMBAlert 3.460 2.500 3.214
IBUS ******* ******* 0.060
CR 0.400 ******* 0.003
Max Min Reading
------------- --------- --------- ---------
Pout (W) ******* ******* 13.447
STEP.547(UUT Test seq.547) : Input Source Distortion_Multi or Single ---- ( PASS
STEP.548(UUT Test seq.548) : Static ACDC 34970_or_Load_Multi or Single(---- PASS
ElapsedTime (S)= 1'810
Vin (V)= 200.00
Fin (Hz)= 50.00
Delay Time (ms)= 1000.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 128.700 ******* ******* 128.697
12Vsb 2.500 ******* ******* 2.500
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 12.810 11.590 12.185
12VSb 12.600 11.400 11.995
PWOK 3.460 2.500 3.227
Vin_Good 3.460 2.500 3.232
SMBAlert 3.460 2.500 3.218
IBUS ******* ******* 6.359
CR 0.400 ******* -0.017
Max Min Reading
------------- --------- --------- ---------
Pout (W) ******* ******* XXXXXXX
STEP.549(UUT Test seq.549) : Input Source Set SinWaveform_Multi or Single - PASS
STEP.550(UUT Test seq.550) : Static ACDC 34970_or_Load_Multi or Single(89.5 PASS
ElapsedTime (S)= 2'277
Vin (V)= 89.50
Fin (Hz)= 47.00
Delay Time (ms)= 1500.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 1.000 ******* ******* 0.998
12Vsb 0.100 ******* ******* 0.100
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 12.810 11.590 12.259
12VSb 12.600 11.400 12.135
PWOK 3.460 2.500 3.244
Vin_Good 3.460 2.500 3.251
SMBAlert 3.460 2.500 3.214
IBUS ******* ******* 0.060
CR 0.400 ******* 0.003
Max Min Reading
------------- --------- --------- ---------
Pout (W) ******* ******* 13.446
STEP.551(UUT Test seq.551) : Static ACDC 34970_or_Load_Multi or Single(80Va PASS
ElapsedTime (S)= 2'215
Vin (V)= 80.00
Fin (Hz)= 47.00
Delay Time (ms)= 1500.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 1.000 ******* ******* 0.998
12Vsb 0.100 ******* ******* 0.100
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 12.810 11.590 12.259
12VSb 12.600 11.400 12.133
PWOK 3.460 2.500 3.251
Vin_Good 3.460 2.500 3.244
SMBAlert 3.460 2.500 3.219
IBUS ******* ******* 0.061
CR 0.400 ******* 0.003
Max Min Reading
------------- --------- --------- ---------
Pout (W) ******* ******* 13.447
STEP.552(UUT Test seq.552) : Static ACDC 34970_or_Load_Multi or Single(70.5 PASS
ElapsedTime (S)= 2'450
Vin (V)= 70.50
Fin (Hz)= 47.00
Delay Time (ms)= 1500.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 1.000 ******* ******* 0.000
12Vsb 0.100 ******* ******* 0.007
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 0.400 ******* 0.000
12VSb 0.400 ******* 0.110
PWOK 0.400 ******* 0.038
Vin_Good 0.400 ******* 0.039
SMBAlert 0.400 ******* 0.071
IBUS ******* ******* -0.012
CR 0.400 ******* 0.004
Max Min Reading
------------- --------- --------- ---------
Pout (W) ******* ******* 0.001
STEP.553(UUT Test seq.553) : Static ACDC 34970_or_Load_Multi or Single(79.8 PASS
ElapsedTime (S)= 2'231
Vin (V)= 79.80
Fin (Hz)= 47.00
Delay Time (ms)= 1500.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 1.000 ******* ******* 0.000
12Vsb 0.100 ******* ******* 0.008
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 0.400 ******* 0.000
12VSb 0.400 ******* 0.110
PWOK 0.400 ******* 0.038
Vin_Good 0.400 ******* 0.039
SMBAlert 0.400 ******* 0.070
IBUS ******* ******* -0.018
CR 0.400 ******* 0.004
Max Min Reading
------------- --------- --------- ---------
Pout (W) ******* ******* 0.001
STEP.554(UUT Test seq.554) : I2C Read Status Multi_S6(Vin_UV) ---- (0'125) PASS
Adderss :B0
Command Page00 :060200
Command Page01 :060201
Status Word :79
Status Byte :78
Status VOUT :7A
Status IOUT :7B
Status INPUT :7C
Status TEMPERATURE :7D
Status CML :7E
Status FANS :81
---------------------------------
Word SPEC: 18472
Word SPEC: 18472
Word SPEC: 18472
Word SPEC: 18472
Word SPEC: 18472
Word SPEC: 18472
Word SPEC: 18472
Word SPEC: 18472
Word SPEC_Page1: 18472
Word SPEC_Page1: 18472
Word SPEC_Page1: 18472
Word SPEC_Page1: 18472
Word SPEC_Page1: 18472
Word SPEC_Page1: 18472
Word SPEC_Page1: 18472
Word SPEC_Page1: 18472
Byte SPEC : 72
Byte SPEC : 72
Byte SPEC : 72
Byte SPEC : 72
Byte SPEC : 72
Byte SPEC : 72
Byte SPEC : 72
Byte SPEC : 72
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Input SPEC : 56
Input SPEC : 56
Input SPEC : 56
Input SPEC : 56
Input SPEC : 56
Input SPEC : 56
Input SPEC : 56
Input SPEC : 56
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
----------------------------------
Word_Page_00 : 18472
Word_Page_01 : 18472
Status_Byte_P00 : 72
Status_Byte_P01 : 72
Status_VOUT_P00 : 0
Status_VOUT_P01 : 0
Status_IOUT_P00 : 0
Status_IOUT_P01 : 0
Status_INPUT_P00 : 56
Status_INPUT_P01 : 56
Status_TEM_P00 : 0
Status_TEM_P01 : 0
Status_CML_P00 : 0
Status_CML_P01 : 0
Status_FANS_P00 : 0
Status_FANS_P01 : 0
STEP.555(UUT Test seq.555) : Static ACDC 34970_or_Load_Multi or Single(89.5 PASS
ElapsedTime (S)= 2'527
Vin (V)= 89.50
Fin (Hz)= 47.00
Delay Time (ms)= 1500.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 71.300 ******* ******* 71.298
12Vsb 2.500 ******* ******* 2.500
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 12.810 11.590 12.216
12VSb 12.600 11.400 12.003
PWOK 3.460 2.500 3.234
Vin_Good 3.460 2.500 3.233
SMBAlert 3.460 2.500 3.215
IBUS ******* ******* 3.532
CR 0.400 ******* -0.009
Max Min Reading
------------- --------- --------- ---------
Pout (W) ******* ******* 900.953
STEP.556(UUT Test seq.556) : Static ACDC 34970_or_Load_Multi or Single(80Va PASS
ElapsedTime (S)= 2'247
Vin (V)= 80.00
Fin (Hz)= 47.00
Delay Time (ms)= 1500.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 71.300 ******* ******* 71.298
12Vsb 2.500 ******* ******* 2.500
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 12.810 11.590 12.214
12VSb 12.600 11.400 12.005
PWOK 3.460 2.500 3.233
Vin_Good 3.460 2.500 3.238
SMBAlert 3.460 2.500 3.219
IBUS ******* ******* 3.532
CR 0.400 ******* -0.009
Max Min Reading
------------- --------- --------- ---------
Pout (W) ******* ******* 900.850
STEP.557(UUT Test seq.557) : Static ACDC 34970_or_Load_Multi or Single(70.5 PASS
ElapsedTime (S)= 2'527
Vin (V)= 70.50
Fin (Hz)= 47.00
Delay Time (ms)= 1500.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 71.300 ******* ******* 0.000
12Vsb 2.500 ******* ******* 0.006
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 0.400 ******* 0.000
12VSb 0.400 ******* 0.099
PWOK 0.400 ******* 0.038
Vin_Good 0.400 ******* 0.039
SMBAlert 0.400 ******* 0.071
IBUS ******* ******* 0.005
CR 0.400 ******* 0.004
Max Min Reading
------------- --------- --------- ---------
Pout (W) ******* ******* 0.001
STEP.558(UUT Test seq.558) : Static ACDC 34970_or_Load_Multi or Single(79.8 PASS
ElapsedTime (S)= 2'262
Vin (V)= 79.80
Fin (Hz)= 47.00
Delay Time (ms)= 1500.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 71.300 ******* ******* 0.000
12Vsb 2.500 ******* ******* 0.008
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 0.400 ******* 0.000
12VSb 0.400 ******* 0.099
PWOK 0.400 ******* 0.039
Vin_Good 0.400 ******* 0.039
SMBAlert 0.400 ******* 0.071
IBUS ******* ******* -0.045
CR 0.400 ******* 0.004
Max Min Reading
------------- --------- --------- ---------
Pout (W) ******* ******* 0.001
STEP.559(UUT Test seq.559) : AC Line Sag Surge 80611N-2_Multi_S5(90V-5S) -- PASS
ElapsedTime (S)= 7'364
Vin (V)= 90.00
Fin (Hz)= 47.00
Delay Time (ms)= 1000.00
Drop Time (ms)= 5000.00
Drop Recovery Time(ms)= 1000.00
Drop Voltage (v)= 0.00
Drop Frequency (Hz)= 47.00
Repeat Count = 1
Degree = 0
Duty cycle (%)= 100.000000
Load Loading Vpk Max Vpk Min Vpk High Vpk Low
Name (A/Ohm/V) (V) (V) (V) (V)
------------- ----------- --------- --------- --------- ---------
12V 71.300 ********* ********* 12.206 0.014
12Vsb 2.500 ********* ********* 12.053 0.110
PWOK 0.000 ********* ********* 3.266 0.068
Vin_Good 0.000 ********* ********* 3.268 0.056
SMBAlert 0.000 ********* ********* 3.259 0.110
STEP.560(UUT Test seq.560) : Static ACDC 34970_or_Load_Multi or Single ---- PASS
ElapsedTime (S)= 2'605
Vin (V)= 90.00
Fin (Hz)= 47.00
Delay Time (ms)= 1500.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 71.300 ******* ******* 71.298
12Vsb 2.500 ******* ******* 2.500
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 12.810 11.590 12.216
12VSb 12.600 11.400 12.005
PWOK 3.460 2.500 3.237
Vin_Good 3.460 2.500 3.238
SMBAlert 3.460 2.500 3.218
IBUS ******* ******* 3.533
CR 0.400 ******* -0.009
Max Min Reading
------------- --------- --------- ---------
Pout (W) ******* ******* 901.011
STEP.561(UUT Test seq.561) : AC Source ON/OFF(input source)_Multi_S2 ---- ( PASS
(The Report Format of this Sequence was not found)
STEP.562(UUT Test seq.562) : AC Line Sag Surge 80611N-2_Multi_S5(264V-5S) - PASS
ElapsedTime (S)= 9'407
Vin (V)= 264.00
Fin (Hz)= 63.00
Delay Time (ms)= 3000.00
Drop Time (ms)= 5000.00
Drop Recovery Time(ms)= 1000.00
Drop Voltage (v)= 0.00
Drop Frequency (Hz)= 63.00
Repeat Count = 1
Degree = 0
Duty cycle (%)= 100.000000
Load Loading Vpk Max Vpk Min Vpk High Vpk Low
Name (A/Ohm/V) (V) (V) (V) (V)
------------- ----------- --------- --------- --------- ---------
12V 161.500 ********* ********* 12.176 0.014
12Vsb 2.500 ********* ********* 12.041 0.108
PWOK 0.000 ********* ********* 3.252 0.052
Vin_Good 0.000 ********* ********* 3.266 0.038
SMBAlert 0.000 ********* ********* 3.265 0.110
STEP.563(UUT Test seq.563) : Static ACDC 34970_or_Load_Multi or Single ---- PASS
ElapsedTime (S)= 2'293
Vin (V)= 264.00
Fin (Hz)= 63.00
Delay Time (ms)= 1500.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 161.500 ******* ******* 161.497
12Vsb 2.500 ******* ******* 2.500
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 12.810 11.590 12.159
12VSb 12.600 11.400 11.994
PWOK 3.460 2.500 3.225
Vin_Good 3.460 2.500 3.221
SMBAlert 3.460 2.500 3.228
IBUS ******* ******* 8.004
CR 0.400 ******* -0.021
Max Min Reading
------------- --------- --------- ---------
Pout (W) ******* ******* XXXXXXX
STEP.564(UUT Test seq.564) : AC Source ON/OFF(input source)_Multi_S2 ---- ( PASS
(The Report Format of this Sequence was not found)
STEP.565(UUT Test seq.565) : AC Line Sag Surge 80611N-2_Multi_S5(115V-->97. PASS
ElapsedTime (S)= 19'391
Vin (V)= 115.00
Fin (Hz)= 60.00
Delay Time (ms)= 3000.00
Drop Time (ms)= 15000.00
Drop Recovery Time(ms)= 1000.00
Drop Voltage (v)= 97.75
Drop Frequency (Hz)= 50.00
Repeat Count = 1
Degree = 0
Duty cycle (%)= 100.000000
Load Loading Vpk Max Vpk Min Vpk High Vpk Low
Name (A/Ohm/V) (V) (V) (V) (V)
------------- ----------- --------- --------- --------- ---------
12V 71.300 12.810 11.590 12.239 12.216
12Vsb 2.500 12.600 11.400 12.037 12.024
PWOK 0.000 3.460 2.500 3.268 3.273
Vin_Good 0.000 3.460 2.500 3.262 3.263
SMBAlert 0.000 3.460 2.500 3.260 3.255
STEP.566(UUT Test seq.566) : I2C Read Status Multi_S6 ---- (0'125) -------- PASS
Adderss :B0
Command Page00 :060200
Command Page01 :060201
Status Word :79
Status Byte :78
Status VOUT :7A
Status IOUT :7B
Status INPUT :7C
Status TEMPERATURE :7D
Status CML :7E
Status FANS :81
---------------------------------
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
----------------------------------
Word_Page_00 : 0
Word_Page_01 : 0
Status_Byte_P00 : 0
Status_Byte_P01 : 0
Status_VOUT_P00 : 0
Status_VOUT_P01 : 0
Status_IOUT_P00 : 0
Status_IOUT_P01 : 0
Status_INPUT_P00 : 0
Status_INPUT_P01 : 0
Status_TEM_P00 : 0
Status_TEM_P01 : 0
Status_CML_P00 : 0
Status_CML_P01 : 0
Status_FANS_P00 : 0
Status_FANS_P01 : 0
STEP.567(UUT Test seq.567) : AC Line Sag Surge 80611N-2_Multi_S5(115V-->132 PASS
ElapsedTime (S)= 19'344
Vin (V)= 115.00
Fin (Hz)= 60.00
Delay Time (ms)= 3000.00
Drop Time (ms)= 15000.00
Drop Recovery Time(ms)= 1000.00
Drop Voltage (v)= 132.25
Drop Frequency (Hz)= 50.00
Repeat Count = 1
Degree = 0
Duty cycle (%)= 100.000000
Load Loading Vpk Max Vpk Min Vpk High Vpk Low
Name (A/Ohm/V) (V) (V) (V) (V)
------------- ----------- --------- --------- --------- ---------
12V 79.500 12.810 11.590 12.233 12.209
12Vsb 2.500 12.600 11.400 12.036 12.024
PWOK 0.000 3.460 2.500 3.267 3.272
Vin_Good 0.000 3.460 2.500 3.260 3.260
SMBAlert 0.000 3.460 2.500 3.260 3.256
STEP.568(UUT Test seq.568) : I2C Read Status Multi_S6 ---- (0'109) -------- PASS
Adderss :B0
Command Page00 :060200
Command Page01 :060201
Status Word :79
Status Byte :78
Status VOUT :7A
Status IOUT :7B
Status INPUT :7C
Status TEMPERATURE :7D
Status CML :7E
Status FANS :81
---------------------------------
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
----------------------------------
Word_Page_00 : 0
Word_Page_01 : 0
Status_Byte_P00 : 0
Status_Byte_P01 : 0
Status_VOUT_P00 : 0
Status_VOUT_P01 : 0
Status_IOUT_P00 : 0
Status_IOUT_P01 : 0
Status_INPUT_P00 : 0
Status_INPUT_P01 : 0
Status_TEM_P00 : 0
Status_TEM_P01 : 0
Status_CML_P00 : 0
Status_CML_P01 : 0
Status_FANS_P00 : 0
Status_FANS_P01 : 0
STEP.569(UUT Test seq.569) : AC Source ON/OFF(input source)_Multi_S2 ---- ( PASS
(The Report Format of this Sequence was not found)
STEP.570(UUT Test seq.570) : Set Input Condition_Load_S4 ---- (0'016) ----- PASS
Vin (V)= 90.000
Fin (Hz)= 47.000
Load Loading
Name (A/Ohm/V)
------------- ----------
12V 49.9100
12Vsb 1.7500
PWOK 0.0000
Vin_Good 0.0000
SMBAlert 0.0000
STEP.571(UUT Test seq.571) : Set Drop Time ---- (0'000) ------------------- PASS
Drop Time= 10
STEP.572(UUT Test seq.572) : AC_DC Line Sag Surge 80611N-2_Multi_S2(90Vac - PASS
ElapsedTime (S)= 3'901
Vin (V)= 90.00
Fin (Hz)= 47.00
Delay Time (ms)= 3000.00
Drop Time (ms)= 10.00
Drop Recovery Time(ms)= 500.00
Drop Voltage (v)= 0.00
Drop Frequency (Hz)= 47.00
Repeat Count = 1
Degree = 0
Duty cycle (%)= 100.000000
Load Loading Vpk Max Vpk Min Vpk High Vpk Low
Name (A/Ohm/V) (V) (V) (V) (V)
------------- ----------- --------- --------- --------- ---------
12V 49.910 12.810 11.590 12.251 12.232
12Vsb 1.750 12.600 11.400 12.057 12.046
PWOK 0.000 3.460 2.500 3.270 3.277
Vin_Good 0.000 3.460 ********* 3.263 0.061
SMBAlert 0.000 3.460 ********* 3.258 3.257
STEP.573(UUT Test seq.573) : I2C Read Status Multi_S6(90Vac -->0Vac - 10ms- PASS
Adderss :B0
Command Page00 :060200
Command Page01 :060201
Status Word :79
Status Byte :78
Status VOUT :7A
Status IOUT :7B
Status INPUT :7C
Status TEMPERATURE :7D
Status CML :7E
Status FANS :81
---------------------------------
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
----------------------------------
Word_Page_00 : 0
Word_Page_01 : 0
Status_Byte_P00 : 0
Status_Byte_P01 : 0
Status_VOUT_P00 : 0
Status_VOUT_P01 : 0
Status_IOUT_P00 : 0
Status_IOUT_P01 : 0
Status_INPUT_P00 : 0
Status_INPUT_P01 : 0
Status_TEM_P00 : 0
Status_TEM_P01 : 0
Status_CML_P00 : 0
Status_CML_P01 : 0
Status_FANS_P00 : 0
Status_FANS_P01 : 0
STEP.574(UUT Test seq.574) : AC_DC Line Sag Surge 80611N-2_Multi_S2(90Vac - PASS
ElapsedTime (S)= 1'373
Vin (V)= 90.00
Fin (Hz)= 47.00
Delay Time (ms)= 500.00
Drop Time (ms)= 10.00
Drop Recovery Time(ms)= 500.00
Drop Voltage (v)= 0.00
Drop Frequency (Hz)= 47.00
Repeat Count = 1
Degree = 45
Duty cycle (%)= 100.000000
Load Loading Vpk Max Vpk Min Vpk High Vpk Low
Name (A/Ohm/V) (V) (V) (V) (V)
------------- ----------- --------- --------- --------- ---------
12V 49.910 12.810 11.590 12.251 12.231
12Vsb 1.750 12.600 11.400 12.058 12.047
PWOK 0.000 3.460 2.500 3.270 3.277
Vin_Good 0.000 3.460 ********* 3.263 0.065
SMBAlert 0.000 3.460 ********* 3.259 3.257
STEP.575(UUT Test seq.575) : I2C Read Status Multi_S6(90Vac -->0Vac - 10ms- PASS
Adderss :B0
Command Page00 :060200
Command Page01 :060201
Status Word :79
Status Byte :78
Status VOUT :7A
Status IOUT :7B
Status INPUT :7C
Status TEMPERATURE :7D
Status CML :7E
Status FANS :81
---------------------------------
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
----------------------------------
Word_Page_00 : 0
Word_Page_01 : 0
Status_Byte_P00 : 0
Status_Byte_P01 : 0
Status_VOUT_P00 : 0
Status_VOUT_P01 : 0
Status_IOUT_P00 : 0
Status_IOUT_P01 : 0
Status_INPUT_P00 : 0
Status_INPUT_P01 : 0
Status_TEM_P00 : 0
Status_TEM_P01 : 0
Status_CML_P00 : 0
Status_CML_P01 : 0
Status_FANS_P00 : 0
Status_FANS_P01 : 0
STEP.576(UUT Test seq.576) : AC_DC Line Sag Surge 80611N-2_Multi_S2(90Vac - PASS
ElapsedTime (S)= 1'389
Vin (V)= 90.00
Fin (Hz)= 47.00
Delay Time (ms)= 500.00
Drop Time (ms)= 10.00
Drop Recovery Time(ms)= 500.00
Drop Voltage (v)= 0.00
Drop Frequency (Hz)= 47.00
Repeat Count = 1
Degree = 90
Duty cycle (%)= 100.000000
Load Loading Vpk Max Vpk Min Vpk High Vpk Low
Name (A/Ohm/V) (V) (V) (V) (V)
------------- ----------- --------- --------- --------- ---------
12V 49.910 12.810 11.590 12.251 12.231
12Vsb 1.750 12.600 11.400 12.056 12.046
PWOK 0.000 3.460 2.500 3.270 3.277
Vin_Good 0.000 3.460 ********* 3.265 0.065
SMBAlert 0.000 3.460 ********* 3.258 3.255
STEP.577(UUT Test seq.577) : I2C Read Status Multi_S6(90Vac -->0Vac - 10ms- PASS
Adderss :B0
Command Page00 :060200
Command Page01 :060201
Status Word :79
Status Byte :78
Status VOUT :7A
Status IOUT :7B
Status INPUT :7C
Status TEMPERATURE :7D
Status CML :7E
Status FANS :81
---------------------------------
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
----------------------------------
Word_Page_00 : 0
Word_Page_01 : 0
Status_Byte_P00 : 0
Status_Byte_P01 : 0
Status_VOUT_P00 : 0
Status_VOUT_P01 : 0
Status_IOUT_P00 : 0
Status_IOUT_P01 : 0
Status_INPUT_P00 : 0
Status_INPUT_P01 : 0
Status_TEM_P00 : 0
Status_TEM_P01 : 0
Status_CML_P00 : 0
Status_CML_P01 : 0
Status_FANS_P00 : 0
Status_FANS_P01 : 0
STEP.578(UUT Test seq.578) : AC_DC Line Sag Surge 80611N-2_Multi_S2(90Vac - PASS
ElapsedTime (S)= 1'373
Vin (V)= 90.00
Fin (Hz)= 47.00
Delay Time (ms)= 500.00
Drop Time (ms)= 10.00
Drop Recovery Time(ms)= 500.00
Drop Voltage (v)= 0.00
Drop Frequency (Hz)= 47.00
Repeat Count = 1
Degree =135
Duty cycle (%)= 100.000000
Load Loading Vpk Max Vpk Min Vpk High Vpk Low
Name (A/Ohm/V) (V) (V) (V) (V)
------------- ----------- --------- --------- --------- ---------
12V 49.910 12.810 11.590 12.251 12.233
12Vsb 1.750 12.600 11.400 12.056 12.047
PWOK 0.000 3.460 2.500 3.270 3.278
Vin_Good 0.000 3.460 ********* 3.263 0.063
SMBAlert 0.000 3.460 ********* 3.258 3.257
STEP.579(UUT Test seq.579) : I2C Read Status Multi_S6(90Vac -->0Vac - 10ms- PASS
Adderss :B0
Command Page00 :060200
Command Page01 :060201
Status Word :79
Status Byte :78
Status VOUT :7A
Status IOUT :7B
Status INPUT :7C
Status TEMPERATURE :7D
Status CML :7E
Status FANS :81
---------------------------------
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
----------------------------------
Word_Page_00 : 0
Word_Page_01 : 0
Status_Byte_P00 : 0
Status_Byte_P01 : 0
Status_VOUT_P00 : 0
Status_VOUT_P01 : 0
Status_IOUT_P00 : 0
Status_IOUT_P01 : 0
Status_INPUT_P00 : 0
Status_INPUT_P01 : 0
Status_TEM_P00 : 0
Status_TEM_P01 : 0
Status_CML_P00 : 0
Status_CML_P01 : 0
Status_FANS_P00 : 0
Status_FANS_P01 : 0
STEP.580(UUT Test seq.580) : AC_DC Line Sag Surge 80611N-2_Multi_S2(90Vac - PASS
ElapsedTime (S)= 1'373
Vin (V)= 90.00
Fin (Hz)= 47.00
Delay Time (ms)= 500.00
Drop Time (ms)= 10.00
Drop Recovery Time(ms)= 500.00
Drop Voltage (v)= 0.00
Drop Frequency (Hz)= 47.00
Repeat Count = 1
Degree =225
Duty cycle (%)= 100.000000
Load Loading Vpk Max Vpk Min Vpk High Vpk Low
Name (A/Ohm/V) (V) (V) (V) (V)
------------- ----------- --------- --------- --------- ---------
12V 49.910 12.810 11.590 12.251 12.231
12Vsb 1.750 12.600 11.400 12.057 12.047
PWOK 0.000 3.460 2.500 3.270 3.277
Vin_Good 0.000 3.460 ********* 3.263 0.064
SMBAlert 0.000 3.460 ********* 3.258 3.257
STEP.581(UUT Test seq.581) : I2C Read Status Multi_S6(90Vac -->0Vac - 10ms- PASS
Adderss :B0
Command Page00 :060200
Command Page01 :060201
Status Word :79
Status Byte :78
Status VOUT :7A
Status IOUT :7B
Status INPUT :7C
Status TEMPERATURE :7D
Status CML :7E
Status FANS :81
---------------------------------
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
----------------------------------
Word_Page_00 : 0
Word_Page_01 : 0
Status_Byte_P00 : 0
Status_Byte_P01 : 0
Status_VOUT_P00 : 0
Status_VOUT_P01 : 0
Status_IOUT_P00 : 0
Status_IOUT_P01 : 0
Status_INPUT_P00 : 0
Status_INPUT_P01 : 0
Status_TEM_P00 : 0
Status_TEM_P01 : 0
Status_CML_P00 : 0
Status_CML_P01 : 0
Status_FANS_P00 : 0
Status_FANS_P01 : 0
STEP.582(UUT Test seq.582) : AC_DC Line Sag Surge 80611N-2_Multi_S2(90Vac - PASS
ElapsedTime (S)= 1'341
Vin (V)= 90.00
Fin (Hz)= 47.00
Delay Time (ms)= 500.00
Drop Time (ms)= 10.00
Drop Recovery Time(ms)= 500.00
Drop Voltage (v)= 0.00
Drop Frequency (Hz)= 47.00
Repeat Count = 1
Degree =270
Duty cycle (%)= 100.000000
Load Loading Vpk Max Vpk Min Vpk High Vpk Low
Name (A/Ohm/V) (V) (V) (V) (V)
------------- ----------- --------- --------- --------- ---------
12V 49.910 12.810 11.590 12.249 12.231
12Vsb 1.750 12.600 11.400 12.057 12.047
PWOK 0.000 3.460 2.500 3.270 3.278
Vin_Good 0.000 3.460 ********* 3.263 0.065
SMBAlert 0.000 3.460 ********* 3.258 3.255
STEP.583(UUT Test seq.583) : I2C Read Status Multi_S6(90Vac -->0Vac - 10ms- PASS
Adderss :B0
Command Page00 :060200
Command Page01 :060201
Status Word :79
Status Byte :78
Status VOUT :7A
Status IOUT :7B
Status INPUT :7C
Status TEMPERATURE :7D
Status CML :7E
Status FANS :81
---------------------------------
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
----------------------------------
Word_Page_00 : 0
Word_Page_01 : 0
Status_Byte_P00 : 0
Status_Byte_P01 : 0
Status_VOUT_P00 : 0
Status_VOUT_P01 : 0
Status_IOUT_P00 : 0
Status_IOUT_P01 : 0
Status_INPUT_P00 : 0
Status_INPUT_P01 : 0
Status_TEM_P00 : 0
Status_TEM_P01 : 0
Status_CML_P00 : 0
Status_CML_P01 : 0
Status_FANS_P00 : 0
Status_FANS_P01 : 0
STEP.584(UUT Test seq.584) : AC_DC Line Sag Surge 80611N-2_Multi_S2(90Vac - PASS
ElapsedTime (S)= 1'357
Vin (V)= 90.00
Fin (Hz)= 47.00
Delay Time (ms)= 500.00
Drop Time (ms)= 10.00
Drop Recovery Time(ms)= 500.00
Drop Voltage (v)= 0.00
Drop Frequency (Hz)= 47.00
Repeat Count = 1
Degree =315
Duty cycle (%)= 100.000000
Load Loading Vpk Max Vpk Min Vpk High Vpk Low
Name (A/Ohm/V) (V) (V) (V) (V)
------------- ----------- --------- --------- --------- ---------
12V 49.910 12.810 11.590 12.249 12.231
12Vsb 1.750 12.600 11.400 12.057 12.047
PWOK 0.000 3.460 2.500 3.270 3.277
Vin_Good 0.000 3.460 ********* 3.264 0.063
SMBAlert 0.000 3.460 ********* 3.257 3.255
STEP.585(UUT Test seq.585) : I2C Read Status Multi_S6(90Vac -->0Vac - 10ms- PASS
Adderss :B0
Command Page00 :060200
Command Page01 :060201
Status Word :79
Status Byte :78
Status VOUT :7A
Status IOUT :7B
Status INPUT :7C
Status TEMPERATURE :7D
Status CML :7E
Status FANS :81
---------------------------------
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
----------------------------------
Word_Page_00 : 0
Word_Page_01 : 0
Status_Byte_P00 : 0
Status_Byte_P01 : 0
Status_VOUT_P00 : 0
Status_VOUT_P01 : 0
Status_IOUT_P00 : 0
Status_IOUT_P01 : 0
Status_INPUT_P00 : 0
Status_INPUT_P01 : 0
Status_TEM_P00 : 0
Status_TEM_P01 : 0
Status_CML_P00 : 0
Status_CML_P01 : 0
Status_FANS_P00 : 0
Status_FANS_P01 : 0
STEP.586(UUT Test seq.586) : AC Source ON/OFF(input source)_Multi_S2 ---- ( PASS
(The Report Format of this Sequence was not found)
STEP.587(UUT Test seq.587) : Set Input Condition_Load_S4 ---- (0'000) ----- PASS
Vin (V)= 100.000
Fin (Hz)= 60.000
Load Loading
Name (A/Ohm/V)
------------- ----------
12V 55.6500
12Vsb 1.7500
PWOK 0.0000
Vin_Good 0.0000
SMBAlert 0.0000
STEP.588(UUT Test seq.588) : Set Drop Time ---- (0'000) ------------------- PASS
Drop Time= 10
STEP.589(UUT Test seq.589) : AC_DC Line Sag Surge 80611N-2_Multi_S2(100Vac PASS
ElapsedTime (S)= 3'900
Vin (V)= 100.00
Fin (Hz)= 60.00
Delay Time (ms)= 3000.00
Drop Time (ms)= 10.00
Drop Recovery Time(ms)= 500.00
Drop Voltage (v)= 0.00
Drop Frequency (Hz)= 60.00
Repeat Count = 1
Degree = 0
Duty cycle (%)= 100.000000
Load Loading Vpk Max Vpk Min Vpk High Vpk Low
Name (A/Ohm/V) (V) (V) (V) (V)
------------- ----------- --------- --------- --------- ---------
12V 55.650 12.810 11.590 12.245 12.224
12Vsb 1.750 12.600 11.400 12.055 12.046
PWOK 0.000 3.460 2.500 3.269 3.275
Vin_Good 0.000 3.460 ********* 3.263 0.064
SMBAlert 0.000 3.460 ********* 3.258 3.257
STEP.590(UUT Test seq.590) : I2C Read Status Multi_S6(100Vac -->0Vac - 10ms PASS
Adderss :B0
Command Page00 :060200
Command Page01 :060201
Status Word :79
Status Byte :78
Status VOUT :7A
Status IOUT :7B
Status INPUT :7C
Status TEMPERATURE :7D
Status CML :7E
Status FANS :81
---------------------------------
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
----------------------------------
Word_Page_00 : 0
Word_Page_01 : 0
Status_Byte_P00 : 0
Status_Byte_P01 : 0
Status_VOUT_P00 : 0
Status_VOUT_P01 : 0
Status_IOUT_P00 : 0
Status_IOUT_P01 : 0
Status_INPUT_P00 : 0
Status_INPUT_P01 : 0
Status_TEM_P00 : 0
Status_TEM_P01 : 0
Status_CML_P00 : 0
Status_CML_P01 : 0
Status_FANS_P00 : 0
Status_FANS_P01 : 0
STEP.591(UUT Test seq.591) : AC_DC Line Sag Surge 80611N-2_Multi_S2(100Vac PASS
ElapsedTime (S)= 1'404
Vin (V)= 100.00
Fin (Hz)= 60.00
Delay Time (ms)= 500.00
Drop Time (ms)= 10.00
Drop Recovery Time(ms)= 500.00
Drop Voltage (v)= 0.00
Drop Frequency (Hz)= 60.00
Repeat Count = 1
Degree = 45
Duty cycle (%)= 100.000000
Load Loading Vpk Max Vpk Min Vpk High Vpk Low
Name (A/Ohm/V) (V) (V) (V) (V)
------------- ----------- --------- --------- --------- ---------
12V 55.650 12.810 11.590 12.247 12.226
12Vsb 1.750 12.600 11.400 12.055 12.046
PWOK 0.000 3.460 2.500 3.270 3.274
Vin_Good 0.000 3.460 ********* 3.262 0.064
SMBAlert 0.000 3.460 ********* 3.258 3.257
STEP.592(UUT Test seq.592) : I2C Read Status Multi_S6(100Vac -->0Vac - 10ms PASS
Adderss :B0
Command Page00 :060200
Command Page01 :060201
Status Word :79
Status Byte :78
Status VOUT :7A
Status IOUT :7B
Status INPUT :7C
Status TEMPERATURE :7D
Status CML :7E
Status FANS :81
---------------------------------
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
----------------------------------
Word_Page_00 : 0
Word_Page_01 : 0
Status_Byte_P00 : 0
Status_Byte_P01 : 0
Status_VOUT_P00 : 0
Status_VOUT_P01 : 0
Status_IOUT_P00 : 0
Status_IOUT_P01 : 0
Status_INPUT_P00 : 0
Status_INPUT_P01 : 0
Status_TEM_P00 : 0
Status_TEM_P01 : 0
Status_CML_P00 : 0
Status_CML_P01 : 0
Status_FANS_P00 : 0
Status_FANS_P01 : 0
STEP.593(UUT Test seq.593) : AC_DC Line Sag Surge 80611N-2_Multi_S2(100Vac PASS
ElapsedTime (S)= 1'357
Vin (V)= 100.00
Fin (Hz)= 60.00
Delay Time (ms)= 500.00
Drop Time (ms)= 10.00
Drop Recovery Time(ms)= 500.00
Drop Voltage (v)= 0.00
Drop Frequency (Hz)= 60.00
Repeat Count = 1
Degree = 90
Duty cycle (%)= 100.000000
Load Loading Vpk Max Vpk Min Vpk High Vpk Low
Name (A/Ohm/V) (V) (V) (V) (V)
------------- ----------- --------- --------- --------- ---------
12V 55.650 12.810 11.590 12.245 12.227
12Vsb 1.750 12.600 11.400 12.055 12.046
PWOK 0.000 3.460 2.500 3.269 3.277
Vin_Good 0.000 3.460 ********* 3.262 0.061
SMBAlert 0.000 3.460 ********* 3.257 3.257
STEP.594(UUT Test seq.594) : I2C Read Status Multi_S6(100Vac -->0Vac - 10ms PASS
Adderss :B0
Command Page00 :060200
Command Page01 :060201
Status Word :79
Status Byte :78
Status VOUT :7A
Status IOUT :7B
Status INPUT :7C
Status TEMPERATURE :7D
Status CML :7E
Status FANS :81
---------------------------------
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
----------------------------------
Word_Page_00 : 0
Word_Page_01 : 0
Status_Byte_P00 : 0
Status_Byte_P01 : 0
Status_VOUT_P00 : 0
Status_VOUT_P01 : 0
Status_IOUT_P00 : 0
Status_IOUT_P01 : 0
Status_INPUT_P00 : 0
Status_INPUT_P01 : 0
Status_TEM_P00 : 0
Status_TEM_P01 : 0
Status_CML_P00 : 0
Status_CML_P01 : 0
Status_FANS_P00 : 0
Status_FANS_P01 : 0
STEP.595(UUT Test seq.595) : AC_DC Line Sag Surge 80611N-2_Multi_S2(100Vac PASS
ElapsedTime (S)= 1'342
Vin (V)= 100.00
Fin (Hz)= 60.00
Delay Time (ms)= 500.00
Drop Time (ms)= 10.00
Drop Recovery Time(ms)= 500.00
Drop Voltage (v)= 0.00
Drop Frequency (Hz)= 60.00
Repeat Count = 1
Degree =135
Duty cycle (%)= 100.000000
Load Loading Vpk Max Vpk Min Vpk High Vpk Low
Name (A/Ohm/V) (V) (V) (V) (V)
------------- ----------- --------- --------- --------- ---------
12V 55.650 12.810 11.590 12.245 12.226
12Vsb 1.750 12.600 11.400 12.057 12.047
PWOK 0.000 3.460 2.500 3.268 3.277
Vin_Good 0.000 3.460 ********* 3.263 0.062
SMBAlert 0.000 3.460 ********* 3.259 3.257
STEP.596(UUT Test seq.596) : I2C Read Status Multi_S6(100Vac -->0Vac - 10ms PASS
Adderss :B0
Command Page00 :060200
Command Page01 :060201
Status Word :79
Status Byte :78
Status VOUT :7A
Status IOUT :7B
Status INPUT :7C
Status TEMPERATURE :7D
Status CML :7E
Status FANS :81
---------------------------------
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
----------------------------------
Word_Page_00 : 0
Word_Page_01 : 0
Status_Byte_P00 : 0
Status_Byte_P01 : 0
Status_VOUT_P00 : 0
Status_VOUT_P01 : 0
Status_IOUT_P00 : 0
Status_IOUT_P01 : 0
Status_INPUT_P00 : 0
Status_INPUT_P01 : 0
Status_TEM_P00 : 0
Status_TEM_P01 : 0
Status_CML_P00 : 0
Status_CML_P01 : 0
Status_FANS_P00 : 0
Status_FANS_P01 : 0
STEP.597(UUT Test seq.597) : AC_DC Line Sag Surge 80611N-2_Multi_S2(100Vac PASS
ElapsedTime (S)= 1'388
Vin (V)= 100.00
Fin (Hz)= 60.00
Delay Time (ms)= 500.00
Drop Time (ms)= 10.00
Drop Recovery Time(ms)= 500.00
Drop Voltage (v)= 0.00
Drop Frequency (Hz)= 60.00
Repeat Count = 1
Degree =225
Duty cycle (%)= 100.000000
Load Loading Vpk Max Vpk Min Vpk High Vpk Low
Name (A/Ohm/V) (V) (V) (V) (V)
------------- ----------- --------- --------- --------- ---------
12V 55.650 12.810 11.590 12.247 12.227
12Vsb 1.750 12.600 11.400 12.057 12.046
PWOK 0.000 3.460 2.500 3.269 3.275
Vin_Good 0.000 3.460 ********* 3.263 0.065
SMBAlert 0.000 3.460 ********* 3.258 3.257
STEP.598(UUT Test seq.598) : I2C Read Status Multi_S6(100Vac -->0Vac - 10ms PASS
Adderss :B0
Command Page00 :060200
Command Page01 :060201
Status Word :79
Status Byte :78
Status VOUT :7A
Status IOUT :7B
Status INPUT :7C
Status TEMPERATURE :7D
Status CML :7E
Status FANS :81
---------------------------------
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
----------------------------------
Word_Page_00 : 0
Word_Page_01 : 0
Status_Byte_P00 : 0
Status_Byte_P01 : 0
Status_VOUT_P00 : 0
Status_VOUT_P01 : 0
Status_IOUT_P00 : 0
Status_IOUT_P01 : 0
Status_INPUT_P00 : 0
Status_INPUT_P01 : 0
Status_TEM_P00 : 0
Status_TEM_P01 : 0
Status_CML_P00 : 0
Status_CML_P01 : 0
Status_FANS_P00 : 0
Status_FANS_P01 : 0
STEP.599(UUT Test seq.599) : AC_DC Line Sag Surge 80611N-2_Multi_S2(100Vac PASS
ElapsedTime (S)= 1'342
Vin (V)= 100.00
Fin (Hz)= 60.00
Delay Time (ms)= 500.00
Drop Time (ms)= 10.00
Drop Recovery Time(ms)= 500.00
Drop Voltage (v)= 0.00
Drop Frequency (Hz)= 60.00
Repeat Count = 1
Degree =270
Duty cycle (%)= 100.000000
Load Loading Vpk Max Vpk Min Vpk High Vpk Low
Name (A/Ohm/V) (V) (V) (V) (V)
------------- ----------- --------- --------- --------- ---------
12V 55.650 12.810 11.590 12.247 12.227
12Vsb 1.750 12.600 11.400 12.057 12.047
PWOK 0.000 3.460 2.500 3.270 3.275
Vin_Good 0.000 3.460 ********* 3.263 0.062
SMBAlert 0.000 3.460 ********* 3.257 3.257
STEP.600(UUT Test seq.600) : I2C Read Status Multi_S6(100Vac -->0Vac - 10ms PASS
Adderss :B0
Command Page00 :060200
Command Page01 :060201
Status Word :79
Status Byte :78
Status VOUT :7A
Status IOUT :7B
Status INPUT :7C
Status TEMPERATURE :7D
Status CML :7E
Status FANS :81
---------------------------------
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
----------------------------------
Word_Page_00 : 0
Word_Page_01 : 0
Status_Byte_P00 : 0
Status_Byte_P01 : 0
Status_VOUT_P00 : 0
Status_VOUT_P01 : 0
Status_IOUT_P00 : 0
Status_IOUT_P01 : 0
Status_INPUT_P00 : 0
Status_INPUT_P01 : 0
Status_TEM_P00 : 0
Status_TEM_P01 : 0
Status_CML_P00 : 0
Status_CML_P01 : 0
Status_FANS_P00 : 0
Status_FANS_P01 : 0
STEP.601(UUT Test seq.601) : AC_DC Line Sag Surge 80611N-2_Multi_S2(100Vac PASS
ElapsedTime (S)= 1'357
Vin (V)= 100.00
Fin (Hz)= 60.00
Delay Time (ms)= 500.00
Drop Time (ms)= 10.00
Drop Recovery Time(ms)= 500.00
Drop Voltage (v)= 0.00
Drop Frequency (Hz)= 60.00
Repeat Count = 1
Degree =315
Duty cycle (%)= 100.000000
Load Loading Vpk Max Vpk Min Vpk High Vpk Low
Name (A/Ohm/V) (V) (V) (V) (V)
------------- ----------- --------- --------- --------- ---------
12V 55.650 12.810 11.590 12.247 12.226
12Vsb 1.750 12.600 11.400 12.057 12.047
PWOK 0.000 3.460 2.500 3.269 3.275
Vin_Good 0.000 3.460 ********* 3.263 0.065
SMBAlert 0.000 3.460 ********* 3.258 3.258
STEP.602(UUT Test seq.602) : I2C Read Status Multi_S6(100Vac -->0Vac - 10ms PASS
Adderss :B0
Command Page00 :060200
Command Page01 :060201
Status Word :79
Status Byte :78
Status VOUT :7A
Status IOUT :7B
Status INPUT :7C
Status TEMPERATURE :7D
Status CML :7E
Status FANS :81
---------------------------------
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
----------------------------------
Word_Page_00 : 0
Word_Page_01 : 0
Status_Byte_P00 : 0
Status_Byte_P01 : 0
Status_VOUT_P00 : 0
Status_VOUT_P01 : 0
Status_IOUT_P00 : 0
Status_IOUT_P01 : 0
Status_INPUT_P00 : 0
Status_INPUT_P01 : 0
Status_TEM_P00 : 0
Status_TEM_P01 : 0
Status_CML_P00 : 0
Status_CML_P01 : 0
Status_FANS_P00 : 0
Status_FANS_P01 : 0
STEP.603(UUT Test seq.603) : AC Source ON/OFF(input source)_Multi_S2 ---- ( PASS
(The Report Format of this Sequence was not found)
STEP.604(UUT Test seq.604) : Set Input Condition_Load_S4 ---- (0'000) ----- PASS
Vin (V)= 180.000
Fin (Hz)= 47.000
Load Loading
Name (A/Ohm/V)
------------- ----------
12V 90.0900
12Vsb 1.7500
PWOK 0.0000
Vin_Good 0.0000
SMBAlert 0.0000
STEP.605(UUT Test seq.605) : Set Drop Time ---- (0'000) ------------------- PASS
Drop Time= 10
STEP.606(UUT Test seq.606) : AC_DC Line Sag Surge 80611N-2_Multi_S2(180Vac PASS
ElapsedTime (S)= 3'931
Vin (V)= 180.00
Fin (Hz)= 47.00
Delay Time (ms)= 3000.00
Drop Time (ms)= 10.00
Drop Recovery Time(ms)= 500.00
Drop Voltage (v)= 0.00
Drop Frequency (Hz)= 47.00
Repeat Count = 1
Degree = 0
Duty cycle (%)= 100.000000
Load Loading Vpk Max Vpk Min Vpk High Vpk Low
Name (A/Ohm/V) (V) (V) (V) (V)
------------- ----------- --------- --------- --------- ---------
12V 90.090 12.810 11.590 12.225 12.204
12Vsb 1.750 12.600 11.400 12.052 12.042
PWOK 0.000 3.460 2.500 3.264 3.272
Vin_Good 0.000 3.460 ********* 3.257 0.057
SMBAlert 0.000 3.460 ********* 3.260 3.259
STEP.607(UUT Test seq.607) : I2C Read Status Multi_S6(180Vac -->0Vac - 10ms PASS
Adderss :B0
Command Page00 :060200
Command Page01 :060201
Status Word :79
Status Byte :78
Status VOUT :7A
Status IOUT :7B
Status INPUT :7C
Status TEMPERATURE :7D
Status CML :7E
Status FANS :81
---------------------------------
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
----------------------------------
Word_Page_00 : 0
Word_Page_01 : 0
Status_Byte_P00 : 0
Status_Byte_P01 : 0
Status_VOUT_P00 : 0
Status_VOUT_P01 : 0
Status_IOUT_P00 : 0
Status_IOUT_P01 : 0
Status_INPUT_P00 : 0
Status_INPUT_P01 : 0
Status_TEM_P00 : 0
Status_TEM_P01 : 0
Status_CML_P00 : 0
Status_CML_P01 : 0
Status_FANS_P00 : 0
Status_FANS_P01 : 0
STEP.608(UUT Test seq.608) : AC_DC Line Sag Surge 80611N-2_Multi_S2(180Vac PASS
ElapsedTime (S)= 1'358
Vin (V)= 180.00
Fin (Hz)= 47.00
Delay Time (ms)= 500.00
Drop Time (ms)= 10.00
Drop Recovery Time(ms)= 500.00
Drop Voltage (v)= 0.00
Drop Frequency (Hz)= 47.00
Repeat Count = 1
Degree = 45
Duty cycle (%)= 100.000000
Load Loading Vpk Max Vpk Min Vpk High Vpk Low
Name (A/Ohm/V) (V) (V) (V) (V)
------------- ----------- --------- --------- --------- ---------
12V 90.090 12.810 11.590 12.225 12.205
12Vsb 1.750 12.600 11.400 12.051 12.043
PWOK 0.000 3.460 2.500 3.264 3.271
Vin_Good 0.000 3.460 ********* 3.260 0.060
SMBAlert 0.000 3.460 ********* 3.260 3.258
STEP.609(UUT Test seq.609) : I2C Read Status Multi_S6(180Vac -->0Vac - 10ms PASS
Adderss :B0
Command Page00 :060200
Command Page01 :060201
Status Word :79
Status Byte :78
Status VOUT :7A
Status IOUT :7B
Status INPUT :7C
Status TEMPERATURE :7D
Status CML :7E
Status FANS :81
---------------------------------
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
----------------------------------
Word_Page_00 : 0
Word_Page_01 : 0
Status_Byte_P00 : 0
Status_Byte_P01 : 0
Status_VOUT_P00 : 0
Status_VOUT_P01 : 0
Status_IOUT_P00 : 0
Status_IOUT_P01 : 0
Status_INPUT_P00 : 0
Status_INPUT_P01 : 0
Status_TEM_P00 : 0
Status_TEM_P01 : 0
Status_CML_P00 : 0
Status_CML_P01 : 0
Status_FANS_P00 : 0
Status_FANS_P01 : 0
STEP.610(UUT Test seq.610) : AC_DC Line Sag Surge 80611N-2_Multi_S2(180Vac PASS
ElapsedTime (S)= 1'389
Vin (V)= 180.00
Fin (Hz)= 47.00
Delay Time (ms)= 500.00
Drop Time (ms)= 10.00
Drop Recovery Time(ms)= 500.00
Drop Voltage (v)= 0.00
Drop Frequency (Hz)= 47.00
Repeat Count = 1
Degree = 90
Duty cycle (%)= 100.000000
Load Loading Vpk Max Vpk Min Vpk High Vpk Low
Name (A/Ohm/V) (V) (V) (V) (V)
------------- ----------- --------- --------- --------- ---------
12V 90.090 12.810 11.590 12.224 12.204
12Vsb 1.750 12.600 11.400 12.052 12.044
PWOK 0.000 3.460 2.500 3.264 3.271
Vin_Good 0.000 3.460 ********* 3.260 0.060
SMBAlert 0.000 3.460 ********* 3.260 3.258
STEP.611(UUT Test seq.611) : I2C Read Status Multi_S6(180Vac -->0Vac - 10ms PASS
Adderss :B0
Command Page00 :060200
Command Page01 :060201
Status Word :79
Status Byte :78
Status VOUT :7A
Status IOUT :7B
Status INPUT :7C
Status TEMPERATURE :7D
Status CML :7E
Status FANS :81
---------------------------------
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
----------------------------------
Word_Page_00 : 0
Word_Page_01 : 0
Status_Byte_P00 : 0
Status_Byte_P01 : 0
Status_VOUT_P00 : 0
Status_VOUT_P01 : 0
Status_IOUT_P00 : 0
Status_IOUT_P01 : 0
Status_INPUT_P00 : 0
Status_INPUT_P01 : 0
Status_TEM_P00 : 0
Status_TEM_P01 : 0
Status_CML_P00 : 0
Status_CML_P01 : 0
Status_FANS_P00 : 0
Status_FANS_P01 : 0
STEP.612(UUT Test seq.612) : AC_DC Line Sag Surge 80611N-2_Multi_S2(180Vac PASS
ElapsedTime (S)= 1'373
Vin (V)= 180.00
Fin (Hz)= 47.00
Delay Time (ms)= 500.00
Drop Time (ms)= 10.00
Drop Recovery Time(ms)= 500.00
Drop Voltage (v)= 0.00
Drop Frequency (Hz)= 47.00
Repeat Count = 1
Degree =135
Duty cycle (%)= 100.000000
Load Loading Vpk Max Vpk Min Vpk High Vpk Low
Name (A/Ohm/V) (V) (V) (V) (V)
------------- ----------- --------- --------- --------- ---------
12V 90.090 12.810 11.590 12.225 12.205
12Vsb 1.750 12.600 11.400 12.052 12.043
PWOK 0.000 3.460 2.500 3.265 3.271
Vin_Good 0.000 3.460 ********* 3.259 0.061
SMBAlert 0.000 3.460 ********* 3.260 3.259
STEP.613(UUT Test seq.613) : I2C Read Status Multi_S6(180Vac -->0Vac - 10ms PASS
Adderss :B0
Command Page00 :060200
Command Page01 :060201
Status Word :79
Status Byte :78
Status VOUT :7A
Status IOUT :7B
Status INPUT :7C
Status TEMPERATURE :7D
Status CML :7E
Status FANS :81
---------------------------------
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
----------------------------------
Word_Page_00 : 0
Word_Page_01 : 0
Status_Byte_P00 : 0
Status_Byte_P01 : 0
Status_VOUT_P00 : 0
Status_VOUT_P01 : 0
Status_IOUT_P00 : 0
Status_IOUT_P01 : 0
Status_INPUT_P00 : 0
Status_INPUT_P01 : 0
Status_TEM_P00 : 0
Status_TEM_P01 : 0
Status_CML_P00 : 0
Status_CML_P01 : 0
Status_FANS_P00 : 0
Status_FANS_P01 : 0
STEP.614(UUT Test seq.614) : AC_DC Line Sag Surge 80611N-2_Multi_S2(180Vac PASS
ElapsedTime (S)= 1'279
Vin (V)= 180.00
Fin (Hz)= 47.00
Delay Time (ms)= 500.00
Drop Time (ms)= 10.00
Drop Recovery Time(ms)= 500.00
Drop Voltage (v)= 0.00
Drop Frequency (Hz)= 47.00
Repeat Count = 1
Degree =225
Duty cycle (%)= 100.000000
Load Loading Vpk Max Vpk Min Vpk High Vpk Low
Name (A/Ohm/V) (V) (V) (V) (V)
------------- ----------- --------- --------- --------- ---------
12V 90.090 12.810 11.590 12.225 12.205
12Vsb 1.750 12.600 11.400 12.051 12.042
PWOK 0.000 3.460 2.500 3.266 3.272
Vin_Good 0.000 3.460 ********* 3.259 0.059
SMBAlert 0.000 3.460 ********* 3.260 3.260
STEP.615(UUT Test seq.615) : I2C Read Status Multi_S6(180Vac -->0Vac - 10ms PASS
Adderss :B0
Command Page00 :060200
Command Page01 :060201
Status Word :79
Status Byte :78
Status VOUT :7A
Status IOUT :7B
Status INPUT :7C
Status TEMPERATURE :7D
Status CML :7E
Status FANS :81
---------------------------------
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
----------------------------------
Word_Page_00 : 0
Word_Page_01 : 0
Status_Byte_P00 : 0
Status_Byte_P01 : 0
Status_VOUT_P00 : 0
Status_VOUT_P01 : 0
Status_IOUT_P00 : 0
Status_IOUT_P01 : 0
Status_INPUT_P00 : 0
Status_INPUT_P01 : 0
Status_TEM_P00 : 0
Status_TEM_P01 : 0
Status_CML_P00 : 0
Status_CML_P01 : 0
Status_FANS_P00 : 0
Status_FANS_P01 : 0
STEP.616(UUT Test seq.616) : AC_DC Line Sag Surge 80611N-2_Multi_S2(180Vac PASS
ElapsedTime (S)= 1'357
Vin (V)= 180.00
Fin (Hz)= 47.00
Delay Time (ms)= 500.00
Drop Time (ms)= 10.00
Drop Recovery Time(ms)= 500.00
Drop Voltage (v)= 0.00
Drop Frequency (Hz)= 47.00
Repeat Count = 1
Degree =270
Duty cycle (%)= 100.000000
Load Loading Vpk Max Vpk Min Vpk High Vpk Low
Name (A/Ohm/V) (V) (V) (V) (V)
------------- ----------- --------- --------- --------- ---------
12V 90.090 12.810 11.590 12.225 12.205
12Vsb 1.750 12.600 11.400 12.051 12.044
PWOK 0.000 3.460 2.500 3.264 3.271
Vin_Good 0.000 3.460 ********* 3.259 0.058
SMBAlert 0.000 3.460 ********* 3.260 3.258
STEP.617(UUT Test seq.617) : I2C Read Status Multi_S6(180Vac -->0Vac - 10ms PASS
Adderss :B0
Command Page00 :060200
Command Page01 :060201
Status Word :79
Status Byte :78
Status VOUT :7A
Status IOUT :7B
Status INPUT :7C
Status TEMPERATURE :7D
Status CML :7E
Status FANS :81
---------------------------------
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
----------------------------------
Word_Page_00 : 0
Word_Page_01 : 0
Status_Byte_P00 : 0
Status_Byte_P01 : 0
Status_VOUT_P00 : 0
Status_VOUT_P01 : 0
Status_IOUT_P00 : 0
Status_IOUT_P01 : 0
Status_INPUT_P00 : 0
Status_INPUT_P01 : 0
Status_TEM_P00 : 0
Status_TEM_P01 : 0
Status_CML_P00 : 0
Status_CML_P01 : 0
Status_FANS_P00 : 0
Status_FANS_P01 : 0
STEP.618(UUT Test seq.618) : AC_DC Line Sag Surge 80611N-2_Multi_S2(180Vac PASS
ElapsedTime (S)= 1'404
Vin (V)= 180.00
Fin (Hz)= 47.00
Delay Time (ms)= 500.00
Drop Time (ms)= 10.00
Drop Recovery Time(ms)= 500.00
Drop Voltage (v)= 0.00
Drop Frequency (Hz)= 47.00
Repeat Count = 1
Degree =315
Duty cycle (%)= 100.000000
Load Loading Vpk Max Vpk Min Vpk High Vpk Low
Name (A/Ohm/V) (V) (V) (V) (V)
------------- ----------- --------- --------- --------- ---------
12V 90.090 12.810 11.590 12.224 12.205
12Vsb 1.750 12.600 11.400 12.050 12.043
PWOK 0.000 3.460 2.500 3.265 3.272
Vin_Good 0.000 3.460 ********* 3.259 0.061
SMBAlert 0.000 3.460 ********* 3.260 3.258
STEP.619(UUT Test seq.619) : I2C Read Status Multi_S6(180Vac -->0Vac - 10ms PASS
Adderss :B0
Command Page00 :060200
Command Page01 :060201
Status Word :79
Status Byte :78
Status VOUT :7A
Status IOUT :7B
Status INPUT :7C
Status TEMPERATURE :7D
Status CML :7E
Status FANS :81
---------------------------------
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
----------------------------------
Word_Page_00 : 0
Word_Page_01 : 0
Status_Byte_P00 : 0
Status_Byte_P01 : 0
Status_VOUT_P00 : 0
Status_VOUT_P01 : 0
Status_IOUT_P00 : 0
Status_IOUT_P01 : 0
Status_INPUT_P00 : 0
Status_INPUT_P01 : 0
Status_TEM_P00 : 0
Status_TEM_P01 : 0
Status_CML_P00 : 0
Status_CML_P01 : 0
Status_FANS_P00 : 0
Status_FANS_P01 : 0
STEP.620(UUT Test seq.620) : AC Source ON/OFF(input source)_Multi_S2 ---- ( PASS
(The Report Format of this Sequence was not found)
STEP.621(UUT Test seq.621) : Set Input Condition_Load_S4 ---- (0'016) ----- PASS
Vin (V)= 200.000
Fin (Hz)= 50.000
Load Loading
Name (A/Ohm/V)
------------- ----------
12V 101.5700
12Vsb 1.7500
PWOK 0.0000
Vin_Good 0.0000
SMBAlert 0.0000
STEP.622(UUT Test seq.622) : Set Drop Time ---- (0'000) ------------------- PASS
Drop Time= 10
STEP.623(UUT Test seq.623) : AC_DC Line Sag Surge 80611N-2_Multi_S2(200Vac PASS
ElapsedTime (S)= 3'884
Vin (V)= 200.00
Fin (Hz)= 50.00
Delay Time (ms)= 3000.00
Drop Time (ms)= 10.00
Drop Recovery Time(ms)= 500.00
Drop Voltage (v)= 0.00
Drop Frequency (Hz)= 50.00
Repeat Count = 1
Degree = 0
Duty cycle (%)= 100.000000
Load Loading Vpk Max Vpk Min Vpk High Vpk Low
Name (A/Ohm/V) (V) (V) (V) (V)
------------- ----------- --------- --------- --------- ---------
12V 101.570 12.810 11.590 12.217 12.197
12Vsb 1.750 12.600 11.400 12.049 12.041
PWOK 0.000 3.460 2.500 3.263 3.269
Vin_Good 0.000 3.460 ********* 3.256 0.058
SMBAlert 0.000 3.460 ********* 3.260 3.259
STEP.624(UUT Test seq.624) : I2C Read Status Multi_S6(200Vac -->0Vac - 10ms PASS
Adderss :B0
Command Page00 :060200
Command Page01 :060201
Status Word :79
Status Byte :78
Status VOUT :7A
Status IOUT :7B
Status INPUT :7C
Status TEMPERATURE :7D
Status CML :7E
Status FANS :81
---------------------------------
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
----------------------------------
Word_Page_00 : 0
Word_Page_01 : 0
Status_Byte_P00 : 0
Status_Byte_P01 : 0
Status_VOUT_P00 : 0
Status_VOUT_P01 : 0
Status_IOUT_P00 : 0
Status_IOUT_P01 : 0
Status_INPUT_P00 : 0
Status_INPUT_P01 : 0
Status_TEM_P00 : 0
Status_TEM_P01 : 0
Status_CML_P00 : 0
Status_CML_P01 : 0
Status_FANS_P00 : 0
Status_FANS_P01 : 0
STEP.625(UUT Test seq.625) : AC_DC Line Sag Surge 80611N-2_Multi_S2(200Vac PASS
ElapsedTime (S)= 1'264
Vin (V)= 200.00
Fin (Hz)= 50.00
Delay Time (ms)= 500.00
Drop Time (ms)= 10.00
Drop Recovery Time(ms)= 500.00
Drop Voltage (v)= 0.00
Drop Frequency (Hz)= 50.00
Repeat Count = 1
Degree = 45
Duty cycle (%)= 100.000000
Load Loading Vpk Max Vpk Min Vpk High Vpk Low
Name (A/Ohm/V) (V) (V) (V) (V)
------------- ----------- --------- --------- --------- ---------
12V 101.570 12.810 11.590 12.217 12.197
12Vsb 1.750 12.600 11.400 12.051 12.043
PWOK 0.000 3.460 2.500 3.263 3.269
Vin_Good 0.000 3.460 ********* 3.256 0.056
SMBAlert 0.000 3.460 ********* 3.260 3.258
STEP.626(UUT Test seq.626) : I2C Read Status Multi_S6(200Vac -->0Vac - 10ms PASS
Adderss :B0
Command Page00 :060200
Command Page01 :060201
Status Word :79
Status Byte :78
Status VOUT :7A
Status IOUT :7B
Status INPUT :7C
Status TEMPERATURE :7D
Status CML :7E
Status FANS :81
---------------------------------
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
----------------------------------
Word_Page_00 : 0
Word_Page_01 : 0
Status_Byte_P00 : 0
Status_Byte_P01 : 0
Status_VOUT_P00 : 0
Status_VOUT_P01 : 0
Status_IOUT_P00 : 0
Status_IOUT_P01 : 0
Status_INPUT_P00 : 0
Status_INPUT_P01 : 0
Status_TEM_P00 : 0
Status_TEM_P01 : 0
Status_CML_P00 : 0
Status_CML_P01 : 0
Status_FANS_P00 : 0
Status_FANS_P01 : 0
STEP.627(UUT Test seq.627) : AC_DC Line Sag Surge 80611N-2_Multi_S2(200Vac PASS
ElapsedTime (S)= 1'357
Vin (V)= 200.00
Fin (Hz)= 50.00
Delay Time (ms)= 500.00
Drop Time (ms)= 10.00
Drop Recovery Time(ms)= 500.00
Drop Voltage (v)= 0.00
Drop Frequency (Hz)= 50.00
Repeat Count = 1
Degree = 90
Duty cycle (%)= 100.000000
Load Loading Vpk Max Vpk Min Vpk High Vpk Low
Name (A/Ohm/V) (V) (V) (V) (V)
------------- ----------- --------- --------- --------- ---------
12V 101.570 12.810 11.590 12.217 12.198
12Vsb 1.750 12.600 11.400 12.050 12.042
PWOK 0.000 3.460 2.500 3.263 3.270
Vin_Good 0.000 3.460 ********* 3.257 0.060
SMBAlert 0.000 3.460 ********* 3.260 3.260
STEP.628(UUT Test seq.628) : I2C Read Status Multi_S6(200Vac -->0Vac - 10ms PASS
Adderss :B0
Command Page00 :060200
Command Page01 :060201
Status Word :79
Status Byte :78
Status VOUT :7A
Status IOUT :7B
Status INPUT :7C
Status TEMPERATURE :7D
Status CML :7E
Status FANS :81
---------------------------------
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
----------------------------------
Word_Page_00 : 0
Word_Page_01 : 0
Status_Byte_P00 : 0
Status_Byte_P01 : 0
Status_VOUT_P00 : 0
Status_VOUT_P01 : 0
Status_IOUT_P00 : 0
Status_IOUT_P01 : 0
Status_INPUT_P00 : 0
Status_INPUT_P01 : 0
Status_TEM_P00 : 0
Status_TEM_P01 : 0
Status_CML_P00 : 0
Status_CML_P01 : 0
Status_FANS_P00 : 0
Status_FANS_P01 : 0
STEP.629(UUT Test seq.629) : AC_DC Line Sag Surge 80611N-2_Multi_S2(200Vac PASS
ElapsedTime (S)= 1'388
Vin (V)= 200.00
Fin (Hz)= 50.00
Delay Time (ms)= 500.00
Drop Time (ms)= 10.00
Drop Recovery Time(ms)= 500.00
Drop Voltage (v)= 0.00
Drop Frequency (Hz)= 50.00
Repeat Count = 1
Degree =135
Duty cycle (%)= 100.000000
Load Loading Vpk Max Vpk Min Vpk High Vpk Low
Name (A/Ohm/V) (V) (V) (V) (V)
------------- ----------- --------- --------- --------- ---------
12V 101.570 12.810 11.590 12.218 12.198
12Vsb 1.750 12.600 11.400 12.050 12.043
PWOK 0.000 3.460 2.500 3.263 3.271
Vin_Good 0.000 3.460 ********* 3.257 0.058
SMBAlert 0.000 3.460 ********* 3.260 3.260
STEP.630(UUT Test seq.630) : I2C Read Status Multi_S6(200Vac -->0Vac - 10ms PASS
Adderss :B0
Command Page00 :060200
Command Page01 :060201
Status Word :79
Status Byte :78
Status VOUT :7A
Status IOUT :7B
Status INPUT :7C
Status TEMPERATURE :7D
Status CML :7E
Status FANS :81
---------------------------------
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
----------------------------------
Word_Page_00 : 0
Word_Page_01 : 0
Status_Byte_P00 : 0
Status_Byte_P01 : 0
Status_VOUT_P00 : 0
Status_VOUT_P01 : 0
Status_IOUT_P00 : 0
Status_IOUT_P01 : 0
Status_INPUT_P00 : 0
Status_INPUT_P01 : 0
Status_TEM_P00 : 0
Status_TEM_P01 : 0
Status_CML_P00 : 0
Status_CML_P01 : 0
Status_FANS_P00 : 0
Status_FANS_P01 : 0
STEP.631(UUT Test seq.631) : AC_DC Line Sag Surge 80611N-2_Multi_S2(200Vac PASS
ElapsedTime (S)= 1'373
Vin (V)= 200.00
Fin (Hz)= 50.00
Delay Time (ms)= 500.00
Drop Time (ms)= 10.00
Drop Recovery Time(ms)= 500.00
Drop Voltage (v)= 0.00
Drop Frequency (Hz)= 50.00
Repeat Count = 1
Degree =225
Duty cycle (%)= 100.000000
Load Loading Vpk Max Vpk Min Vpk High Vpk Low
Name (A/Ohm/V) (V) (V) (V) (V)
------------- ----------- --------- --------- --------- ---------
12V 101.570 12.810 11.590 12.217 12.198
12Vsb 1.750 12.600 11.400 12.050 12.042
PWOK 0.000 3.460 2.500 3.263 3.271
Vin_Good 0.000 3.460 ********* 3.256 0.056
SMBAlert 0.000 3.460 ********* 3.260 3.259
STEP.632(UUT Test seq.632) : I2C Read Status Multi_S6(200Vac -->0Vac - 10ms PASS
Adderss :B0
Command Page00 :060200
Command Page01 :060201
Status Word :79
Status Byte :78
Status VOUT :7A
Status IOUT :7B
Status INPUT :7C
Status TEMPERATURE :7D
Status CML :7E
Status FANS :81
---------------------------------
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
----------------------------------
Word_Page_00 : 0
Word_Page_01 : 0
Status_Byte_P00 : 0
Status_Byte_P01 : 0
Status_VOUT_P00 : 0
Status_VOUT_P01 : 0
Status_IOUT_P00 : 0
Status_IOUT_P01 : 0
Status_INPUT_P00 : 0
Status_INPUT_P01 : 0
Status_TEM_P00 : 0
Status_TEM_P01 : 0
Status_CML_P00 : 0
Status_CML_P01 : 0
Status_FANS_P00 : 0
Status_FANS_P01 : 0
STEP.633(UUT Test seq.633) : AC_DC Line Sag Surge 80611N-2_Multi_S2(200Vac PASS
ElapsedTime (S)= 1'388
Vin (V)= 200.00
Fin (Hz)= 50.00
Delay Time (ms)= 500.00
Drop Time (ms)= 10.00
Drop Recovery Time(ms)= 500.00
Drop Voltage (v)= 0.00
Drop Frequency (Hz)= 50.00
Repeat Count = 1
Degree =270
Duty cycle (%)= 100.000000
Load Loading Vpk Max Vpk Min Vpk High Vpk Low
Name (A/Ohm/V) (V) (V) (V) (V)
------------- ----------- --------- --------- --------- ---------
12V 101.570 12.810 11.590 12.217 12.200
12Vsb 1.750 12.600 11.400 12.050 12.042
PWOK 0.000 3.460 2.500 3.263 3.270
Vin_Good 0.000 3.460 ********* 3.257 0.056
SMBAlert 0.000 3.460 ********* 3.260 3.258
STEP.634(UUT Test seq.634) : I2C Read Status Multi_S6(200Vac -->0Vac - 10ms PASS
Adderss :B0
Command Page00 :060200
Command Page01 :060201
Status Word :79
Status Byte :78
Status VOUT :7A
Status IOUT :7B
Status INPUT :7C
Status TEMPERATURE :7D
Status CML :7E
Status FANS :81
---------------------------------
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
----------------------------------
Word_Page_00 : 0
Word_Page_01 : 0
Status_Byte_P00 : 0
Status_Byte_P01 : 0
Status_VOUT_P00 : 0
Status_VOUT_P01 : 0
Status_IOUT_P00 : 0
Status_IOUT_P01 : 0
Status_INPUT_P00 : 0
Status_INPUT_P01 : 0
Status_TEM_P00 : 0
Status_TEM_P01 : 0
Status_CML_P00 : 0
Status_CML_P01 : 0
Status_FANS_P00 : 0
Status_FANS_P01 : 0
STEP.635(UUT Test seq.635) : AC_DC Line Sag Surge 80611N-2_Multi_S2(200Vac PASS
ElapsedTime (S)= 1'342
Vin (V)= 200.00
Fin (Hz)= 50.00
Delay Time (ms)= 500.00
Drop Time (ms)= 10.00
Drop Recovery Time(ms)= 500.00
Drop Voltage (v)= 0.00
Drop Frequency (Hz)= 50.00
Repeat Count = 1
Degree =315
Duty cycle (%)= 100.000000
Load Loading Vpk Max Vpk Min Vpk High Vpk Low
Name (A/Ohm/V) (V) (V) (V) (V)
------------- ----------- --------- --------- --------- ---------
12V 101.570 12.810 11.590 12.218 12.197
12Vsb 1.750 12.600 11.400 12.049 12.043
PWOK 0.000 3.460 2.500 3.263 3.270
Vin_Good 0.000 3.460 ********* 3.257 0.055
SMBAlert 0.000 3.460 ********* 3.260 3.259
STEP.636(UUT Test seq.636) : I2C Read Status Multi_S6(200Vac -->0Vac - 10ms PASS
Adderss :B0
Command Page00 :060200
Command Page01 :060201
Status Word :79
Status Byte :78
Status VOUT :7A
Status IOUT :7B
Status INPUT :7C
Status TEMPERATURE :7D
Status CML :7E
Status FANS :81
---------------------------------
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
----------------------------------
Word_Page_00 : 0
Word_Page_01 : 0
Status_Byte_P00 : 0
Status_Byte_P01 : 0
Status_VOUT_P00 : 0
Status_VOUT_P01 : 0
Status_IOUT_P00 : 0
Status_IOUT_P01 : 0
Status_INPUT_P00 : 0
Status_INPUT_P01 : 0
Status_TEM_P00 : 0
Status_TEM_P01 : 0
Status_CML_P00 : 0
Status_CML_P01 : 0
Status_FANS_P00 : 0
Status_FANS_P01 : 0
STEP.637(UUT Test seq.637) : AC Source ON/OFF(input source)_Multi_S2 ---- ( PASS
(The Report Format of this Sequence was not found)
STEP.638(UUT Test seq.638) : Set Input Condition_Load_S4 ---- (0'015) ----- PASS
Vin (V)= 220.000
Fin (Hz)= 50.000
Load Loading
Name (A/Ohm/V)
------------- ----------
12V 113.0500
12Vsb 1.7500
PWOK 0.0000
Vin_Good 0.0000
SMBAlert 0.0000
STEP.639(UUT Test seq.639) : Set Drop Time ---- (0'000) ------------------- PASS
Drop Time= 10
STEP.640(UUT Test seq.640) : AC_DC Line Sag Surge 80611N-2_Multi_S2(220Vac PASS
ElapsedTime (S)= 3'869
Vin (V)= 220.00
Fin (Hz)= 50.00
Delay Time (ms)= 3000.00
Drop Time (ms)= 10.00
Drop Recovery Time(ms)= 500.00
Drop Voltage (v)= 0.00
Drop Frequency (Hz)= 50.00
Repeat Count = 1
Degree = 0
Duty cycle (%)= 100.000000
Load Loading Vpk Max Vpk Min Vpk High Vpk Low
Name (A/Ohm/V) (V) (V) (V) (V)
------------- ----------- --------- --------- --------- ---------
12V 113.050 12.810 11.590 12.209 12.190
12Vsb 1.750 12.600 11.400 12.049 12.040
PWOK 0.000 3.460 2.500 3.262 3.269
Vin_Good 0.000 3.460 ********* 3.255 0.056
SMBAlert 0.000 3.460 ********* 3.260 3.257
STEP.641(UUT Test seq.641) : I2C Read Status Multi_S6(220Vac -->0Vac - 10ms PASS
Adderss :B0
Command Page00 :060200
Command Page01 :060201
Status Word :79
Status Byte :78
Status VOUT :7A
Status IOUT :7B
Status INPUT :7C
Status TEMPERATURE :7D
Status CML :7E
Status FANS :81
---------------------------------
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
----------------------------------
Word_Page_00 : 0
Word_Page_01 : 0
Status_Byte_P00 : 0
Status_Byte_P01 : 0
Status_VOUT_P00 : 0
Status_VOUT_P01 : 0
Status_IOUT_P00 : 0
Status_IOUT_P01 : 0
Status_INPUT_P00 : 0
Status_INPUT_P01 : 0
Status_TEM_P00 : 0
Status_TEM_P01 : 0
Status_CML_P00 : 0
Status_CML_P01 : 0
Status_FANS_P00 : 0
Status_FANS_P01 : 0
STEP.642(UUT Test seq.642) : AC_DC Line Sag Surge 80611N-2_Multi_S2(220Vac PASS
ElapsedTime (S)= 1'373
Vin (V)= 220.00
Fin (Hz)= 50.00
Delay Time (ms)= 500.00
Drop Time (ms)= 10.00
Drop Recovery Time(ms)= 500.00
Drop Voltage (v)= 0.00
Drop Frequency (Hz)= 50.00
Repeat Count = 1
Degree = 45
Duty cycle (%)= 100.000000
Load Loading Vpk Max Vpk Min Vpk High Vpk Low
Name (A/Ohm/V) (V) (V) (V) (V)
------------- ----------- --------- --------- --------- ---------
12V 113.050 12.810 11.590 12.210 12.190
12Vsb 1.750 12.600 11.400 12.047 12.040
PWOK 0.000 3.460 2.500 3.261 3.270
Vin_Good 0.000 3.460 ********* 3.253 0.055
SMBAlert 0.000 3.460 ********* 3.262 3.259
STEP.643(UUT Test seq.643) : I2C Read Status Multi_S6(220Vac -->0Vac - 10ms PASS
Adderss :B0
Command Page00 :060200
Command Page01 :060201
Status Word :79
Status Byte :78
Status VOUT :7A
Status IOUT :7B
Status INPUT :7C
Status TEMPERATURE :7D
Status CML :7E
Status FANS :81
---------------------------------
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
----------------------------------
Word_Page_00 : 0
Word_Page_01 : 0
Status_Byte_P00 : 0
Status_Byte_P01 : 0
Status_VOUT_P00 : 0
Status_VOUT_P01 : 0
Status_IOUT_P00 : 0
Status_IOUT_P01 : 0
Status_INPUT_P00 : 0
Status_INPUT_P01 : 0
Status_TEM_P00 : 0
Status_TEM_P01 : 0
Status_CML_P00 : 0
Status_CML_P01 : 0
Status_FANS_P00 : 0
Status_FANS_P01 : 0
STEP.644(UUT Test seq.644) : AC_DC Line Sag Surge 80611N-2_Multi_S2(220Vac PASS
ElapsedTime (S)= 1'358
Vin (V)= 220.00
Fin (Hz)= 50.00
Delay Time (ms)= 500.00
Drop Time (ms)= 10.00
Drop Recovery Time(ms)= 500.00
Drop Voltage (v)= 0.00
Drop Frequency (Hz)= 50.00
Repeat Count = 1
Degree = 90
Duty cycle (%)= 100.000000
Load Loading Vpk Max Vpk Min Vpk High Vpk Low
Name (A/Ohm/V) (V) (V) (V) (V)
------------- ----------- --------- --------- --------- ---------
12V 113.050 12.810 11.590 12.209 12.191
12Vsb 1.750 12.600 11.400 12.049 12.041
PWOK 0.000 3.460 2.500 3.262 3.268
Vin_Good 0.000 3.460 ********* 3.255 0.052
SMBAlert 0.000 3.460 ********* 3.262 3.260
STEP.645(UUT Test seq.645) : I2C Read Status Multi_S6(220Vac -->0Vac - 10ms PASS
Adderss :B0
Command Page00 :060200
Command Page01 :060201
Status Word :79
Status Byte :78
Status VOUT :7A
Status IOUT :7B
Status INPUT :7C
Status TEMPERATURE :7D
Status CML :7E
Status FANS :81
---------------------------------
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
----------------------------------
Word_Page_00 : 0
Word_Page_01 : 0
Status_Byte_P00 : 0
Status_Byte_P01 : 0
Status_VOUT_P00 : 0
Status_VOUT_P01 : 0
Status_IOUT_P00 : 0
Status_IOUT_P01 : 0
Status_INPUT_P00 : 0
Status_INPUT_P01 : 0
Status_TEM_P00 : 0
Status_TEM_P01 : 0
Status_CML_P00 : 0
Status_CML_P01 : 0
Status_FANS_P00 : 0
Status_FANS_P01 : 0
STEP.646(UUT Test seq.646) : AC_DC Line Sag Surge 80611N-2_Multi_S2(220Vac PASS
ElapsedTime (S)= 1'357
Vin (V)= 220.00
Fin (Hz)= 50.00
Delay Time (ms)= 500.00
Drop Time (ms)= 10.00
Drop Recovery Time(ms)= 500.00
Drop Voltage (v)= 0.00
Drop Frequency (Hz)= 50.00
Repeat Count = 1
Degree =135
Duty cycle (%)= 100.000000
Load Loading Vpk Max Vpk Min Vpk High Vpk Low
Name (A/Ohm/V) (V) (V) (V) (V)
------------- ----------- --------- --------- --------- ---------
12V 113.050 12.810 11.590 12.210 12.190
12Vsb 1.750 12.600 11.400 12.050 12.041
PWOK 0.000 3.460 2.500 3.261 3.269
Vin_Good 0.000 3.460 ********* 3.254 0.056
SMBAlert 0.000 3.460 ********* 3.262 3.260
STEP.647(UUT Test seq.647) : I2C Read Status Multi_S6(220Vac -->0Vac - 10ms PASS
Adderss :B0
Command Page00 :060200
Command Page01 :060201
Status Word :79
Status Byte :78
Status VOUT :7A
Status IOUT :7B
Status INPUT :7C
Status TEMPERATURE :7D
Status CML :7E
Status FANS :81
---------------------------------
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
----------------------------------
Word_Page_00 : 0
Word_Page_01 : 0
Status_Byte_P00 : 0
Status_Byte_P01 : 0
Status_VOUT_P00 : 0
Status_VOUT_P01 : 0
Status_IOUT_P00 : 0
Status_IOUT_P01 : 0
Status_INPUT_P00 : 0
Status_INPUT_P01 : 0
Status_TEM_P00 : 0
Status_TEM_P01 : 0
Status_CML_P00 : 0
Status_CML_P01 : 0
Status_FANS_P00 : 0
Status_FANS_P01 : 0
STEP.648(UUT Test seq.648) : AC_DC Line Sag Surge 80611N-2_Multi_S2(220Vac PASS
ElapsedTime (S)= 1'404
Vin (V)= 220.00
Fin (Hz)= 50.00
Delay Time (ms)= 500.00
Drop Time (ms)= 10.00
Drop Recovery Time(ms)= 500.00
Drop Voltage (v)= 0.00
Drop Frequency (Hz)= 50.00
Repeat Count = 1
Degree =225
Duty cycle (%)= 100.000000
Load Loading Vpk Max Vpk Min Vpk High Vpk Low
Name (A/Ohm/V) (V) (V) (V) (V)
------------- ----------- --------- --------- --------- ---------
12V 113.050 12.810 11.590 12.210 12.191
12Vsb 1.750 12.600 11.400 12.049 12.042
PWOK 0.000 3.460 2.500 3.261 3.268
Vin_Good 0.000 3.460 ********* 3.254 0.054
SMBAlert 0.000 3.460 ********* 3.263 3.261
STEP.649(UUT Test seq.649) : I2C Read Status Multi_S6(220Vac -->0Vac - 10ms PASS
Adderss :B0
Command Page00 :060200
Command Page01 :060201
Status Word :79
Status Byte :78
Status VOUT :7A
Status IOUT :7B
Status INPUT :7C
Status TEMPERATURE :7D
Status CML :7E
Status FANS :81
---------------------------------
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
----------------------------------
Word_Page_00 : 0
Word_Page_01 : 0
Status_Byte_P00 : 0
Status_Byte_P01 : 0
Status_VOUT_P00 : 0
Status_VOUT_P01 : 0
Status_IOUT_P00 : 0
Status_IOUT_P01 : 0
Status_INPUT_P00 : 0
Status_INPUT_P01 : 0
Status_TEM_P00 : 0
Status_TEM_P01 : 0
Status_CML_P00 : 0
Status_CML_P01 : 0
Status_FANS_P00 : 0
Status_FANS_P01 : 0
STEP.650(UUT Test seq.650) : AC_DC Line Sag Surge 80611N-2_Multi_S2(220Vac PASS
ElapsedTime (S)= 1'373
Vin (V)= 220.00
Fin (Hz)= 50.00
Delay Time (ms)= 500.00
Drop Time (ms)= 10.00
Drop Recovery Time(ms)= 500.00
Drop Voltage (v)= 0.00
Drop Frequency (Hz)= 50.00
Repeat Count = 1
Degree =270
Duty cycle (%)= 100.000000
Load Loading Vpk Max Vpk Min Vpk High Vpk Low
Name (A/Ohm/V) (V) (V) (V) (V)
------------- ----------- --------- --------- --------- ---------
12V 113.050 12.810 11.590 12.210 12.190
12Vsb 1.750 12.600 11.400 12.049 12.041
PWOK 0.000 3.460 2.500 3.261 3.269
Vin_Good 0.000 3.460 ********* 3.254 0.056
SMBAlert 0.000 3.460 ********* 3.262 3.260
STEP.651(UUT Test seq.651) : I2C Read Status Multi_S6(220Vac -->0Vac - 10ms PASS
Adderss :B0
Command Page00 :060200
Command Page01 :060201
Status Word :79
Status Byte :78
Status VOUT :7A
Status IOUT :7B
Status INPUT :7C
Status TEMPERATURE :7D
Status CML :7E
Status FANS :81
---------------------------------
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
----------------------------------
Word_Page_00 : 0
Word_Page_01 : 0
Status_Byte_P00 : 0
Status_Byte_P01 : 0
Status_VOUT_P00 : 0
Status_VOUT_P01 : 0
Status_IOUT_P00 : 0
Status_IOUT_P01 : 0
Status_INPUT_P00 : 0
Status_INPUT_P01 : 0
Status_TEM_P00 : 0
Status_TEM_P01 : 0
Status_CML_P00 : 0
Status_CML_P01 : 0
Status_FANS_P00 : 0
Status_FANS_P01 : 0
STEP.652(UUT Test seq.652) : AC_DC Line Sag Surge 80611N-2_Multi_S2(220Vac PASS
ElapsedTime (S)= 1'373
Vin (V)= 220.00
Fin (Hz)= 50.00
Delay Time (ms)= 500.00
Drop Time (ms)= 10.00
Drop Recovery Time(ms)= 500.00
Drop Voltage (v)= 0.00
Drop Frequency (Hz)= 50.00
Repeat Count = 1
Degree =315
Duty cycle (%)= 100.000000
Load Loading Vpk Max Vpk Min Vpk High Vpk Low
Name (A/Ohm/V) (V) (V) (V) (V)
------------- ----------- --------- --------- --------- ---------
12V 113.050 12.810 11.590 12.211 12.190
12Vsb 1.750 12.600 11.400 12.049 12.040
PWOK 0.000 3.460 2.500 3.261 3.268
Vin_Good 0.000 3.460 ********* 3.255 0.056
SMBAlert 0.000 3.460 ********* 3.260 3.260
STEP.653(UUT Test seq.653) : I2C Read Status Multi_S6(220Vac -->0Vac - 10ms PASS
Adderss :B0
Command Page00 :060200
Command Page01 :060201
Status Word :79
Status Byte :78
Status VOUT :7A
Status IOUT :7B
Status INPUT :7C
Status TEMPERATURE :7D
Status CML :7E
Status FANS :81
---------------------------------
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
----------------------------------
Word_Page_00 : 0
Word_Page_01 : 0
Status_Byte_P00 : 0
Status_Byte_P01 : 0
Status_VOUT_P00 : 0
Status_VOUT_P01 : 0
Status_IOUT_P00 : 0
Status_IOUT_P01 : 0
Status_INPUT_P00 : 0
Status_INPUT_P01 : 0
Status_TEM_P00 : 0
Status_TEM_P01 : 0
Status_CML_P00 : 0
Status_CML_P01 : 0
Status_FANS_P00 : 0
Status_FANS_P01 : 0
STEP.654(UUT Test seq.654) : AC Source ON/OFF(input source)_Multi_S2 ---- ( PASS
(The Report Format of this Sequence was not found)
STEP.655(UUT Test seq.655) : Set Input Condition_Load_S4 ---- (0'000) ----- PASS
Vin (V)= 264.000
Fin (Hz)= 63.000
Load Loading
Name (A/Ohm/V)
------------- ----------
12V 113.0500
12Vsb 1.7500
PWOK 0.0000
Vin_Good 0.0000
SMBAlert 0.0000
STEP.656(UUT Test seq.656) : Set Drop Time ---- (0'000) ------------------- PASS
Drop Time= 10
STEP.657(UUT Test seq.657) : AC_DC Line Sag Surge 80611N-2_Multi_S2(264Vac PASS
ElapsedTime (S)= 3'931
Vin (V)= 264.00
Fin (Hz)= 63.00
Delay Time (ms)= 3000.00
Drop Time (ms)= 10.00
Drop Recovery Time(ms)= 500.00
Drop Voltage (v)= 0.00
Drop Frequency (Hz)= 63.00
Repeat Count = 1
Degree = 0
Duty cycle (%)= 100.000000
Load Loading Vpk Max Vpk Min Vpk High Vpk Low
Name (A/Ohm/V) (V) (V) (V) (V)
------------- ----------- --------- --------- --------- ---------
12V 113.050 12.810 11.590 12.210 12.189
12Vsb 1.750 12.600 11.400 12.049 12.038
PWOK 0.000 3.460 2.500 3.260 3.268
Vin_Good 0.000 3.460 ********* 3.254 0.056
SMBAlert 0.000 3.460 ********* 3.260 3.260
STEP.658(UUT Test seq.658) : I2C Read Status Multi_S6(264Vac -->0Vac - 10ms PASS
Adderss :B0
Command Page00 :060200
Command Page01 :060201
Status Word :79
Status Byte :78
Status VOUT :7A
Status IOUT :7B
Status INPUT :7C
Status TEMPERATURE :7D
Status CML :7E
Status FANS :81
---------------------------------
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
----------------------------------
Word_Page_00 : 0
Word_Page_01 : 0
Status_Byte_P00 : 0
Status_Byte_P01 : 0
Status_VOUT_P00 : 0
Status_VOUT_P01 : 0
Status_IOUT_P00 : 0
Status_IOUT_P01 : 0
Status_INPUT_P00 : 0
Status_INPUT_P01 : 0
Status_TEM_P00 : 0
Status_TEM_P01 : 0
Status_CML_P00 : 0
Status_CML_P01 : 0
Status_FANS_P00 : 0
Status_FANS_P01 : 0
STEP.659(UUT Test seq.659) : AC_DC Line Sag Surge 80611N-2_Multi_S2(264Vac PASS
ElapsedTime (S)= 1'420
Vin (V)= 264.00
Fin (Hz)= 63.00
Delay Time (ms)= 500.00
Drop Time (ms)= 10.00
Drop Recovery Time(ms)= 500.00
Drop Voltage (v)= 0.00
Drop Frequency (Hz)= 63.00
Repeat Count = 1
Degree = 45
Duty cycle (%)= 100.000000
Load Loading Vpk Max Vpk Min Vpk High Vpk Low
Name (A/Ohm/V) (V) (V) (V) (V)
------------- ----------- --------- --------- --------- ---------
12V 113.050 12.810 11.590 12.209 12.190
12Vsb 1.750 12.600 11.400 12.049 12.041
PWOK 0.000 3.460 2.500 3.261 3.268
Vin_Good 0.000 3.460 ********* 3.255 0.055
SMBAlert 0.000 3.460 ********* 3.260 3.260
STEP.660(UUT Test seq.660) : I2C Read Status Multi_S6(264Vac -->0Vac - 10ms PASS
Adderss :B0
Command Page00 :060200
Command Page01 :060201
Status Word :79
Status Byte :78
Status VOUT :7A
Status IOUT :7B
Status INPUT :7C
Status TEMPERATURE :7D
Status CML :7E
Status FANS :81
---------------------------------
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
----------------------------------
Word_Page_00 : 0
Word_Page_01 : 0
Status_Byte_P00 : 0
Status_Byte_P01 : 0
Status_VOUT_P00 : 0
Status_VOUT_P01 : 0
Status_IOUT_P00 : 0
Status_IOUT_P01 : 0
Status_INPUT_P00 : 0
Status_INPUT_P01 : 0
Status_TEM_P00 : 0
Status_TEM_P01 : 0
Status_CML_P00 : 0
Status_CML_P01 : 0
Status_FANS_P00 : 0
Status_FANS_P01 : 0
STEP.661(UUT Test seq.661) : AC_DC Line Sag Surge 80611N-2_Multi_S2(264Vac PASS
ElapsedTime (S)= 1'388
Vin (V)= 264.00
Fin (Hz)= 63.00
Delay Time (ms)= 500.00
Drop Time (ms)= 10.00
Drop Recovery Time(ms)= 500.00
Drop Voltage (v)= 0.00
Drop Frequency (Hz)= 63.00
Repeat Count = 1
Degree = 90
Duty cycle (%)= 100.000000
Load Loading Vpk Max Vpk Min Vpk High Vpk Low
Name (A/Ohm/V) (V) (V) (V) (V)
------------- ----------- --------- --------- --------- ---------
12V 113.050 12.810 11.590 12.209 12.190
12Vsb 1.750 12.600 11.400 12.049 12.041
PWOK 0.000 3.460 2.500 3.260 3.268
Vin_Good 0.000 3.460 ********* 3.253 0.055
SMBAlert 0.000 3.460 ********* 3.262 3.260
STEP.662(UUT Test seq.662) : I2C Read Status Multi_S6(264Vac -->0Vac - 10ms PASS
Adderss :B0
Command Page00 :060200
Command Page01 :060201
Status Word :79
Status Byte :78
Status VOUT :7A
Status IOUT :7B
Status INPUT :7C
Status TEMPERATURE :7D
Status CML :7E
Status FANS :81
---------------------------------
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
----------------------------------
Word_Page_00 : 0
Word_Page_01 : 0
Status_Byte_P00 : 0
Status_Byte_P01 : 0
Status_VOUT_P00 : 0
Status_VOUT_P01 : 0
Status_IOUT_P00 : 0
Status_IOUT_P01 : 0
Status_INPUT_P00 : 0
Status_INPUT_P01 : 0
Status_TEM_P00 : 0
Status_TEM_P01 : 0
Status_CML_P00 : 0
Status_CML_P01 : 0
Status_FANS_P00 : 0
Status_FANS_P01 : 0
STEP.663(UUT Test seq.663) : AC_DC Line Sag Surge 80611N-2_Multi_S2(264Vac PASS
ElapsedTime (S)= 1'373
Vin (V)= 264.00
Fin (Hz)= 63.00
Delay Time (ms)= 500.00
Drop Time (ms)= 10.00
Drop Recovery Time(ms)= 500.00
Drop Voltage (v)= 0.00
Drop Frequency (Hz)= 63.00
Repeat Count = 1
Degree =135
Duty cycle (%)= 100.000000
Load Loading Vpk Max Vpk Min Vpk High Vpk Low
Name (A/Ohm/V) (V) (V) (V) (V)
------------- ----------- --------- --------- --------- ---------
12V 113.050 12.810 11.590 12.209 12.191
12Vsb 1.750 12.600 11.400 12.049 12.041
PWOK 0.000 3.460 2.500 3.260 3.268
Vin_Good 0.000 3.460 ********* 3.254 0.056
SMBAlert 0.000 3.460 ********* 3.260 3.260
STEP.664(UUT Test seq.664) : I2C Read Status Multi_S6(264Vac -->0Vac - 10ms PASS
Adderss :B0
Command Page00 :060200
Command Page01 :060201
Status Word :79
Status Byte :78
Status VOUT :7A
Status IOUT :7B
Status INPUT :7C
Status TEMPERATURE :7D
Status CML :7E
Status FANS :81
---------------------------------
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
----------------------------------
Word_Page_00 : 0
Word_Page_01 : 0
Status_Byte_P00 : 0
Status_Byte_P01 : 0
Status_VOUT_P00 : 0
Status_VOUT_P01 : 0
Status_IOUT_P00 : 0
Status_IOUT_P01 : 0
Status_INPUT_P00 : 0
Status_INPUT_P01 : 0
Status_TEM_P00 : 0
Status_TEM_P01 : 0
Status_CML_P00 : 0
Status_CML_P01 : 0
Status_FANS_P00 : 0
Status_FANS_P01 : 0
STEP.665(UUT Test seq.665) : AC_DC Line Sag Surge 80611N-2_Multi_S2(264Vac PASS
ElapsedTime (S)= 1'326
Vin (V)= 264.00
Fin (Hz)= 63.00
Delay Time (ms)= 500.00
Drop Time (ms)= 10.00
Drop Recovery Time(ms)= 500.00
Drop Voltage (v)= 0.00
Drop Frequency (Hz)= 63.00
Repeat Count = 1
Degree =225
Duty cycle (%)= 100.000000
Load Loading Vpk Max Vpk Min Vpk High Vpk Low
Name (A/Ohm/V) (V) (V) (V) (V)
------------- ----------- --------- --------- --------- ---------
12V 113.050 12.810 11.590 12.210 12.190
12Vsb 1.750 12.600 11.400 12.049 12.040
PWOK 0.000 3.460 2.500 3.261 3.269
Vin_Good 0.000 3.460 ********* 3.255 0.052
SMBAlert 0.000 3.460 ********* 3.260 3.260
STEP.666(UUT Test seq.666) : I2C Read Status Multi_S6(264Vac -->0Vac - 10ms PASS
Adderss :B0
Command Page00 :060200
Command Page01 :060201
Status Word :79
Status Byte :78
Status VOUT :7A
Status IOUT :7B
Status INPUT :7C
Status TEMPERATURE :7D
Status CML :7E
Status FANS :81
---------------------------------
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
----------------------------------
Word_Page_00 : 0
Word_Page_01 : 0
Status_Byte_P00 : 0
Status_Byte_P01 : 0
Status_VOUT_P00 : 0
Status_VOUT_P01 : 0
Status_IOUT_P00 : 0
Status_IOUT_P01 : 0
Status_INPUT_P00 : 0
Status_INPUT_P01 : 0
Status_TEM_P00 : 0
Status_TEM_P01 : 0
Status_CML_P00 : 0
Status_CML_P01 : 0
Status_FANS_P00 : 0
Status_FANS_P01 : 0
STEP.667(UUT Test seq.667) : AC_DC Line Sag Surge 80611N-2_Multi_S2(264Vac PASS
ElapsedTime (S)= 1'357
Vin (V)= 264.00
Fin (Hz)= 63.00
Delay Time (ms)= 500.00
Drop Time (ms)= 10.00
Drop Recovery Time(ms)= 500.00
Drop Voltage (v)= 0.00
Drop Frequency (Hz)= 63.00
Repeat Count = 1
Degree =270
Duty cycle (%)= 100.000000
Load Loading Vpk Max Vpk Min Vpk High Vpk Low
Name (A/Ohm/V) (V) (V) (V) (V)
------------- ----------- --------- --------- --------- ---------
12V 113.050 12.810 11.590 12.209 12.191
12Vsb 1.750 12.600 11.400 12.049 12.041
PWOK 0.000 3.460 2.500 3.261 3.270
Vin_Good 0.000 3.460 ********* 3.254 0.054
SMBAlert 0.000 3.460 ********* 3.262 3.260
STEP.668(UUT Test seq.668) : I2C Read Status Multi_S6(264Vac -->0Vac - 10ms PASS
Adderss :B0
Command Page00 :060200
Command Page01 :060201
Status Word :79
Status Byte :78
Status VOUT :7A
Status IOUT :7B
Status INPUT :7C
Status TEMPERATURE :7D
Status CML :7E
Status FANS :81
---------------------------------
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
----------------------------------
Word_Page_00 : 0
Word_Page_01 : 0
Status_Byte_P00 : 0
Status_Byte_P01 : 0
Status_VOUT_P00 : 0
Status_VOUT_P01 : 0
Status_IOUT_P00 : 0
Status_IOUT_P01 : 0
Status_INPUT_P00 : 0
Status_INPUT_P01 : 0
Status_TEM_P00 : 0
Status_TEM_P01 : 0
Status_CML_P00 : 0
Status_CML_P01 : 0
Status_FANS_P00 : 0
Status_FANS_P01 : 0
STEP.669(UUT Test seq.669) : AC_DC Line Sag Surge 80611N-2_Multi_S2(264Vac PASS
ElapsedTime (S)= 1'342
Vin (V)= 264.00
Fin (Hz)= 63.00
Delay Time (ms)= 500.00
Drop Time (ms)= 10.00
Drop Recovery Time(ms)= 500.00
Drop Voltage (v)= 0.00
Drop Frequency (Hz)= 63.00
Repeat Count = 1
Degree =315
Duty cycle (%)= 100.000000
Load Loading Vpk Max Vpk Min Vpk High Vpk Low
Name (A/Ohm/V) (V) (V) (V) (V)
------------- ----------- --------- --------- --------- ---------
12V 113.050 12.810 11.590 12.209 12.190
12Vsb 1.750 12.600 11.400 12.047 12.040
PWOK 0.000 3.460 2.500 3.261 3.268
Vin_Good 0.000 3.460 ********* 3.254 0.054
SMBAlert 0.000 3.460 ********* 3.260 3.260
STEP.670(UUT Test seq.670) : I2C Read Status Multi_S6(264Vac -->0Vac - 10ms PASS
Adderss :B0
Command Page00 :060200
Command Page01 :060201
Status Word :79
Status Byte :78
Status VOUT :7A
Status IOUT :7B
Status INPUT :7C
Status TEMPERATURE :7D
Status CML :7E
Status FANS :81
---------------------------------
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
----------------------------------
Word_Page_00 : 0
Word_Page_01 : 0
Status_Byte_P00 : 0
Status_Byte_P01 : 0
Status_VOUT_P00 : 0
Status_VOUT_P01 : 0
Status_IOUT_P00 : 0
Status_IOUT_P01 : 0
Status_INPUT_P00 : 0
Status_INPUT_P01 : 0
Status_TEM_P00 : 0
Status_TEM_P01 : 0
Status_CML_P00 : 0
Status_CML_P01 : 0
Status_FANS_P00 : 0
Status_FANS_P01 : 0
STEP.671(UUT Test seq.671) : AC Source ON/OFF(input source)_Multi_S2 ---- ( PASS
(The Report Format of this Sequence was not found)
STEP.672(UUT Test seq.672) : AC Line Sag Surge 80611N-2_Multi_S5(115Vac --> PASS
ElapsedTime (S)= 4'430
Vin (V)= 115.00
Fin (Hz)= 60.00
Delay Time (ms)= 3000.00
Drop Time (ms)= 10.00
Drop Recovery Time(ms)= 1000.00
Drop Voltage (v)= 80.50
Drop Frequency (Hz)= 50.00
Repeat Count = 1
Degree = 0
Duty cycle (%)= 100.000000
Load Loading Vpk Max Vpk Min Vpk High Vpk Low
Name (A/Ohm/V) (V) (V) (V) (V)
------------- ----------- --------- --------- --------- ---------
12V 71.300 12.810 11.590 12.237 12.216
12Vsb 2.500 12.600 11.400 12.036 12.025
PWOK 0.000 3.460 2.500 3.267 3.275
Vin_Good 0.000 3.460 2.500 3.260 3.263
SMBAlert 0.000 3.460 2.500 3.259 3.257
STEP.673(UUT Test seq.673) : I2C Read Status Multi_S6(115Vac -->80.5Vac - 0 PASS
Adderss :B0
Command Page00 :060200
Command Page01 :060201
Status Word :79
Status Byte :78
Status VOUT :7A
Status IOUT :7B
Status INPUT :7C
Status TEMPERATURE :7D
Status CML :7E
Status FANS :81
---------------------------------
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
----------------------------------
Word_Page_00 : 0
Word_Page_01 : 0
Status_Byte_P00 : 0
Status_Byte_P01 : 0
Status_VOUT_P00 : 0
Status_VOUT_P01 : 0
Status_IOUT_P00 : 0
Status_IOUT_P01 : 0
Status_INPUT_P00 : 0
Status_INPUT_P01 : 0
Status_TEM_P00 : 0
Status_TEM_P01 : 0
Status_CML_P00 : 0
Status_CML_P01 : 0
Status_FANS_P00 : 0
Status_FANS_P01 : 0
STEP.674(UUT Test seq.674) : AC Line Sag Surge 80611N-2_Multi_S5(115Vac --> PASS
ElapsedTime (S)= 2'356
Vin (V)= 115.00
Fin (Hz)= 60.00
Delay Time (ms)= 1000.00
Drop Time (ms)= 10.00
Drop Recovery Time(ms)= 1000.00
Drop Voltage (v)= 149.50
Drop Frequency (Hz)= 50.00
Repeat Count = 1
Degree = 0
Duty cycle (%)= 100.000000
Load Loading Vpk Max Vpk Min Vpk High Vpk Low
Name (A/Ohm/V) (V) (V) (V) (V)
------------- ----------- --------- --------- --------- ---------
12V 79.500 12.810 11.590 12.232 12.211
12Vsb 2.500 12.600 11.400 12.036 12.024
PWOK 0.000 3.460 2.500 3.265 3.275
Vin_Good 0.000 3.460 2.500 3.259 3.262
SMBAlert 0.000 3.460 2.500 3.259 3.258
STEP.675(UUT Test seq.675) : I2C Read Status Multi_S6(115Vac -->149.5Vac - PASS
Adderss :B0
Command Page00 :060200
Command Page01 :060201
Status Word :79
Status Byte :78
Status VOUT :7A
Status IOUT :7B
Status INPUT :7C
Status TEMPERATURE :7D
Status CML :7E
Status FANS :81
---------------------------------
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
----------------------------------
Word_Page_00 : 0
Word_Page_01 : 0
Status_Byte_P00 : 0
Status_Byte_P01 : 0
Status_VOUT_P00 : 0
Status_VOUT_P01 : 0
Status_IOUT_P00 : 0
Status_IOUT_P01 : 0
Status_INPUT_P00 : 0
Status_INPUT_P01 : 0
Status_TEM_P00 : 0
Status_TEM_P01 : 0
Status_CML_P00 : 0
Status_CML_P01 : 0
Status_FANS_P00 : 0
Status_FANS_P01 : 0
STEP.676(UUT Test seq.676) : AC Source ON/OFF(input source)_Multi_S2 ---- ( PASS
(The Report Format of this Sequence was not found)
STEP.677(UUT Test seq.677) : AC Line Sag Surge 80611N-2_Multi_S5(220Vac --> PASS
ElapsedTime (S)= 4'056
Vin (V)= 220.00
Fin (Hz)= 50.00
Delay Time (ms)= 3000.00
Drop Time (ms)= 100.00
Drop Recovery Time(ms)= 500.00
Drop Voltage (v)= 253.00
Drop Frequency (Hz)= 50.00
Repeat Count = 1
Degree = 0
Duty cycle (%)= 100.000000
Load Loading Vpk Max Vpk Min Vpk High Vpk Low
Name (A/Ohm/V) (V) (V) (V) (V)
------------- ----------- --------- --------- --------- ---------
12V 161.500 12.810 11.590 12.179 12.160
12Vsb 2.500 12.600 11.400 12.025 12.016
PWOK 0.000 3.460 2.500 3.254 3.262
Vin_Good 0.000 3.460 2.500 3.247 3.248
SMBAlert 0.000 3.460 2.500 3.264 3.263
STEP.678(UUT Test seq.678) : I2C Read Status Multi_S6(220Vac -->253Vac - 10 PASS
Adderss :B0
Command Page00 :060200
Command Page01 :060201
Status Word :79
Status Byte :78
Status VOUT :7A
Status IOUT :7B
Status INPUT :7C
Status TEMPERATURE :7D
Status CML :7E
Status FANS :81
---------------------------------
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
----------------------------------
Word_Page_00 : 0
Word_Page_01 : 0
Status_Byte_P00 : 0
Status_Byte_P01 : 0
Status_VOUT_P00 : 0
Status_VOUT_P01 : 0
Status_IOUT_P00 : 0
Status_IOUT_P01 : 0
Status_INPUT_P00 : 0
Status_INPUT_P01 : 0
Status_TEM_P00 : 0
Status_TEM_P01 : 0
Status_CML_P00 : 0
Status_CML_P01 : 0
Status_FANS_P00 : 0
Status_FANS_P01 : 0
STEP.679(UUT Test seq.679) : AC Line Sag Surge 80611N-2_Multi_S5(220Vac --> PASS
ElapsedTime (S)= 2'543
Vin (V)= 220.00
Fin (Hz)= 50.00
Delay Time (ms)= 500.00
Drop Time (ms)= 10.00
Drop Recovery Time(ms)= 500.00
Drop Voltage (v)= 286.00
Drop Frequency (Hz)= 50.00
Repeat Count = 1
Degree = 0
Duty cycle (%)= 100.000000
Load Loading Vpk Max Vpk Min Vpk High Vpk Low
Name (A/Ohm/V) (V) (V) (V) (V)
------------- ----------- --------- --------- --------- ---------
12V 161.500 12.810 11.590 12.178 12.157
12Vsb 2.500 12.600 11.400 12.025 12.016
PWOK 0.000 3.460 2.500 3.253 3.263
Vin_Good 0.000 3.460 2.500 3.247 3.250
SMBAlert 0.000 3.460 2.500 3.264 3.262
STEP.680(UUT Test seq.680) : I2C Read Status Multi_S6(220Vac -->286Vac - 0. PASS
Adderss :B0
Command Page00 :060200
Command Page01 :060201
Status Word :79
Status Byte :78
Status VOUT :7A
Status IOUT :7B
Status INPUT :7C
Status TEMPERATURE :7D
Status CML :7E
Status FANS :81
---------------------------------
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
----------------------------------
Word_Page_00 : 0
Word_Page_01 : 0
Status_Byte_P00 : 0
Status_Byte_P01 : 0
Status_VOUT_P00 : 0
Status_VOUT_P01 : 0
Status_IOUT_P00 : 0
Status_IOUT_P01 : 0
Status_INPUT_P00 : 0
Status_INPUT_P01 : 0
Status_TEM_P00 : 0
Status_TEM_P01 : 0
Status_CML_P00 : 0
Status_CML_P01 : 0
Status_FANS_P00 : 0
Status_FANS_P01 : 0
STEP.681(UUT Test seq.681) : AC Line Sag Surge 80611N-2_Multi_S5(220Vac --> PASS
ElapsedTime (S)= 2'012
Vin (V)= 220.00
Fin (Hz)= 50.00
Delay Time (ms)= 1000.00
Drop Time (ms)= 100.00
Drop Recovery Time(ms)= 500.00
Drop Voltage (v)= 253.00
Drop Frequency (Hz)= 50.00
Repeat Count = 1
Degree = 0
Duty cycle (%)= 100.000000
Load Loading Vpk Max Vpk Min Vpk High Vpk Low
Name (A/Ohm/V) (V) (V) (V) (V)
------------- ----------- --------- --------- --------- ---------
12V 1.000 12.810 11.590 12.281 12.260
12Vsb 0.100 12.600 11.400 12.165 12.158
PWOK 0.000 3.460 2.500 3.278 3.287
Vin_Good 0.000 3.460 2.500 3.272 3.276
SMBAlert 0.000 3.460 2.500 3.255 3.253
STEP.682(UUT Test seq.682) : I2C Read Status Multi_S6(220Vac -->253Vac - 10 PASS
Adderss :B0
Command Page00 :060200
Command Page01 :060201
Status Word :79
Status Byte :78
Status VOUT :7A
Status IOUT :7B
Status INPUT :7C
Status TEMPERATURE :7D
Status CML :7E
Status FANS :81
---------------------------------
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
----------------------------------
Word_Page_00 : 0
Word_Page_01 : 0
Status_Byte_P00 : 0
Status_Byte_P01 : 0
Status_VOUT_P00 : 0
Status_VOUT_P01 : 0
Status_IOUT_P00 : 0
Status_IOUT_P01 : 0
Status_INPUT_P00 : 0
Status_INPUT_P01 : 0
Status_TEM_P00 : 0
Status_TEM_P01 : 0
Status_CML_P00 : 0
Status_CML_P01 : 0
Status_FANS_P00 : 0
Status_FANS_P01 : 0
STEP.683(UUT Test seq.683) : AC Line Sag Surge 80611N-2_Multi_S5(220Vac --> PASS
ElapsedTime (S)= 1'404
Vin (V)= 220.00
Fin (Hz)= 50.00
Delay Time (ms)= 500.00
Drop Time (ms)= 10.00
Drop Recovery Time(ms)= 500.00
Drop Voltage (v)= 286.00
Drop Frequency (Hz)= 50.00
Repeat Count = 1
Degree = 0
Duty cycle (%)= 100.000000
Load Loading Vpk Max Vpk Min Vpk High Vpk Low
Name (A/Ohm/V) (V) (V) (V) (V)
------------- ----------- --------- --------- --------- ---------
12V 1.000 12.810 11.590 12.283 12.259
12Vsb 0.100 12.600 11.400 12.161 12.157
PWOK 0.000 3.460 2.500 3.278 3.286
Vin_Good 0.000 3.460 2.500 3.271 3.275
SMBAlert 0.000 3.460 2.500 3.255 3.253
STEP.684(UUT Test seq.684) : I2C Read Status Multi_S6(220Vac -->286Vac - 0. PASS
Adderss :B0
Command Page00 :060200
Command Page01 :060201
Status Word :79
Status Byte :78
Status VOUT :7A
Status IOUT :7B
Status INPUT :7C
Status TEMPERATURE :7D
Status CML :7E
Status FANS :81
---------------------------------
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
----------------------------------
Word_Page_00 : 0
Word_Page_01 : 0
Status_Byte_P00 : 0
Status_Byte_P01 : 0
Status_VOUT_P00 : 0
Status_VOUT_P01 : 0
Status_IOUT_P00 : 0
Status_IOUT_P01 : 0
Status_INPUT_P00 : 0
Status_INPUT_P01 : 0
Status_TEM_P00 : 0
Status_TEM_P01 : 0
Status_CML_P00 : 0
Status_CML_P01 : 0
Status_FANS_P00 : 0
Status_FANS_P01 : 0
STEP.685(UUT Test seq.685) : UUT Off_Multi_S2 ---- (1'108) ---------------- PASS
STEP.686(UUT Test seq.686) : FAN Full Speed delay time Multi ---- (10'093) PASS
STEP.687(UUT Test seq.687) : FAN Speed Normal_Multi ---- (0'109) ---------- PASS
(The Report Format of this Sequence was not found)
STEP.688(UUT Test seq.688) : 61512 Ac Source ACDC Mode_Multi_S2 ---- (0'156 PASS
(The Report Format of this Sequence was not found)
STEP.689(UUT Test seq.689) : TTL & Relay Setup ---- (0'219) --------------- PASS
(The Report Format of this Sequence was not found)
STEP.690(UUT Test seq.690) : Input Output Accuracy Multi or Single_S3(230Va PASS
ElapsedTime (S)= 6'489
Vin (V)= 230.00
Fin (Hz)= 50.00
Delay Time (ms)= 5000.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 161.500 ******* ******* 161.497
12Vsb 2.500 ******* ******* 2.500
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
------------Load--------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V ******* ******* 0.000
12Vsb ******* ******* 0.000
PWOK ******* ******* 0.000
Vin_Good ******* ******* 0.000
SMBAlert ******* ******* 0.000
-------34970----------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 12.350 11.590 12.164
12VSb 12.600 11.400 11.994
PWOK 3.460 2.500 3.222
Vin_Good 3.460 2.500 3.225
SMBAlert 3.460 2.500 3.222
IBUS 8.200 7.800 8.001
CR 0.400 ******* -0.022
Max Min Reading
------------- ---------- ---------- ----------
Vrms (V) ******** ******** 229.4996
PF 1.0000 0.9900 0.9984
THDi (%) 5.0000 * 2.4353
Irms (A) 10.0000 ******** 9.6297
Pin (W) ******** ******** 2206.4348
Pout (W) ******** ******** 1994.4075
Eff (%) 99.0000 89.0000 90.3905
Load Noise Range Noise B.W
Name (V) (MHz)
------------- ----------- ---------
12V 2 20.000
12Vsb 2 20.000
PWOK 2 20.000
Vin_Good 2 20.000
SMBAlert 2 20.000
Load Vpp Noise Vpp Noise Vpp Noise
Name Max(mV) Min(mV) (mV)
------------- ------------ ------------ ------------
12V 120.000 0.000 15.430
12Vsb 120.000 0.000 16.050
PWOK ********* ********* 25.280
Vin_Good ********* ********* 24.430
SMBAlert ********* ********* 27.000
MCU Accuracy ---------------------------------------------
Spec Status Reading Status
----------- ------------- ----------------
Mcu Status 0 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Reading
-------- ---------
Vin_M 228.7500
Iin_M 9.6563
Pin_M 2216.0000
Vout_M 12.2012
Iout_M 161.2500
Pout_M 1968.0000
Max Min Reading
--------------------- --------- --------- ---------
Mcu_Vin_VS_Vin (%) 2.000 * 0.3266
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 * 0.2756
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 * 0.4335
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 * 0.3069
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 * 0.1529
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 * 0.1820
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Max Min Reading
-------------- --------- --------- ---------
Temperature 1 200.00 0.00 58.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Max Min Reading
-------------- --------- --------- ---------
Temperature 2 200.00 0.00 73.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Max Min Reading
-------- --------- --------- ---------
Fan RPM 28000 ****** 11115
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
STEP.691(UUT Test seq.691) : Harmonic Multi UUT_Test_S2 ---- (2'122) ------ PASS
Standard = 1 (1:IEC-1000-3-2, 2:Japan)
Class = 0 (0:A, 1:B, 2:C, 3:D, 4:A-1)
Delay Time (ms)= 2000
Load Loading
Name (A/Ohm/V)
------------- ----------
12V 161.500
12Vsb 2.500
PWOK 0.000
Vin_Good 0.000
SMBAlert 0.000
Max Min Reading
------------- --------- --------- ---------
Pin (W) ******* ******* 2207.60
THD (%) 5.00 ******* 2.37
Input Voltage Reading (V) = 229.48
Spectrum Limit Reading
------------- --------- ---------
1 ********* 9.643
2 1.080 0.036
3 2.300 0.212
4 0.430 0.005
5 1.140 0.040
6 0.300 0.010
7 0.770 0.043
8 0.230 0.008
9 0.400 0.039
10 0.184 0.011
11 0.330 0.026
12 0.153 0.004
13 0.210 0.021
14 0.131 0.003
15 0.150 0.016
16 0.115 0.004
17 0.132 0.001
18 0.102 0.003
19 0.118 0.003
20 0.092 0.005
21 0.107 0.002
22 0.084 0.004
23 0.098 0.006
24 0.077 0.004
25 0.090 0.009
26 0.071 0.010
27 0.083 0.015
28 0.066 0.008
29 0.078 0.020
30 0.061 0.012
31 0.073 0.017
32 0.058 0.005
33 0.068 0.018
34 0.054 0.003
35 0.064 0.017
36 0.051 0.004
37 0.061 0.020
38 0.048 0.006
39 0.058 0.026
40 0.046 0.011
STEP.692(UUT Test seq.692) : Input Output Accuracy Multi or Single_S3(230Va PASS
ElapsedTime (S)= 6'318
Vin (V)= 230.00
Fin (Hz)= 50.00
Delay Time (ms)= 5000.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 145.350 ******* ******* 145.347
12Vsb 2.250 ******* ******* 2.250
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
------------Load--------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V ******* ******* 0.000
12Vsb ******* ******* 0.000
PWOK ******* ******* 0.000
Vin_Good ******* ******* 0.000
SMBAlert ******* ******* 0.000
-------34970----------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 12.350 11.590 12.175
12VSb 12.600 11.400 12.003
PWOK 3.460 2.500 3.225
Vin_Good 3.460 2.500 3.229
SMBAlert 3.460 2.500 3.220
IBUS ******* ******* 7.193
CR 0.400 ******* -0.020
Max Min Reading
------------- ---------- ---------- ----------
Vrms (V) ******** ******** 229.5368
PF 1.0000 0.9800 0.9984
THDi (%) 8.0000 * 2.4590
Irms (A) ******** ******** 8.6363
Pin (W) ******** ******** 1979.2577
Pout (W) ******** ******** 1796.5977
Eff (%) 99.0000 ******** 90.7713
Load Noise Range Noise B.W
Name (V) (MHz)
------------- ----------- ---------
12V 2 20.000
12Vsb 2 20.000
PWOK 2 20.000
Vin_Good 2 20.000
SMBAlert 2 20.000
Load Vpp Noise Vpp Noise Vpp Noise
Name Max(mV) Min(mV) (mV)
------------- ------------ ------------ ------------
12V 120.000 0.000 14.720
12Vsb 120.000 0.000 13.960
PWOK ********* ********* 24.310
Vin_Good ********* ********* 23.770
SMBAlert ********* ********* 26.010
MCU Accuracy ---------------------------------------------
Spec Status Reading Status
----------- ------------- ----------------
Mcu Status 0 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Reading
-------- ---------
Vin_M 228.7500
Iin_M 8.6719
Pin_M 1988.0000
Vout_M 12.2070
Iout_M 145.2500
Pout_M 1772.0000
Max Min Reading
--------------------- --------- --------- ---------
Mcu_Vin_VS_Vin (%) 2.000 * 0.3428
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 * 0.4118
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 * 0.4417
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 * 0.2636
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 * 0.0667
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 * 0.1361
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Max Min Reading
-------------- --------- --------- ---------
Temperature 1 200.00 0.00 57.50
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Max Min Reading
-------------- --------- --------- ---------
Temperature 2 200.00 0.00 79.50
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Max Min Reading
-------- --------- --------- ---------
Fan RPM 28000 ****** 11116
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
STEP.693(UUT Test seq.693) : Harmonic Multi UUT_Test_S2 ---- (2'122) ------ PASS
Standard = 1 (1:IEC-1000-3-2, 2:Japan)
Class = 0 (0:A, 1:B, 2:C, 3:D, 4:A-1)
Delay Time (ms)= 2000
Load Loading
Name (A/Ohm/V)
------------- ----------
12V 145.350
12Vsb 2.250
PWOK 0.000
Vin_Good 0.000
SMBAlert 0.000
Max Min Reading
------------- --------- --------- ---------
Pin (W) ******* ******* 1979.69
THD (%) ******* ******* 2.50
Input Voltage Reading (V) = 229.54
Spectrum Limit Reading
------------- --------- ---------
1 ********* 8.627
2 1.080 0.018
3 2.300 0.193
4 0.430 0.007
5 1.140 0.045
6 0.300 0.004
7 0.770 0.028
8 0.230 0.013
9 0.400 0.036
10 0.184 0.007
11 0.330 0.030
12 0.153 0.005
13 0.210 0.021
14 0.131 0.006
15 0.150 0.019
16 0.115 0.012
17 0.132 0.011
18 0.102 0.004
19 0.118 0.009
20 0.092 0.005
21 0.107 0.005
22 0.084 0.003
23 0.098 0.003
24 0.077 0.007
25 0.090 0.007
26 0.071 0.006
27 0.083 0.006
28 0.066 0.002
29 0.078 0.007
30 0.061 0.011
31 0.073 0.009
32 0.058 0.002
33 0.068 0.014
34 0.054 0.008
35 0.064 0.024
36 0.051 0.008
37 0.061 0.019
38 0.048 0.004
39 0.058 0.023
40 0.046 0.004
STEP.694(UUT Test seq.694) : Input Output Accuracy Multi or Single_S3(230Va PASS
ElapsedTime (S)= 6'318
Vin (V)= 230.00
Fin (Hz)= 50.00
Delay Time (ms)= 5000.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 129.200 ******* ******* 129.197
12Vsb 2.000 ******* ******* 2.000
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
------------Load--------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V ******* ******* 0.000
12Vsb ******* ******* 0.000
PWOK ******* ******* 0.000
Vin_Good ******* ******* 0.000
SMBAlert ******* ******* 0.000
-------34970----------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 12.350 11.590 12.185
12VSb 12.600 11.400 12.011
PWOK 3.460 2.500 3.225
Vin_Good 3.460 2.500 3.229
SMBAlert 3.460 2.500 3.223
IBUS ******* ******* 6.385
CR 0.400 ******* -0.017
Max Min Reading
------------- ---------- ---------- ----------
Vrms (V) ******** ******** 229.6182
PF 1.0000 0.9800 0.9987
THDi (%) 8.0000 * 2.4413
Irms (A) ******** ******** 7.6465
Pin (W) ******** ******** 1753.4857
Pout (W) ******** ******** 1598.2297
Eff (%) 99.0000 ******** 91.1459
Load Noise Range Noise B.W
Name (V) (MHz)
------------- ----------- ---------
12V 2 20.000
12Vsb 2 20.000
PWOK 2 20.000
Vin_Good 2 20.000
SMBAlert 2 20.000
Load Vpp Noise Vpp Noise Vpp Noise
Name Max(mV) Min(mV) (mV)
------------- ------------ ------------ ------------
12V 120.000 0.000 14.260
12Vsb 120.000 0.000 13.190
PWOK ********* ********* 24.030
Vin_Good ********* ********* 23.790
SMBAlert ********* ********* 25.990
MCU Accuracy ---------------------------------------------
Spec Status Reading Status
----------- ------------- ----------------
Mcu Status 0 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Reading
-------- ---------
Vin_M 229.0000
Iin_M 7.6797
Pin_M 1758.0000
Vout_M 12.2129
Iout_M 129.0000
Pout_M 1576.0000
Max Min Reading
--------------------- --------- --------- ---------
Mcu_Vin_VS_Vin (%) 2.000 * 0.2692
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 * 0.4341
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 * 0.2574
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 * 0.2325
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 * 0.1525
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 * 0.1137
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Max Min Reading
-------------- --------- --------- ---------
Temperature 1 200.00 0.00 56.50
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Max Min Reading
-------------- --------- --------- ---------
Temperature 2 200.00 0.00 81.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Max Min Reading
-------- --------- --------- ---------
Fan RPM 28000 ****** 11115
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
STEP.695(UUT Test seq.695) : Harmonic Multi UUT_Test_S2 ---- (2'153) ------ PASS
Standard = 1 (1:IEC-1000-3-2, 2:Japan)
Class = 0 (0:A, 1:B, 2:C, 3:D, 4:A-1)
Delay Time (ms)= 2000
Load Loading
Name (A/Ohm/V)
------------- ----------
12V 129.200
12Vsb 2.000
PWOK 0.000
Vin_Good 0.000
SMBAlert 0.000
Max Min Reading
------------- --------- --------- ---------
Pin (W) ******* ******* 1753.59
THD (%) ******* ******* 2.54
Input Voltage Reading (V) = 229.62
Spectrum Limit Reading
------------- --------- ---------
1 ********* 7.631
2 1.080 0.005
3 2.300 0.174
4 0.430 0.006
5 1.140 0.048
6 0.300 0.005
7 0.770 0.030
8 0.230 0.005
9 0.400 0.026
10 0.184 0.005
11 0.330 0.021
12 0.153 0.004
13 0.210 0.011
14 0.131 0.004
15 0.150 0.007
16 0.115 0.004
17 0.132 0.005
18 0.102 0.005
19 0.118 0.003
20 0.092 0.006
21 0.107 0.001
22 0.084 0.002
23 0.098 0.006
24 0.077 0.005
25 0.090 0.006
26 0.071 0.003
27 0.083 0.013
28 0.066 0.003
29 0.078 0.011
30 0.061 0.005
31 0.073 0.018
32 0.058 0.004
33 0.068 0.007
34 0.054 0.005
35 0.064 0.013
36 0.051 0.003
37 0.061 0.015
38 0.048 0.003
39 0.058 0.021
40 0.046 0.001
STEP.696(UUT Test seq.696) : Input Output Accuracy Multi or Single_S3(230Va PASS
ElapsedTime (S)= 6'256
Vin (V)= 230.00
Fin (Hz)= 50.00
Delay Time (ms)= 5000.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 113.050 ******* ******* 113.047
12Vsb 1.750 ******* ******* 1.750
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
------------Load--------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V ******* ******* 0.000
12Vsb ******* ******* 0.000
PWOK ******* ******* 0.000
Vin_Good ******* ******* 0.000
SMBAlert ******* ******* 0.000
-------34970----------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 12.350 11.590 12.194
12VSb 12.600 11.400 12.020
PWOK 3.460 2.500 3.233
Vin_Good 3.460 2.500 3.228
SMBAlert 3.460 2.500 3.226
IBUS ******* ******* 5.582
CR 0.400 ******* -0.015
Max Min Reading
------------- ---------- ---------- ----------
Vrms (V) ******** ******** 229.7214
PF 1.0000 0.9800 0.9987
THDi (%) 8.0000 * 2.4283
Irms (A) ******** ******** 6.6676
Pin (W) ******** ******** 1529.7255
Pout (W) ******** ******** 1399.5505
Eff (%) 99.0000 ******** 91.4903
Load Noise Range Noise B.W
Name (V) (MHz)
------------- ----------- ---------
12V 2 20.000
12Vsb 2 20.000
PWOK 2 20.000
Vin_Good 2 20.000
SMBAlert 2 20.000
Load Vpp Noise Vpp Noise Vpp Noise
Name Max(mV) Min(mV) (mV)
------------- ------------ ------------ ------------
12V 120.000 0.000 12.570
12Vsb 120.000 0.000 11.450
PWOK ********* ********* 23.490
Vin_Good ********* ********* 23.430
SMBAlert ********* ********* 25.200
MCU Accuracy ---------------------------------------------
Spec Status Reading Status
----------- ------------- ----------------
Mcu Status 0 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Reading
-------- ---------
Vin_M 229.2500
Iin_M 6.6875
Pin_M 1532.0000
Vout_M 12.2168
Iout_M 113.0000
Pout_M 1380.0000
Max Min Reading
--------------------- --------- --------- ---------
Mcu_Vin_VS_Vin (%) 2.000 * 0.2052
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 * 0.2991
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 * 0.1487
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 * 0.1854
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 * 0.0416
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 * 0.1076
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Max Min Reading
-------------- --------- --------- ---------
Temperature 1 200.00 0.00 56.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Max Min Reading
-------------- --------- --------- ---------
Temperature 2 200.00 0.00 81.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Max Min Reading
-------- --------- --------- ---------
Fan RPM 28000 ****** 11092
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
STEP.697(UUT Test seq.697) : Harmonic Multi UUT_Test_S2 ---- (2'122) ------ PASS
Standard = 1 (1:IEC-1000-3-2, 2:Japan)
Class = 0 (0:A, 1:B, 2:C, 3:D, 4:A-1)
Delay Time (ms)= 2000
Load Loading
Name (A/Ohm/V)
------------- ----------
12V 113.050
12Vsb 1.750
PWOK 0.000
Vin_Good 0.000
SMBAlert 0.000
Max Min Reading
------------- --------- --------- ---------
Pin (W) ******* ******* 1526.96
THD (%) ******* ******* 2.52
Input Voltage Reading (V) = 229.72
Spectrum Limit Reading
------------- --------- ---------
1 ********* 6.649
2 1.080 0.012
3 2.300 0.149
4 0.430 0.004
5 1.140 0.033
6 0.300 0.006
7 0.770 0.026
8 0.230 0.001
9 0.400 0.018
10 0.184 0.003
11 0.330 0.016
12 0.153 0.000
13 0.210 0.008
14 0.131 0.004
15 0.150 0.009
16 0.115 0.005
17 0.132 0.005
18 0.102 0.004
19 0.118 0.004
20 0.092 0.001
21 0.107 0.001
22 0.084 0.003
23 0.098 0.006
24 0.077 0.006
25 0.090 0.009
26 0.071 0.003
27 0.083 0.012
28 0.066 0.002
29 0.078 0.013
30 0.061 0.003
31 0.073 0.011
32 0.058 0.005
33 0.068 0.011
34 0.054 0.002
35 0.064 0.016
36 0.051 0.001
37 0.061 0.015
38 0.048 0.003
39 0.058 0.018
40 0.046 0.001
STEP.698(UUT Test seq.698) : Input Output Accuracy Multi or Single_S3(230Va PASS
ElapsedTime (S)= 6'271
Vin (V)= 230.00
Fin (Hz)= 50.00
Delay Time (ms)= 5000.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 96.900 ******* ******* 96.898
12Vsb 1.500 ******* ******* 1.500
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
------------Load--------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V ******* ******* 0.000
12Vsb ******* ******* 0.000
PWOK ******* ******* 0.000
Vin_Good ******* ******* 0.000
SMBAlert ******* ******* 0.000
-------34970----------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 12.350 11.590 12.204
12VSb 12.600 11.400 12.029
PWOK 3.460 2.500 3.234
Vin_Good 3.460 2.500 3.235
SMBAlert 3.460 2.500 3.219
IBUS ******* ******* 4.782
CR 0.400 ******* -0.012
Max Min Reading
------------- ---------- ---------- ----------
Vrms (V) ******** ******** 229.7746
PF 1.0000 0.9800 0.9986
THDi (%) 8.0000 * 2.4120
Irms (A) ******** ******** 5.6683
Pin (W) ******** ******** 1300.5852
Pout (W) ******** ******** 1200.5623
Eff (%) 99.0000 ******** 92.3094
Load Noise Range Noise B.W
Name (V) (MHz)
------------- ----------- ---------
12V 2 20.000
12Vsb 2 20.000
PWOK 2 20.000
Vin_Good 2 20.000
SMBAlert 2 20.000
Load Vpp Noise Vpp Noise Vpp Noise
Name Max(mV) Min(mV) (mV)
------------- ------------ ------------ ------------
12V 120.000 0.000 12.580
12Vsb 120.000 0.000 8.690
PWOK ********* ********* 22.560
Vin_Good ********* ********* 23.190
SMBAlert ********* ********* 24.150
MCU Accuracy ---------------------------------------------
Spec Status Reading Status
----------- ------------- ----------------
Mcu Status 0 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Reading
-------- ---------
Vin_M 229.5000
Iin_M 5.6953
Pin_M 1306.0000
Vout_M 12.2227
Iout_M 96.7500
Pout_M 1182.0000
Max Min Reading
--------------------- --------- --------- ---------
Mcu_Vin_VS_Vin (%) 2.000 * 0.1195
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 * 0.4771
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 * 0.4163
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 * 0.1544
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 * 0.1523
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 * 0.0440
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Max Min Reading
-------------- --------- --------- ---------
Temperature 1 200.00 0.00 56.50
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Max Min Reading
-------------- --------- --------- ---------
Temperature 2 200.00 0.00 81.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Max Min Reading
-------- --------- --------- ---------
Fan RPM 28000 ****** 10957
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
STEP.699(UUT Test seq.699) : Harmonic Multi UUT_Test_S2 ---- (2'121) ------ PASS
Standard = 1 (1:IEC-1000-3-2, 2:Japan)
Class = 0 (0:A, 1:B, 2:C, 3:D, 4:A-1)
Delay Time (ms)= 2000
Load Loading
Name (A/Ohm/V)
------------- ----------
12V 96.900
12Vsb 1.500
PWOK 0.000
Vin_Good 0.000
SMBAlert 0.000
Max Min Reading
------------- --------- --------- ---------
Pin (W) ******* ******* 1301.27
THD (%) ******* ******* 2.53
Input Voltage Reading (V) = 229.78
Spectrum Limit Reading
------------- --------- ---------
1 ********* 5.667
2 1.080 0.009
3 2.300 0.129
4 0.430 0.002
5 1.140 0.026
6 0.300 0.002
7 0.770 0.023
8 0.230 0.004
9 0.400 0.015
10 0.184 0.004
11 0.330 0.011
12 0.153 0.005
13 0.210 0.007
14 0.131 0.008
15 0.150 0.007
16 0.115 0.004
17 0.132 0.002
18 0.102 0.001
19 0.118 0.003
20 0.092 0.004
21 0.107 0.003
22 0.084 0.003
23 0.098 0.005
24 0.077 0.004
25 0.090 0.004
26 0.071 0.003
27 0.083 0.008
28 0.066 0.001
29 0.078 0.011
30 0.061 0.001
31 0.073 0.012
32 0.058 0.002
33 0.068 0.015
34 0.054 0.001
35 0.064 0.013
36 0.051 0.005
37 0.061 0.013
38 0.048 0.001
39 0.058 0.012
40 0.046 0.001
STEP.700(UUT Test seq.700) : Input Output Accuracy Multi or Single_S3(230Va PASS
ElapsedTime (S)= 6'302
Vin (V)= 230.00
Fin (Hz)= 50.00
Delay Time (ms)= 5000.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 80.750 ******* ******* 80.748
12Vsb 1.250 ******* ******* 1.250
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
------------Load--------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V ******* ******* 0.000
12Vsb ******* ******* 0.000
PWOK ******* ******* 0.000
Vin_Good ******* ******* 0.000
SMBAlert ******* ******* 0.000
-------34970----------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 12.350 11.590 12.213
12VSb 12.600 11.400 12.039
PWOK 3.460 2.500 3.235
Vin_Good 3.460 2.500 3.237
SMBAlert 3.460 2.500 3.217
IBUS 4.200 3.800 3.999
CR 0.400 ******* -0.010
Max Min Reading
------------- ---------- ---------- ----------
Vrms (V) ******** ******** 229.8651
PF 1.0000 0.9800 0.9977
THDi (%) 8.0000 * 2.7711
Irms (A) ******** ******** 4.6823
Pin (W) ******** ******** 1073.7902
Pout (W) ******** ******** 1001.1952
Eff (%) 99.0000 92.0000 93.2394
Load Noise Range Noise B.W
Name (V) (MHz)
------------- ----------- ---------
12V 2 20.000
12Vsb 2 20.000
PWOK 2 20.000
Vin_Good 2 20.000
SMBAlert 2 20.000
Load Vpp Noise Vpp Noise Vpp Noise
Name Max(mV) Min(mV) (mV)
------------- ------------ ------------ ------------
12V 120.000 0.000 9.220
12Vsb 120.000 0.000 6.810
PWOK ********* ********* 22.200
Vin_Good ********* ********* 21.250
SMBAlert ********* ********* 24.270
MCU Accuracy ---------------------------------------------
Spec Status Reading Status
----------- ------------- ----------------
Mcu Status 0 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Reading
-------- ---------
Vin_M 229.5000
Iin_M 4.6953
Pin_M 1076.0000
Vout_M 12.2266
Iout_M 80.6250
Pout_M 987.0000
Max Min Reading
--------------------- --------- --------- ---------
Mcu_Vin_VS_Vin (%) 2.000 * 0.1588
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 * 0.2776
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 * 0.2058
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 * 0.1136
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 * 0.1520
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 * 0.0865
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Max Min Reading
-------------- --------- --------- ---------
Temperature 1 200.00 0.00 57.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Max Min Reading
-------------- --------- --------- ---------
Temperature 2 200.00 0.00 80.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Max Min Reading
-------- --------- --------- ---------
Fan RPM 28000 ****** 10877
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
STEP.701(UUT Test seq.701) : Harmonic Multi UUT_Test_S2 ---- (2'122) ------ PASS
Standard = 1 (1:IEC-1000-3-2, 2:Japan)
Class = 0 (0:A, 1:B, 2:C, 3:D, 4:A-1)
Delay Time (ms)= 2000
Load Loading
Name (A/Ohm/V)
------------- ----------
12V 80.750
12Vsb 1.250
PWOK 0.000
Vin_Good 0.000
SMBAlert 0.000
Max Min Reading
------------- --------- --------- ---------
Pin (W) ******* ******* 1073.70
THD (%) ******* ******* 2.66
Input Voltage Reading (V) = 229.85
Spectrum Limit Reading
------------- --------- ---------
1 ********* 4.680
2 1.080 0.006
3 2.300 0.117
4 0.430 0.007
5 1.140 0.033
6 0.300 0.006
7 0.770 0.026
8 0.230 0.001
9 0.400 0.017
10 0.184 0.003
11 0.330 0.013
12 0.153 0.005
13 0.210 0.008
14 0.131 0.002
15 0.150 0.004
16 0.115 0.002
17 0.132 0.003
18 0.102 0.003
19 0.118 0.001
20 0.092 0.003
21 0.107 0.007
22 0.084 0.004
23 0.098 0.004
24 0.077 0.003
25 0.090 0.006
26 0.071 0.002
27 0.083 0.012
28 0.066 0.004
29 0.078 0.011
30 0.061 0.001
31 0.073 0.011
32 0.058 0.001
33 0.068 0.014
34 0.054 0.001
35 0.064 0.014
36 0.051 0.001
37 0.061 0.012
38 0.048 0.000
39 0.058 0.013
40 0.046 0.001
STEP.702(UUT Test seq.702) : Input Output Accuracy Multi or Single_S3(230Va PASS
ElapsedTime (S)= 6'302
Vin (V)= 230.00
Fin (Hz)= 50.00
Delay Time (ms)= 5000.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 64.600 ******* ******* 64.598
12Vsb 1.000 ******* ******* 1.000
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
------------Load--------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V ******* ******* 0.000
12Vsb ******* ******* 0.000
PWOK ******* ******* 0.000
Vin_Good ******* ******* 0.000
SMBAlert ******* ******* 0.000
-------34970----------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 12.350 11.590 12.223
12VSb 12.600 11.400 12.051
PWOK 3.460 2.500 3.235
Vin_Good 3.460 2.500 3.242
SMBAlert 3.460 2.500 3.216
IBUS ******* ******* 3.206
CR 0.400 ******* -0.007
Max Min Reading
------------- ---------- ---------- ----------
Vrms (V) ******** ******** 229.9345
PF 1.0000 0.9600 0.9967
THDi (%) 10.0000 * 3.1310
Irms (A) ******** ******** 3.7383
Pin (W) ******** ******** 856.7382
Pout (W) ******** ******** 801.6323
Eff (%) 99.0000 ******** 93.5679
Load Noise Range Noise B.W
Name (V) (MHz)
------------- ----------- ---------
12V 2 20.000
12Vsb 2 20.000
PWOK 2 20.000
Vin_Good 2 20.000
SMBAlert 2 20.000
Load Vpp Noise Vpp Noise Vpp Noise
Name Max(mV) Min(mV) (mV)
------------- ------------ ------------ ------------
12V 120.000 0.000 8.900
12Vsb 120.000 0.000 5.530
PWOK ********* ********* 22.080
Vin_Good ********* ********* 20.930
SMBAlert ********* ********* 24.070
MCU Accuracy ---------------------------------------------
Spec Status Reading Status
----------- ------------- ----------------
Mcu Status 0 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Reading
-------- ---------
Vin_M 229.7500
Iin_M 3.7500
Pin_M 860.0000
Vout_M 12.2324
Iout_M 64.6250
Pout_M 791.0000
Max Min Reading
--------------------- --------- --------- ---------
Mcu_Vin_VS_Vin (%) 2.000 * 0.0802
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 * 0.3120
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 * 0.3807
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 * 0.0767
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 * 0.0423
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 * 0.1797
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Max Min Reading
-------------- --------- --------- ---------
Temperature 1 200.00 0.00 57.50
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Max Min Reading
-------------- --------- --------- ---------
Temperature 2 200.00 0.00 79.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Max Min Reading
-------- --------- --------- ---------
Fan RPM 28000 ****** 10794
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
STEP.703(UUT Test seq.703) : Harmonic Multi UUT_Test_S2 ---- (2'138) ------ PASS
Standard = 1 (1:IEC-1000-3-2, 2:Japan)
Class = 0 (0:A, 1:B, 2:C, 3:D, 4:A-1)
Delay Time (ms)= 2000
Load Loading
Name (A/Ohm/V)
------------- ----------
12V 64.600
12Vsb 1.000
PWOK 0.000
Vin_Good 0.000
SMBAlert 0.000
Max Min Reading
------------- --------- --------- ---------
Pin (W) ******* ******* 857.02
THD (%) ******* ******* 3.00
Input Voltage Reading (V) = 229.91
Spectrum Limit Reading
------------- --------- ---------
1 ********* 3.741
2 1.080 0.002
3 2.300 0.095
4 0.430 0.004
5 1.140 0.032
6 0.300 0.002
7 0.770 0.025
8 0.230 0.004
9 0.400 0.015
10 0.184 0.001
11 0.330 0.012
12 0.153 0.003
13 0.210 0.011
14 0.131 0.001
15 0.150 0.003
16 0.115 0.003
17 0.132 0.001
18 0.102 0.001
19 0.118 0.005
20 0.092 0.001
21 0.107 0.005
22 0.084 0.003
23 0.098 0.006
24 0.077 0.003
25 0.090 0.011
26 0.071 0.002
27 0.083 0.011
28 0.066 0.001
29 0.078 0.011
30 0.061 0.002
31 0.073 0.014
32 0.058 0.002
33 0.068 0.011
34 0.054 0.001
35 0.064 0.012
36 0.051 0.002
37 0.061 0.013
38 0.048 0.001
39 0.058 0.012
40 0.046 0.002
STEP.704(UUT Test seq.704) : Input Output Accuracy Multi or Single_S3(230Va PASS
ElapsedTime (S)= 6'334
Vin (V)= 230.00
Fin (Hz)= 50.00
Delay Time (ms)= 5000.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 48.450 ******* ******* 48.448
12Vsb 0.750 ******* ******* 0.750
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
------------Load--------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V ******* ******* 0.000
12Vsb ******* ******* 0.000
PWOK ******* ******* 0.000
Vin_Good ******* ******* 0.000
SMBAlert ******* ******* 0.000
-------34970----------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 12.350 11.590 12.233
12VSb 12.600 11.400 12.064
PWOK 3.460 2.500 3.238
Vin_Good 3.460 2.500 3.244
SMBAlert 3.460 2.500 3.215
IBUS ******* ******* 2.405
CR 0.400 ******* -0.005
Max Min Reading
------------- ---------- ---------- ----------
Vrms (V) ******** ******** 230.0064
PF 1.0000 0.9600 0.9947
THDi (%) 10.0000 * 3.5724
Irms (A) ******** ******** 2.8114
Pin (W) ******** ******** 643.2000
Pout (W) ******** ******** 601.7278
Eff (%) 99.0000 ******** 93.5522
Load Noise Range Noise B.W
Name (V) (MHz)
------------- ----------- ---------
12V 2 20.000
12Vsb 2 20.000
PWOK 2 20.000
Vin_Good 2 20.000
SMBAlert 2 20.000
Load Vpp Noise Vpp Noise Vpp Noise
Name Max(mV) Min(mV) (mV)
------------- ------------ ------------ ------------
12V 120.000 0.000 8.320
12Vsb 120.000 0.000 4.340
PWOK ********* ********* 21.520
Vin_Good ********* ********* 20.260
SMBAlert ********* ********* 23.430
MCU Accuracy ---------------------------------------------
Spec Status Reading Status
----------- ------------- ----------------
Mcu Status 0 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Reading
-------- ---------
Vin_M 229.7500
Iin_M 2.8125
Pin_M 646.0000
Vout_M 12.2363
Iout_M 48.5000
Pout_M 593.0000
Max Min Reading
--------------------- --------- --------- ---------
Mcu_Vin_VS_Vin (%) 2.000 * 0.1115
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 * 0.0385
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 * 0.4353
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 * 0.0238
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 * 0.1082
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 * 0.0541
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Max Min Reading
-------------- --------- --------- ---------
Temperature 1 200.00 0.00 58.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Max Min Reading
-------------- --------- --------- ---------
Temperature 2 200.00 0.00 77.50
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Max Min Reading
-------- --------- --------- ---------
Fan RPM 28000 ****** 9162
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
STEP.705(UUT Test seq.705) : Harmonic Multi UUT_Test_S2 ---- (2'106) ------ PASS
Standard = 1 (1:IEC-1000-3-2, 2:Japan)
Class = 0 (0:A, 1:B, 2:C, 3:D, 4:A-1)
Delay Time (ms)= 2000
Load Loading
Name (A/Ohm/V)
------------- ----------
12V 48.450
12Vsb 0.750
PWOK 0.000
Vin_Good 0.000
SMBAlert 0.000
Max Min Reading
------------- --------- --------- ---------
Pin (W) ******* ******* 643.32
THD (%) ******* ******* 3.78
Input Voltage Reading (V) = 230.01
Spectrum Limit Reading
------------- --------- ---------
1 ********* 2.813
2 1.080 0.009
3 2.300 0.077
4 0.430 0.001
5 1.140 0.036
6 0.300 0.001
7 0.770 0.020
8 0.230 0.003
9 0.400 0.014
10 0.184 0.003
11 0.330 0.009
12 0.153 0.004
13 0.210 0.009
14 0.131 0.004
15 0.150 0.006
16 0.115 0.005
17 0.132 0.002
18 0.102 0.005
19 0.118 0.004
20 0.092 0.005
21 0.107 0.002
22 0.084 0.005
23 0.098 0.003
24 0.077 0.006
25 0.090 0.008
26 0.071 0.002
27 0.083 0.006
28 0.066 0.003
29 0.078 0.007
30 0.061 0.003
31 0.073 0.009
32 0.058 0.002
33 0.068 0.012
34 0.054 0.002
35 0.064 0.011
36 0.051 0.002
37 0.061 0.010
38 0.048 0.000
39 0.058 0.011
40 0.046 0.002
STEP.706(UUT Test seq.706) : Input Output Accuracy Multi or Single_S3(230Va PASS
ElapsedTime (S)= 6'334
Vin (V)= 230.00
Fin (Hz)= 50.00
Delay Time (ms)= 5000.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 32.300 ******* ******* 32.298
12Vsb 0.500 ******* ******* 0.500
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
------------Load--------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V ******* ******* 0.000
12Vsb ******* ******* 0.000
PWOK ******* ******* 0.000
Vin_Good ******* ******* 0.000
SMBAlert ******* ******* 0.000
-------34970----------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 12.350 11.590 12.243
12VSb 12.600 11.400 12.081
PWOK 3.460 2.500 3.241
Vin_Good 3.460 2.500 3.247
SMBAlert 3.460 2.500 3.213
IBUS 1.800 1.400 1.607
CR 0.400 ******* -0.002
Max Min Reading
------------- ---------- ---------- ----------
Vrms (V) ******** ******** 230.1294
PF 1.0000 0.9600 0.9927
THDi (%) 10.0000 * 5.8955
Irms (A) ******** ******** 1.8899
Pin (W) ******** ******** 431.7542
Pout (W) ******** ******** 401.4637
Eff (%) 99.0000 91.0000 92.9843
Load Noise Range Noise B.W
Name (V) (MHz)
------------- ----------- ---------
12V 2 20.000
12Vsb 2 20.000
PWOK 2 20.000
Vin_Good 2 20.000
SMBAlert 2 20.000
Load Vpp Noise Vpp Noise Vpp Noise
Name Max(mV) Min(mV) (mV)
------------- ------------ ------------ ------------
12V 120.000 0.000 8.470
12Vsb 120.000 0.000 3.570
PWOK ********* ********* 21.100
Vin_Good ********* ********* 20.240
SMBAlert ********* ********* 23.100
MCU Accuracy ---------------------------------------------
Spec Status Reading Status
----------- ------------- ----------------
Mcu Status 0 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Reading
-------- ---------
Vin_M 230.0000
Iin_M 1.8867
Pin_M 431.5000
Vout_M 12.2422
Iout_M 32.3750
Pout_M 396.0000
Max Min Reading
--------------------- --------- --------- ---------
Mcu_Vin_VS_Vin (%) 2.000 * 0.0562
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 * 0.1673
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 * 0.0589
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 * 0.0069
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 * 0.2390
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 * 0.1459
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Max Min Reading
-------------- --------- --------- ---------
Temperature 1 200.00 0.00 59.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Max Min Reading
-------------- --------- --------- ---------
Temperature 2 200.00 0.00 76.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Max Min Reading
-------- --------- --------- ---------
Fan RPM 28000 ****** 9037
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
STEP.707(UUT Test seq.707) : Harmonic Multi UUT_Test_S2 ---- (2'122) ------ PASS
Standard = 1 (1:IEC-1000-3-2, 2:Japan)
Class = 0 (0:A, 1:B, 2:C, 3:D, 4:A-1)
Delay Time (ms)= 2000
Load Loading
Name (A/Ohm/V)
------------- ----------
12V 32.300
12Vsb 0.500
PWOK 0.000
Vin_Good 0.000
SMBAlert 0.000
Max Min Reading
------------- --------- --------- ---------
Pin (W) ******* ******* 431.79
THD (%) ******* ******* 6.02
Input Voltage Reading (V) = 230.13
Spectrum Limit Reading
------------- --------- ---------
1 ********* 1.885
2 1.080 0.005
3 2.300 0.091
4 0.430 0.003
5 1.140 0.017
6 0.300 0.004
7 0.770 0.023
8 0.230 0.004
9 0.400 0.014
10 0.184 0.005
11 0.330 0.022
12 0.153 0.003
13 0.210 0.007
14 0.131 0.007
15 0.150 0.014
16 0.115 0.008
17 0.132 0.015
18 0.102 0.001
19 0.118 0.028
20 0.092 0.007
21 0.107 0.028
22 0.084 0.005
23 0.098 0.016
24 0.077 0.004
25 0.090 0.010
26 0.071 0.003
27 0.083 0.006
28 0.066 0.004
29 0.078 0.008
30 0.061 0.006
31 0.073 0.009
32 0.058 0.004
33 0.068 0.003
34 0.054 0.003
35 0.064 0.003
36 0.051 0.006
37 0.061 0.004
38 0.048 0.002
39 0.058 0.007
40 0.046 0.001
STEP.708(UUT Test seq.708) : Input Output Accuracy Multi or Single_S3(230Va PASS
ElapsedTime (S)= 6'427
Vin (V)= 230.00
Fin (Hz)= 50.00
Delay Time (ms)= 5000.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 16.150 ******* ******* 16.148
12Vsb 0.250 ******* ******* 0.250
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
------------Load--------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V ******* ******* 0.000
12Vsb ******* ******* 0.000
PWOK ******* ******* 0.000
Vin_Good ******* ******* 0.000
SMBAlert ******* ******* 0.000
-------34970----------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 12.350 11.590 12.253
12VSb 12.600 11.400 12.107
PWOK 3.460 2.500 3.242
Vin_Good 3.460 2.500 3.249
SMBAlert 3.460 2.500 3.214
IBUS 1.000 0.600 0.810
CR 0.400 ******* 0.001
Max Min Reading
------------- ---------- ---------- ----------
Vrms (V) ******** ******** 230.2223
PF 1.0000 0.9000 0.9835
THDi (%) 20.0000 * 7.3699
Irms (A) ******** ******** 0.9762
Pin (W) ******** ******** 221.0283
Pout (W) ******** ******** 200.8941
Eff (%) 99.0000 88.0000 90.8907
Load Noise Range Noise B.W
Name (V) (MHz)
------------- ----------- ---------
12V 2 20.000
12Vsb 2 20.000
PWOK 2 20.000
Vin_Good 2 20.000
SMBAlert 2 20.000
Load Vpp Noise Vpp Noise Vpp Noise
Name Max(mV) Min(mV) (mV)
------------- ------------ ------------ ------------
12V 120.000 0.000 23.080
12Vsb 120.000 0.000 2.980
PWOK ********* ********* 20.340
Vin_Good ********* ********* 19.210
SMBAlert ********* ********* 22.270
MCU Accuracy ---------------------------------------------
Spec Status Reading Status
----------- ------------- ----------------
Mcu Status 0 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Reading
-------- ---------
Vin_M 230.2500
Iin_M 0.9883
Pin_M 219.5000
Vout_M 12.2480
Iout_M 16.2813
Pout_M 199.2500
Max Min Reading
--------------------- --------- --------- ---------
Mcu_Vin_VS_Vin (%) 5.000 * 0.0120
Mcu_Vin_VS_Vin (%) 5.000 *
Mcu_Vin_VS_Vin (%) 5.000 *
Mcu_Vin_VS_Vin (%) 5.000 *
Mcu_Vin_VS_Vin (%) 5.000 *
Mcu_Vin_VS_Vin (%) 5.000 *
Mcu_Vin_VS_Vin (%) 5.000 *
Mcu_Vin_VS_Vin (%) 5.000 *
Mcu_Iin_VS_Iin (%) 5.000 * 1.2358
Mcu_Iin_VS_Iin (%) 5.000 *
Mcu_Iin_VS_Iin (%) 5.000 *
Mcu_Iin_VS_Iin (%) 5.000 *
Mcu_Iin_VS_Iin (%) 5.000 *
Mcu_Iin_VS_Iin (%) 5.000 *
Mcu_Iin_VS_Iin (%) 5.000 *
Mcu_Iin_VS_Iin (%) 5.000 *
Mcu_Pin_VS_Pin (%) 5.000 * 0.6914
Mcu_Pin_VS_Pin (%) 5.000 *
Mcu_Pin_VS_Pin (%) 5.000 *
Mcu_Pin_VS_Pin (%) 5.000 *
Mcu_Pin_VS_Pin (%) 5.000 *
Mcu_Pin_VS_Pin (%) 5.000 *
Mcu_Pin_VS_Pin (%) 5.000 *
Mcu_Pin_VS_Pin (%) 5.000 *
Mcu_Vout_VS_Vout (%) 5.000 * 0.0437
Mcu_Vout_VS_Vout (%) 5.000 *
Mcu_Vout_VS_Vout (%) 5.000 *
Mcu_Vout_VS_Vout (%) 5.000 *
Mcu_Vout_VS_Vout (%) 5.000 *
Mcu_Vout_VS_Vout (%) 5.000 *
Mcu_Vout_VS_Vout (%) 5.000 *
Mcu_Vout_VS_Vout (%) 5.000 *
Mcu_Iout_VS_Iout (%) 5.000 * 0.8258
Mcu_Iout_VS_Iout (%) 5.000 *
Mcu_Iout_VS_Iout (%) 5.000 *
Mcu_Iout_VS_Iout (%) 5.000 *
Mcu_Iout_VS_Iout (%) 5.000 *
Mcu_Iout_VS_Iout (%) 5.000 *
Mcu_Iout_VS_Iout (%) 5.000 *
Mcu_Iout_VS_Iout (%) 5.000 *
Mcu_Pout_VS_Pout (%) 5.000 * 0.6991
Mcu_Pout_VS_Pout (%) 5.000 *
Mcu_Pout_VS_Pout (%) 5.000 *
Mcu_Pout_VS_Pout (%) 5.000 *
Mcu_Pout_VS_Pout (%) 5.000 *
Mcu_Pout_VS_Pout (%) 5.000 *
Mcu_Pout_VS_Pout (%) 5.000 *
Mcu_Pout_VS_Pout (%) 5.000 *
Max Min Reading
-------------- --------- --------- ---------
Temperature 1 200.00 0.00 60.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Max Min Reading
-------------- --------- --------- ---------
Temperature 2 200.00 0.00 75.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Max Min Reading
-------- --------- --------- ---------
Fan RPM 28000 ****** 8907
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
STEP.709(UUT Test seq.709) : Harmonic Multi UUT_Test_S2 ---- (2'122) ------ PASS
Standard = 1 (1:IEC-1000-3-2, 2:Japan)
Class = 0 (0:A, 1:B, 2:C, 3:D, 4:A-1)
Delay Time (ms)= 2000
Load Loading
Name (A/Ohm/V)
------------- ----------
12V 16.150
12Vsb 0.250
PWOK 0.000
Vin_Good 0.000
SMBAlert 0.000
Max Min Reading
------------- --------- --------- ---------
Pin (W) ******* ******* 221.14
THD (%) ******* ******* 7.07
Input Voltage Reading (V) = 230.22
Spectrum Limit Reading
------------- --------- ---------
1 ********* 0.971
2 1.080 0.005
3 2.300 0.048
4 0.430 0.002
5 1.140 0.031
6 0.300 0.001
7 0.770 0.021
8 0.230 0.002
9 0.400 0.006
10 0.184 0.002
11 0.330 0.002
12 0.153 0.003
13 0.210 0.011
14 0.131 0.002
15 0.150 0.000
16 0.115 0.000
17 0.132 0.006
18 0.102 0.004
19 0.118 0.011
20 0.092 0.003
21 0.107 0.003
22 0.084 0.004
23 0.098 0.007
24 0.077 0.003
25 0.090 0.002
26 0.071 0.001
27 0.083 0.010
28 0.066 0.002
29 0.078 0.009
30 0.061 0.002
31 0.073 0.004
32 0.058 0.002
33 0.068 0.004
34 0.054 0.001
35 0.064 0.009
36 0.051 0.003
37 0.061 0.005
38 0.048 0.005
39 0.058 0.005
40 0.046 0.004
STEP.710(UUT Test seq.710) : Input Output Accuracy Multi or Single_S3(230Va PASS
ElapsedTime (S)= 6'474
Vin (V)= 230.00
Fin (Hz)= 60.00
Delay Time (ms)= 5000.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 161.500 ******* ******* 161.497
12Vsb 2.500 ******* ******* 2.500
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
------------Load--------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V ******* ******* 0.000
12Vsb ******* ******* 0.000
PWOK ******* ******* 0.000
Vin_Good ******* ******* 0.000
SMBAlert ******* ******* 0.000
-------34970----------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 12.350 11.590 12.167
12VSb 12.600 11.400 11.996
PWOK 3.460 2.500 3.227
Vin_Good 3.460 2.500 3.220
SMBAlert 3.460 2.500 3.228
IBUS 8.200 7.800 8.002
CR 0.400 ******* -0.022
Max Min Reading
------------- ---------- ---------- ----------
Vrms (V) ******** ******** 229.4482
PF 1.0000 0.9900 0.9982
THDi (%) 5.0000 * 2.3456
Irms (A) 10.0000 ******** 9.6369
Pin (W) ******** ******** 2207.2568
Pout (W) ******** ******** 1994.8894
Eff (%) 99.0000 89.0000 90.3787
Load Noise Range Noise B.W
Name (V) (MHz)
------------- ----------- ---------
12V 2 20.000
12Vsb 2 20.000
PWOK 2 20.000
Vin_Good 2 20.000
SMBAlert 2 20.000
Load Vpp Noise Vpp Noise Vpp Noise
Name Max(mV) Min(mV) (mV)
------------- ------------ ------------ ------------
12V 120.000 0.000 15.020
12Vsb 120.000 0.000 15.150
PWOK ********* ********* 24.760
Vin_Good ********* ********* 23.660
SMBAlert ********* ********* 25.950
MCU Accuracy ---------------------------------------------
Spec Status Reading Status
----------- ------------- ----------------
Mcu Status 0 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Reading
-------- ---------
Vin_M 228.7500
Iin_M 9.6563
Pin_M 2204.0000
Vout_M 12.2012
Iout_M 161.2500
Pout_M 1968.0000
Max Min Reading
--------------------- --------- --------- ---------
Mcu_Vin_VS_Vin (%) 2.000 * 0.3043
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 * 0.2013
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 * 0.1476
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 * 0.2825
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 * 0.1529
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 * 0.1577
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Max Min Reading
-------------- --------- --------- ---------
Temperature 1 200.00 0.00 58.50
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Max Min Reading
-------------- --------- --------- ---------
Temperature 2 200.00 0.00 75.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Max Min Reading
-------- --------- --------- ---------
Fan RPM 28000 ****** 11115
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
STEP.711(UUT Test seq.711) : Input Output Accuracy Multi or Single_S3(230Va PASS
ElapsedTime (S)= 6'427
Vin (V)= 230.00
Fin (Hz)= 60.00
Delay Time (ms)= 5000.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 145.350 ******* ******* 145.347
12Vsb 2.250 ******* ******* 2.250
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
------------Load--------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V ******* ******* 0.000
12Vsb ******* ******* 0.000
PWOK ******* ******* 0.000
Vin_Good ******* ******* 0.000
SMBAlert ******* ******* 0.000
-------34970----------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 12.350 11.590 12.176
12VSb 12.600 11.400 12.003
PWOK 3.460 2.500 3.227
Vin_Good 3.460 2.500 3.228
SMBAlert 3.460 2.500 3.220
IBUS ******* ******* 7.194
CR 0.400 ******* -0.019
Max Min Reading
------------- ---------- ---------- ----------
Vrms (V) ******** ******** 229.5427
PF 1.0000 0.9800 0.9983
THDi (%) 8.0000 * 2.2085
Irms (A) ******** ******** 8.6363
Pin (W) ******** ******** 1979.0853
Pout (W) ******** ******** 1796.8129
Eff (%) 99.0000 ******** 90.7901
Load Noise Range Noise B.W
Name (V) (MHz)
------------- ----------- ---------
12V 2 20.000
12Vsb 2 20.000
PWOK 2 20.000
Vin_Good 2 20.000
SMBAlert 2 20.000
Load Vpp Noise Vpp Noise Vpp Noise
Name Max(mV) Min(mV) (mV)
------------- ------------ ------------ ------------
12V 120.000 0.000 14.290
12Vsb 120.000 0.000 14.230
PWOK ********* ********* 23.530
Vin_Good ********* ********* 23.860
SMBAlert ********* ********* 24.130
MCU Accuracy ---------------------------------------------
Spec Status Reading Status
----------- ------------- ----------------
Mcu Status 0 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Reading
-------- ---------
Vin_M 229.0000
Iin_M 8.6563
Pin_M 1978.0000
Vout_M 12.2070
Iout_M 145.2500
Pout_M 1772.0000
Max Min Reading
--------------------- --------- --------- ---------
Mcu_Vin_VS_Vin (%) 2.000 * 0.2364
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 * 0.2309
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 * 0.0548
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 * 0.2514
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 * 0.0667
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 * 0.1239
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Max Min Reading
-------------- --------- --------- ---------
Temperature 1 200.00 0.00 57.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Max Min Reading
-------------- --------- --------- ---------
Temperature 2 200.00 0.00 79.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Max Min Reading
-------- --------- --------- ---------
Fan RPM 28000 ****** 11116
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
STEP.712(UUT Test seq.712) : Input Output Accuracy Multi or Single_S3(230Va PASS
ElapsedTime (S)= 6'302
Vin (V)= 230.00
Fin (Hz)= 60.00
Delay Time (ms)= 5000.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 129.200 ******* ******* 129.197
12Vsb 2.000 ******* ******* 2.000
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
------------Load--------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V ******* ******* 0.000
12Vsb ******* ******* 0.000
PWOK ******* ******* 0.000
Vin_Good ******* ******* 0.000
SMBAlert ******* ******* 0.000
-------34970----------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 12.350 11.590 12.185
12VSb 12.600 11.400 12.011
PWOK 3.460 2.500 3.228
Vin_Good 3.460 2.500 3.230
SMBAlert 3.460 2.500 3.219
IBUS ******* ******* 6.385
CR 0.400 ******* -0.017
Max Min Reading
------------- ---------- ---------- ----------
Vrms (V) ******** ******** 229.6355
PF 1.0000 0.9800 0.9986
THDi (%) 8.0000 * 2.3071
Irms (A) ******** ******** 7.6456
Pin (W) ******** ******** 1753.3008
Pout (W) ******** ******** 1598.2283
Eff (%) 99.0000 ******** 91.1554
Load Noise Range Noise B.W
Name (V) (MHz)
------------- ----------- ---------
12V 2 20.000
12Vsb 2 20.000
PWOK 2 20.000
Vin_Good 2 20.000
SMBAlert 2 20.000
Load Vpp Noise Vpp Noise Vpp Noise
Name Max(mV) Min(mV) (mV)
------------- ------------ ------------ ------------
12V 120.000 0.000 13.020
12Vsb 120.000 0.000 13.200
PWOK ********* ********* 23.670
Vin_Good ********* ********* 23.750
SMBAlert ********* ********* 26.470
MCU Accuracy ---------------------------------------------
Spec Status Reading Status
----------- ------------- ----------------
Mcu Status 0 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Reading
-------- ---------
Vin_M 229.0000
Iin_M 7.6641
Pin_M 1752.0000
Vout_M 12.2129
Iout_M 129.0000
Pout_M 1576.0000
Max Min Reading
--------------------- --------- --------- ---------
Mcu_Vin_VS_Vin (%) 2.000 * 0.2767
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 * 0.2417
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 * 0.0742
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 * 0.2325
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 * 0.1525
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 * 0.1137
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Max Min Reading
-------------- --------- --------- ---------
Temperature 1 200.00 0.00 56.50
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Max Min Reading
-------------- --------- --------- ---------
Temperature 2 200.00 0.00 80.50
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Max Min Reading
-------- --------- --------- ---------
Fan RPM 28000 ****** 11116
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
STEP.713(UUT Test seq.713) : Input Output Accuracy Multi or Single_S3(230Va PASS
ElapsedTime (S)= 6'318
Vin (V)= 230.00
Fin (Hz)= 60.00
Delay Time (ms)= 5000.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 113.050 ******* ******* 113.047
12Vsb 1.750 ******* ******* 1.750
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
------------Load--------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V ******* ******* 0.000
12Vsb ******* ******* 0.000
PWOK ******* ******* 0.000
Vin_Good ******* ******* 0.000
SMBAlert ******* ******* 0.000
-------34970----------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 12.350 11.590 12.195
12VSb 12.600 11.400 12.020
PWOK 3.460 2.500 3.228
Vin_Good 3.460 2.500 3.232
SMBAlert 3.460 2.500 3.222
IBUS ******* ******* 5.582
CR 0.400 ******* -0.015
Max Min Reading
------------- ---------- ---------- ----------
Vrms (V) ******** ******** 229.7328
PF 1.0000 0.9800 0.9986
THDi (%) 8.0000 * 2.1140
Irms (A) ******** ******** 6.6633
Pin (W) ******** ******** 1528.7015
Pout (W) ******** ******** 1399.6342
Eff (%) 99.0000 ******** 91.5571
Load Noise Range Noise B.W
Name (V) (MHz)
------------- ----------- ---------
12V 2 20.000
12Vsb 2 20.000
PWOK 2 20.000
Vin_Good 2 20.000
SMBAlert 2 20.000
Load Vpp Noise Vpp Noise Vpp Noise
Name Max(mV) Min(mV) (mV)
------------- ------------ ------------ ------------
12V 120.000 0.000 13.570
12Vsb 120.000 0.000 11.630
PWOK ********* ********* 22.010
Vin_Good ********* ********* 23.730
SMBAlert ********* ********* 24.900
MCU Accuracy ---------------------------------------------
Spec Status Reading Status
----------- ------------- ----------------
Mcu Status 0 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Reading
-------- ---------
Vin_M 229.2500
Iin_M 6.6797
Pin_M 1526.0000
Vout_M 12.2168
Iout_M 113.0000
Pout_M 1380.0000
Max Min Reading
--------------------- --------- --------- ---------
Mcu_Vin_VS_Vin (%) 2.000 * 0.2101
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 * 0.2462
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 * 0.1767
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 * 0.1793
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 * 0.0416
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 * 0.1016
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Max Min Reading
-------------- --------- --------- ---------
Temperature 1 200.00 0.00 56.50
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Max Min Reading
-------------- --------- --------- ---------
Temperature 2 200.00 0.00 80.50
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Max Min Reading
-------- --------- --------- ---------
Fan RPM 28000 ****** 11095
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
STEP.714(UUT Test seq.714) : Input Output Accuracy Multi or Single_S3(230Va PASS
ElapsedTime (S)= 6'427
Vin (V)= 230.00
Fin (Hz)= 60.00
Delay Time (ms)= 5000.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 96.900 ******* ******* 96.898
12Vsb 1.500 ******* ******* 1.500
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
------------Load--------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V ******* ******* 0.000
12Vsb ******* ******* 0.000
PWOK ******* ******* 0.000
Vin_Good ******* ******* 0.000
SMBAlert ******* ******* 0.000
-------34970----------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 12.350 11.590 12.206
12VSb 12.600 11.400 12.031
PWOK 3.460 2.500 3.236
Vin_Good 3.460 2.500 3.230
SMBAlert 3.460 2.500 3.223
IBUS ******* ******* 4.782
CR 0.400 ******* -0.012
Max Min Reading
------------- ---------- ---------- ----------
Vrms (V) ******** ******** 229.8080
PF 1.0000 0.9800 0.9985
THDi (%) 8.0000 * 2.3189
Irms (A) ******** ******** 5.6694
Pin (W) ******** ******** 1300.9028
Pout (W) ******** ******** 1200.7808
Eff (%) 99.0000 ******** 92.3036
Load Noise Range Noise B.W
Name (V) (MHz)
------------- ----------- ---------
12V 2 20.000
12Vsb 2 20.000
PWOK 2 20.000
Vin_Good 2 20.000
SMBAlert 2 20.000
Load Vpp Noise Vpp Noise Vpp Noise
Name Max(mV) Min(mV) (mV)
------------- ------------ ------------ ------------
12V 120.000 0.000 12.530
12Vsb 120.000 0.000 8.590
PWOK ********* ********* 23.230
Vin_Good ********* ********* 22.750
SMBAlert ********* ********* 24.430
MCU Accuracy ---------------------------------------------
Spec Status Reading Status
----------- ------------- ----------------
Mcu Status 0 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Reading
-------- ---------
Vin_M 229.5000
Iin_M 5.6875
Pin_M 1300.0000
Vout_M 12.2227
Iout_M 96.7500
Pout_M 1182.0000
Max Min Reading
--------------------- --------- --------- ---------
Mcu_Vin_VS_Vin (%) 2.000 * 0.1340
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 * 0.3192
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 * 0.0694
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 * 0.1362
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 * 0.1524
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 * 0.0622
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Max Min Reading
-------------- --------- --------- ---------
Temperature 1 200.00 0.00 56.50
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Max Min Reading
-------------- --------- --------- ---------
Temperature 2 200.00 0.00 80.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Max Min Reading
-------- --------- --------- ---------
Fan RPM 28000 ****** 10960
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
STEP.715(UUT Test seq.715) : Input Output Accuracy Multi or Single_S3(230Va PASS
ElapsedTime (S)= 6'412
Vin (V)= 230.00
Fin (Hz)= 60.00
Delay Time (ms)= 5000.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 80.750 ******* ******* 80.748
12Vsb 1.250 ******* ******* 1.250
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
------------Load--------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V ******* ******* 0.000
12Vsb ******* ******* 0.000
PWOK ******* ******* 0.000
Vin_Good ******* ******* 0.000
SMBAlert ******* ******* 0.000
-------34970----------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 12.350 11.590 12.213
12VSb 12.600 11.400 12.040
PWOK 3.460 2.500 3.234
Vin_Good 3.460 2.500 3.237
SMBAlert 3.460 2.500 3.221
IBUS 4.200 3.800 4.000
CR 0.400 ******* -0.010
Max Min Reading
------------- ---------- ---------- ----------
Vrms (V) ******** ******** 229.8797
PF 1.0000 0.9800 0.9973
THDi (%) 8.0000 * 2.4848
Irms (A) ******** ******** 4.6837
Pin (W) ******** ******** 1073.7930
Pout (W) ******** ******** 1001.2545
Eff (%) 99.0000 92.0000 93.2447
Load Noise Range Noise B.W
Name (V) (MHz)
------------- ----------- ---------
12V 2 20.000
12Vsb 2 20.000
PWOK 2 20.000
Vin_Good 2 20.000
SMBAlert 2 20.000
Load Vpp Noise Vpp Noise Vpp Noise
Name Max(mV) Min(mV) (mV)
------------- ------------ ------------ ------------
12V 120.000 0.000 10.170
12Vsb 120.000 0.000 6.660
PWOK ********* ********* 21.160
Vin_Good ********* ********* 22.010
SMBAlert ********* ********* 22.930
MCU Accuracy ---------------------------------------------
Spec Status Reading Status
----------- ------------- ----------------
Mcu Status 0 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Reading
-------- ---------
Vin_M 229.7500
Iin_M 4.6875
Pin_M 1072.0000
Vout_M 12.2266
Iout_M 80.6250
Pout_M 987.0000
Max Min Reading
--------------------- --------- --------- ---------
Mcu_Vin_VS_Vin (%) 2.000 * 0.0564
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 * 0.0820
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 * 0.1670
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 * 0.1075
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 * 0.1518
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 * 0.0806
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Max Min Reading
-------------- --------- --------- ---------
Temperature 1 200.00 0.00 57.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Max Min Reading
-------------- --------- --------- ---------
Temperature 2 200.00 0.00 80.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Max Min Reading
-------- --------- --------- ---------
Fan RPM 28000 ****** 10874
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
STEP.716(UUT Test seq.716) : Input Output Accuracy Multi or Single_S3(230Va PASS
ElapsedTime (S)= 6'412
Vin (V)= 230.00
Fin (Hz)= 60.00
Delay Time (ms)= 5000.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 64.600 ******* ******* 64.598
12Vsb 1.000 ******* ******* 1.000
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
------------Load--------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V ******* ******* 0.000
12Vsb ******* ******* 0.000
PWOK ******* ******* 0.000
Vin_Good ******* ******* 0.000
SMBAlert ******* ******* 0.000
-------34970----------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 12.350 11.590 12.225
12VSb 12.600 11.400 12.051
PWOK 3.460 2.500 3.235
Vin_Good 3.460 2.500 3.241
SMBAlert 3.460 2.500 3.219
IBUS ******* ******* 3.204
CR 0.400 ******* -0.007
Max Min Reading
------------- ---------- ---------- ----------
Vrms (V) ******** ******** 229.9657
PF 1.0000 0.9600 0.9961
THDi (%) 10.0000 * 2.9567
Irms (A) ******** ******** 3.7412
Pin (W) ******** ******** 856.9490
Pout (W) ******** ******** 801.7278
Eff (%) 99.0000 ******** 93.5561
Load Noise Range Noise B.W
Name (V) (MHz)
------------- ----------- ---------
12V 2 20.000
12Vsb 2 20.000
PWOK 2 20.000
Vin_Good 2 20.000
SMBAlert 2 20.000
Load Vpp Noise Vpp Noise Vpp Noise
Name Max(mV) Min(mV) (mV)
------------- ------------ ------------ ------------
12V 120.000 0.000 8.810
12Vsb 120.000 0.000 5.700
PWOK ********* ********* 22.240
Vin_Good ********* ********* 21.250
SMBAlert ********* ********* 24.660
MCU Accuracy ---------------------------------------------
Spec Status Reading Status
----------- ------------- ----------------
Mcu Status 0 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Reading
-------- ---------
Vin_M 229.7500
Iin_M 3.7422
Pin_M 857.0000
Vout_M 12.2324
Iout_M 64.6250
Pout_M 791.0000
Max Min Reading
--------------------- --------- --------- ---------
Mcu_Vin_VS_Vin (%) 2.000 * 0.0938
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 * 0.0268
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 * 0.0060
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 * 0.0645
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 * 0.0423
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 * 0.1676
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Max Min Reading
-------------- --------- --------- ---------
Temperature 1 200.00 0.00 57.50
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Max Min Reading
-------------- --------- --------- ---------
Temperature 2 200.00 0.00 79.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Max Min Reading
-------- --------- --------- ---------
Fan RPM 28000 ****** 10794
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
STEP.717(UUT Test seq.717) : Input Output Accuracy Multi or Single_S3(230Va PASS
ElapsedTime (S)= 6'303
Vin (V)= 230.00
Fin (Hz)= 60.00
Delay Time (ms)= 5000.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 48.450 ******* ******* 48.448
12Vsb 0.750 ******* ******* 0.750
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
------------Load--------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V ******* ******* 0.000
12Vsb ******* ******* 0.000
PWOK ******* ******* 0.000
Vin_Good ******* ******* 0.000
SMBAlert ******* ******* 0.000
-------34970----------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 12.350 11.590 12.233
12VSb 12.600 11.400 12.065
PWOK 3.460 2.500 3.240
Vin_Good 3.460 2.500 3.240
SMBAlert 3.460 2.500 3.220
IBUS ******* ******* 2.405
CR 0.400 ******* -0.005
Max Min Reading
------------- ---------- ---------- ----------
Vrms (V) ******** ******** 230.0495
PF 1.0000 0.9600 0.9934
THDi (%) 10.0000 * 3.4840
Irms (A) ******** ******** 2.8146
Pin (W) ******** ******** 643.1909
Pout (W) ******** ******** 601.6925
Eff (%) 99.0000 ******** 93.5480
Load Noise Range Noise B.W
Name (V) (MHz)
------------- ----------- ---------
12V 2 20.000
12Vsb 2 20.000
PWOK 2 20.000
Vin_Good 2 20.000
SMBAlert 2 20.000
Load Vpp Noise Vpp Noise Vpp Noise
Name Max(mV) Min(mV) (mV)
------------- ------------ ------------ ------------
12V 120.000 0.000 8.410
12Vsb 120.000 0.000 4.540
PWOK ********* ********* 20.770
Vin_Good ********* ********* 20.670
SMBAlert ********* ********* 22.270
MCU Accuracy ---------------------------------------------
Spec Status Reading Status
----------- ------------- ----------------
Mcu Status 0 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Reading
-------- ---------
Vin_M 230.0000
Iin_M 2.8125
Pin_M 644.0000
Vout_M 12.2363
Iout_M 48.5000
Pout_M 593.0000
Max Min Reading
--------------------- --------- --------- ---------
Mcu_Vin_VS_Vin (%) 2.000 * 0.0215
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 * 0.0735
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 * 0.1258
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 * 0.0299
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 * 0.1082
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 * 0.0601
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Max Min Reading
-------------- --------- --------- ---------
Temperature 1 200.00 0.00 58.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Max Min Reading
-------------- --------- --------- ---------
Temperature 2 200.00 0.00 78.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Max Min Reading
-------- --------- --------- ---------
Fan RPM 28000 ****** 9168
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
STEP.718(UUT Test seq.718) : Input Output Accuracy Multi or Single_S3(230Va PASS
ElapsedTime (S)= 6'334
Vin (V)= 230.00
Fin (Hz)= 60.00
Delay Time (ms)= 5000.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 32.300 ******* ******* 32.298
12Vsb 0.500 ******* ******* 0.500
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
------------Load--------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V ******* ******* 0.000
12Vsb ******* ******* 0.000
PWOK ******* ******* 0.000
Vin_Good ******* ******* 0.000
SMBAlert ******* ******* 0.000
-------34970----------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 12.350 11.590 12.242
12VSb 12.600 11.400 12.081
PWOK 3.460 2.500 3.241
Vin_Good 3.460 2.500 3.247
SMBAlert 3.460 2.500 3.214
IBUS 1.800 1.400 1.606
CR 0.400 ******* -0.002
Max Min Reading
------------- ---------- ---------- ----------
Vrms (V) ******** ******** 230.1324
PF 1.0000 0.9600 0.9909
THDi (%) 10.0000 * 6.3235
Irms (A) ******** ******** 1.8932
Pin (W) ******** ******** 431.7024
Pout (W) ******** ******** 401.4373
Eff (%) 99.0000 91.0000 92.9893
Load Noise Range Noise B.W
Name (V) (MHz)
------------- ----------- ---------
12V 2 20.000
12Vsb 2 20.000
PWOK 2 20.000
Vin_Good 2 20.000
SMBAlert 2 20.000
Load Vpp Noise Vpp Noise Vpp Noise
Name Max(mV) Min(mV) (mV)
------------- ------------ ------------ ------------
12V 120.000 0.000 8.250
12Vsb 120.000 0.000 3.860
PWOK ********* ********* 20.900
Vin_Good ********* ********* 20.310
SMBAlert ********* ********* 22.540
MCU Accuracy ---------------------------------------------
Spec Status Reading Status
----------- ------------- ----------------
Mcu Status 0 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Reading
-------- ---------
Vin_M 230.0000
Iin_M 1.8848
Pin_M 430.5000
Vout_M 12.2422
Iout_M 32.3750
Pout_M 396.0000
Max Min Reading
--------------------- --------- --------- ---------
Mcu_Vin_VS_Vin (%) 2.000 * 0.0575
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 * 0.4438
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 * 0.2785
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 * 0.0009
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 * 0.2396
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 * 0.1526
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Max Min Reading
-------------- --------- --------- ---------
Temperature 1 200.00 0.00 59.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Max Min Reading
-------------- --------- --------- ---------
Temperature 2 200.00 0.00 77.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Max Min Reading
-------- --------- --------- ---------
Fan RPM 28000 ****** 9047
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
STEP.719(UUT Test seq.719) : Input Output Accuracy Multi or Single_S3(230Va PASS
ElapsedTime (S)= 6'302
Vin (V)= 230.00
Fin (Hz)= 60.00
Delay Time (ms)= 5000.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 16.150 ******* ******* 16.148
12Vsb 0.250 ******* ******* 0.250
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
------------Load--------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V ******* ******* 0.000
12Vsb ******* ******* 0.000
PWOK ******* ******* 0.000
Vin_Good ******* ******* 0.000
SMBAlert ******* ******* 0.000
-------34970----------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 12.350 11.590 12.252
12VSb 12.600 11.400 12.107
PWOK 3.460 2.500 3.247
Vin_Good 3.460 2.500 3.246
SMBAlert 3.460 2.500 3.218
IBUS 1.000 0.600 0.810
CR 0.400 ******* 0.000
Max Min Reading
------------- ---------- ---------- ----------
Vrms (V) ******** ******** 230.2416
PF 1.0000 0.9000 0.9782
THDi (%) 20.0000 * 8.0652
Irms (A) ******** ******** 0.9814
Pin (W) ******** ******** 221.0287
Pout (W) ******** ******** 200.8664
Eff (%) 99.0000 88.0000 90.8780
Load Noise Range Noise B.W
Name (V) (MHz)
------------- ----------- ---------
12V 2 20.000
12Vsb 2 20.000
PWOK 2 20.000
Vin_Good 2 20.000
SMBAlert 2 20.000
Load Vpp Noise Vpp Noise Vpp Noise
Name Max(mV) Min(mV) (mV)
------------- ------------ ------------ ------------
12V 120.000 0.000 21.510
12Vsb 120.000 0.000 3.130
PWOK ********* ********* 20.690
Vin_Good ********* ********* 19.450
SMBAlert ********* ********* 22.430
MCU Accuracy ---------------------------------------------
Spec Status Reading Status
----------- ------------- ----------------
Mcu Status 0 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Reading
-------- ---------
Vin_M 230.2500
Iin_M 0.9893
Pin_M 219.0000
Vout_M 12.2480
Iout_M 16.2813
Pout_M 199.2500
Max Min Reading
--------------------- --------- --------- ---------
Mcu_Vin_VS_Vin (%) 5.000 * 0.0036
Mcu_Vin_VS_Vin (%) 5.000 *
Mcu_Vin_VS_Vin (%) 5.000 *
Mcu_Vin_VS_Vin (%) 5.000 *
Mcu_Vin_VS_Vin (%) 5.000 *
Mcu_Vin_VS_Vin (%) 5.000 *
Mcu_Vin_VS_Vin (%) 5.000 *
Mcu_Vin_VS_Vin (%) 5.000 *
Mcu_Iin_VS_Iin (%) 5.000 * 0.7981
Mcu_Iin_VS_Iin (%) 5.000 *
Mcu_Iin_VS_Iin (%) 5.000 *
Mcu_Iin_VS_Iin (%) 5.000 *
Mcu_Iin_VS_Iin (%) 5.000 *
Mcu_Iin_VS_Iin (%) 5.000 *
Mcu_Iin_VS_Iin (%) 5.000 *
Mcu_Iin_VS_Iin (%) 5.000 *
Mcu_Pin_VS_Pin (%) 5.000 * 0.9178
Mcu_Pin_VS_Pin (%) 5.000 *
Mcu_Pin_VS_Pin (%) 5.000 *
Mcu_Pin_VS_Pin (%) 5.000 *
Mcu_Pin_VS_Pin (%) 5.000 *
Mcu_Pin_VS_Pin (%) 5.000 *
Mcu_Pin_VS_Pin (%) 5.000 *
Mcu_Pin_VS_Pin (%) 5.000 *
Mcu_Vout_VS_Vout (%) 5.000 * 0.0316
Mcu_Vout_VS_Vout (%) 5.000 *
Mcu_Vout_VS_Vout (%) 5.000 *
Mcu_Vout_VS_Vout (%) 5.000 *
Mcu_Vout_VS_Vout (%) 5.000 *
Mcu_Vout_VS_Vout (%) 5.000 *
Mcu_Vout_VS_Vout (%) 5.000 *
Mcu_Vout_VS_Vout (%) 5.000 *
Mcu_Iout_VS_Iout (%) 5.000 * 0.8277
Mcu_Iout_VS_Iout (%) 5.000 *
Mcu_Iout_VS_Iout (%) 5.000 *
Mcu_Iout_VS_Iout (%) 5.000 *
Mcu_Iout_VS_Iout (%) 5.000 *
Mcu_Iout_VS_Iout (%) 5.000 *
Mcu_Iout_VS_Iout (%) 5.000 *
Mcu_Iout_VS_Iout (%) 5.000 *
Mcu_Pout_VS_Pout (%) 5.000 * 0.7132
Mcu_Pout_VS_Pout (%) 5.000 *
Mcu_Pout_VS_Pout (%) 5.000 *
Mcu_Pout_VS_Pout (%) 5.000 *
Mcu_Pout_VS_Pout (%) 5.000 *
Mcu_Pout_VS_Pout (%) 5.000 *
Mcu_Pout_VS_Pout (%) 5.000 *
Mcu_Pout_VS_Pout (%) 5.000 *
Max Min Reading
-------------- --------- --------- ---------
Temperature 1 200.00 0.00 59.50
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Max Min Reading
-------------- --------- --------- ---------
Temperature 2 200.00 0.00 75.50
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Max Min Reading
-------- --------- --------- ---------
Fan RPM 28000 ****** 8915
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
STEP.720(UUT Test seq.720) : Input Output Accuracy Multi or Single_S3(240Va PASS
ElapsedTime (S)= 6'443
Vin (V)= 240.00
Fin (Hz)= 60.00
Delay Time (ms)= 5000.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 161.500 ******* ******* 161.497
12Vsb 2.500 ******* ******* 2.500
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
------------Load--------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V ******* ******* 0.000
12Vsb ******* ******* 0.000
PWOK ******* ******* 0.000
Vin_Good ******* ******* 0.000
SMBAlert ******* ******* 0.000
-------34970----------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 12.350 11.590 12.166
12VSb 12.600 11.400 11.994
PWOK 3.460 2.500 3.222
Vin_Good 3.460 2.500 3.226
SMBAlert 3.460 2.500 3.220
IBUS 8.200 7.800 8.003
CR 0.400 ******* -0.022
Max Min Reading
------------- ---------- ---------- ----------
Vrms (V) ******** ******** 239.4590
PF 1.0000 ******** 0.9976
THDi (%) ******** * 2.3318
Irms (A) ******** ******** 9.2211
Pin (W) ******** ******** 2202.8679
Pout (W) ******** ******** 1994.7661
Eff (%) ******** ******** 90.5531
Load Noise Range Noise B.W
Name (V) (MHz)
------------- ----------- ---------
12V 2 20.000
12Vsb 2 20.000
PWOK 2 20.000
Vin_Good 2 20.000
SMBAlert 2 20.000
Load Vpp Noise Vpp Noise Vpp Noise
Name Max(mV) Min(mV) (mV)
------------- ------------ ------------ ------------
12V 120.000 0.000 15.050
12Vsb 120.000 0.000 15.430
PWOK ********* ********* 24.910
Vin_Good ********* ********* 23.910
SMBAlert ********* ********* 26.750
MCU Accuracy ---------------------------------------------
Spec Status Reading Status
----------- ------------- ----------------
Mcu Status 0 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Reading
-------- ---------
Vin_M 238.7500
Iin_M 9.2344
Pin_M 2204.0000
Vout_M 12.2012
Iout_M 161.2500
Pout_M 1968.0000
Max Min Reading
--------------------- --------- --------- ---------
Mcu_Vin_VS_Vin (%) 2.000 * 0.2961
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 * 0.1445
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 * 0.0514
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 * 0.2886
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 * 0.1529
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 * 0.1638
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Max Min Reading
-------------- --------- --------- ---------
Temperature 1 200.00 0.00 58.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Max Min Reading
-------------- --------- --------- ---------
Temperature 2 200.00 0.00 76.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Max Min Reading
-------- --------- --------- ---------
Fan RPM 28000 ****** 11116
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
STEP.721(UUT Test seq.721) : Input Output Accuracy Multi or Single_S3(240Va PASS
ElapsedTime (S)= 6'303
Vin (V)= 240.00
Fin (Hz)= 60.00
Delay Time (ms)= 5000.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 145.350 ******* ******* 145.347
12Vsb 2.250 ******* ******* 2.250
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
------------Load--------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V ******* ******* 0.000
12Vsb ******* ******* 0.000
PWOK ******* ******* 0.000
Vin_Good ******* ******* 0.000
SMBAlert ******* ******* 0.000
-------34970----------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 12.350 11.590 12.175
12VSb 12.600 11.400 12.002
PWOK 3.460 2.500 3.226
Vin_Good 3.460 2.500 3.228
SMBAlert 3.460 2.500 3.219
IBUS ******* ******* 7.190
CR 0.400 ******* -0.020
Max Min Reading
------------- ---------- ---------- ----------
Vrms (V) ******** ******** 239.5452
PF 1.0000 ******** 0.9983
THDi (%) ******** * 2.1953
Irms (A) ******** ******** 8.2626
Pin (W) ******** ******** 1975.8239
Pout (W) ******** ******** 1796.5931
Eff (%) ******** ******** 90.9288
Load Noise Range Noise B.W
Name (V) (MHz)
------------- ----------- ---------
12V 2 20.000
12Vsb 2 20.000
PWOK 2 20.000
Vin_Good 2 20.000
SMBAlert 2 20.000
Load Vpp Noise Vpp Noise Vpp Noise
Name Max(mV) Min(mV) (mV)
------------- ------------ ------------ ------------
12V 120.000 0.000 14.410
12Vsb 120.000 0.000 14.350
PWOK ********* ********* 24.720
Vin_Good ********* ********* 23.740
SMBAlert ********* ********* 26.680
MCU Accuracy ---------------------------------------------
Spec Status Reading Status
----------- ------------- ----------------
Mcu Status 0 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Reading
-------- ---------
Vin_M 239.0000
Iin_M 8.2813
Pin_M 1976.0000
Vout_M 12.2070
Iout_M 145.2500
Pout_M 1772.0000
Max Min Reading
--------------------- --------- --------- ---------
Mcu_Vin_VS_Vin (%) 2.000 * 0.2276
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 * 0.2256
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 * 0.0089
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 * 0.2636
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 * 0.0667
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 * 0.1361
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Max Min Reading
-------------- --------- --------- ---------
Temperature 1 200.00 0.00 57.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Max Min Reading
-------------- --------- --------- ---------
Temperature 2 200.00 0.00 79.50
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Max Min Reading
-------- --------- --------- ---------
Fan RPM 28000 ****** 11116
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
STEP.722(UUT Test seq.722) : Input Output Accuracy Multi or Single_S3(240Va PASS
ElapsedTime (S)= 6'443
Vin (V)= 240.00
Fin (Hz)= 60.00
Delay Time (ms)= 5000.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 129.200 ******* ******* 129.197
12Vsb 2.000 ******* ******* 2.000
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
------------Load--------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V ******* ******* 0.000
12Vsb ******* ******* 0.000
PWOK ******* ******* 0.000
Vin_Good ******* ******* 0.000
SMBAlert ******* ******* 0.000
-------34970----------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 12.350 11.590 12.185
12VSb 12.600 11.400 12.010
PWOK 3.460 2.500 3.231
Vin_Good 3.460 2.500 3.226
SMBAlert 3.460 2.500 3.220
IBUS ******* ******* 6.388
CR 0.400 ******* -0.017
Max Min Reading
------------- ---------- ---------- ----------
Vrms (V) ******** ******** 239.6360
PF 1.0000 ******** 0.9985
THDi (%) ******** * 2.2026
Irms (A) ******** ******** 7.3166
Pin (W) ******** ******** 1750.6296
Pout (W) ******** ******** 1598.2267
Eff (%) ******** ******** 91.2944
Load Noise Range Noise B.W
Name (V) (MHz)
------------- ----------- ---------
12V 2 20.000
12Vsb 2 20.000
PWOK 2 20.000
Vin_Good 2 20.000
SMBAlert 2 20.000
Load Vpp Noise Vpp Noise Vpp Noise
Name Max(mV) Min(mV) (mV)
------------- ------------ ------------ ------------
12V 120.000 0.000 13.280
12Vsb 120.000 0.000 13.290
PWOK ********* ********* 24.670
Vin_Good ********* ********* 23.540
SMBAlert ********* ********* 25.920
MCU Accuracy ---------------------------------------------
Spec Status Reading Status
----------- ------------- ----------------
Mcu Status 0 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Reading
-------- ---------
Vin_M 239.0000
Iin_M 7.3359
Pin_M 1750.0000
Vout_M 12.2129
Iout_M 129.0000
Pout_M 1576.0000
Max Min Reading
--------------------- --------- --------- ---------
Mcu_Vin_VS_Vin (%) 2.000 * 0.2654
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 * 0.2637
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 * 0.0360
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 * 0.2325
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 * 0.1525
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 * 0.1137
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Max Min Reading
-------------- --------- --------- ---------
Temperature 1 200.00 0.00 56.50
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Max Min Reading
-------------- --------- --------- ---------
Temperature 2 200.00 0.00 80.50
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Max Min Reading
-------- --------- --------- ---------
Fan RPM 28000 ****** 11116
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
STEP.723(UUT Test seq.723) : Input Output Accuracy Multi or Single_S3(240Va PASS
ElapsedTime (S)= 6'412
Vin (V)= 240.00
Fin (Hz)= 60.00
Delay Time (ms)= 5000.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 113.050 ******* ******* 113.047
12Vsb 1.750 ******* ******* 1.750
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
------------Load--------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V ******* ******* 0.000
12Vsb ******* ******* 0.000
PWOK ******* ******* 0.000
Vin_Good ******* ******* 0.000
SMBAlert ******* ******* 0.000
-------34970----------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 12.350 11.590 12.194
12VSb 12.600 11.400 12.020
PWOK 3.460 2.500 3.233
Vin_Good 3.460 2.500 3.227
SMBAlert 3.460 2.500 3.225
IBUS ******* ******* 5.581
CR 0.400 ******* -0.015
Max Min Reading
------------- ---------- ---------- ----------
Vrms (V) ******** ******** 239.7147
PF 1.0000 ******** 0.9984
THDi (%) ******** * 2.1529
Irms (A) ******** ******** 6.3815
Pin (W) ******** ******** 1527.3492
Pout (W) ******** ******** 1399.5492
Eff (%) ******** ******** 91.6326
Load Noise Range Noise B.W
Name (V) (MHz)
------------- ----------- ---------
12V 2 20.000
12Vsb 2 20.000
PWOK 2 20.000
Vin_Good 2 20.000
SMBAlert 2 20.000
Load Vpp Noise Vpp Noise Vpp Noise
Name Max(mV) Min(mV) (mV)
------------- ------------ ------------ ------------
12V 120.000 0.000 13.170
12Vsb 120.000 0.000 11.520
PWOK ********* ********* 23.010
Vin_Good ********* ********* 23.880
SMBAlert ********* ********* 24.730
MCU Accuracy ---------------------------------------------
Spec Status Reading Status
----------- ------------- ----------------
Mcu Status 0 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Reading
-------- ---------
Vin_M 239.2500
Iin_M 6.3906
Pin_M 1524.0000
Vout_M 12.2168
Iout_M 113.0000
Pout_M 1380.0000
Max Min Reading
--------------------- --------- --------- ---------
Mcu_Vin_VS_Vin (%) 2.000 * 0.1939
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 * 0.1430
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 * 0.2193
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 * 0.1854
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 * 0.0416
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 * 0.1076
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Max Min Reading
-------------- --------- --------- ---------
Temperature 1 200.00 0.00 56.50
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Max Min Reading
-------------- --------- --------- ---------
Temperature 2 200.00 0.00 80.50
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Max Min Reading
-------- --------- --------- ---------
Fan RPM 28000 ****** 11094
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
STEP.724(UUT Test seq.724) : Input Output Accuracy Multi or Single_S3(240Va PASS
ElapsedTime (S)= 6'334
Vin (V)= 240.00
Fin (Hz)= 60.00
Delay Time (ms)= 5000.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 96.900 ******* ******* 96.897
12Vsb 1.500 ******* ******* 1.500
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
------------Load--------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V ******* ******* 0.000
12Vsb ******* ******* 0.000
PWOK ******* ******* 0.000
Vin_Good ******* ******* 0.000
SMBAlert ******* ******* 0.000
-------34970----------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 12.350 11.590 12.205
12VSb 12.600 11.400 12.029
PWOK 3.460 2.500 3.232
Vin_Good 3.460 2.500 3.237
SMBAlert 3.460 2.500 3.221
IBUS ******* ******* 4.783
CR 0.400 ******* -0.012
Max Min Reading
------------- ---------- ---------- ----------
Vrms (V) ******** ******** 239.7842
PF 1.0000 ******** 0.9982
THDi (%) ******** * 2.2775
Irms (A) ******** ******** 5.4285
Pin (W) ******** ******** 1299.2734
Pout (W) ******** ******** 1200.7045
Eff (%) ******** ******** 92.4135
Load Noise Range Noise B.W
Name (V) (MHz)
------------- ----------- ---------
12V 2 20.000
12Vsb 2 20.000
PWOK 2 20.000
Vin_Good 2 20.000
SMBAlert 2 20.000
Load Vpp Noise Vpp Noise Vpp Noise
Name Max(mV) Min(mV) (mV)
------------- ------------ ------------ ------------
12V 120.000 0.000 12.060
12Vsb 120.000 0.000 8.580
PWOK ********* ********* 22.480
Vin_Good ********* ********* 22.830
SMBAlert ********* ********* 24.350
MCU Accuracy ---------------------------------------------
Spec Status Reading Status
----------- ------------- ----------------
Mcu Status 0 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Reading
-------- ---------
Vin_M 239.5000
Iin_M 5.4453
Pin_M 1300.0000
Vout_M 12.2227
Iout_M 96.7500
Pout_M 1182.0000
Max Min Reading
--------------------- --------- --------- ---------
Mcu_Vin_VS_Vin (%) 2.000 * 0.1185
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 * 0.3096
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 * 0.0559
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 * 0.1423
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 * 0.1522
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 * 0.0560
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Max Min Reading
-------------- --------- --------- ---------
Temperature 1 200.00 0.00 56.50
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Max Min Reading
-------------- --------- --------- ---------
Temperature 2 200.00 0.00 80.50
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Max Min Reading
-------- --------- --------- ---------
Fan RPM 28000 ****** 10961
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
STEP.725(UUT Test seq.725) : Input Output Accuracy Multi or Single_S3(240Va PASS
ElapsedTime (S)= 6'319
Vin (V)= 240.00
Fin (Hz)= 60.00
Delay Time (ms)= 5000.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 80.750 ******* ******* 80.748
12Vsb 1.250 ******* ******* 1.250
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
------------Load--------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V ******* ******* 0.000
12Vsb ******* ******* 0.000
PWOK ******* ******* 0.000
Vin_Good ******* ******* 0.000
SMBAlert ******* ******* 0.000
-------34970----------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 12.350 11.590 12.214
12VSb 12.600 11.400 12.040
PWOK 3.460 2.500 3.239
Vin_Good 3.460 2.500 3.233
SMBAlert 3.460 2.500 3.217
IBUS 4.200 3.800 4.000
CR 0.400 ******* -0.010
Max Min Reading
------------- ---------- ---------- ----------
Vrms (V) ******** ******** 239.9001
PF 1.0000 ******** 0.9968
THDi (%) ******** * 2.6634
Irms (A) ******** ******** 4.4862
Pin (W) ******** ******** 1072.7322
Pout (W) ******** ******** 1001.3152
Eff (%) ******** ******** 93.3425
Load Noise Range Noise B.W
Name (V) (MHz)
------------- ----------- ---------
12V 2 20.000
12Vsb 2 20.000
PWOK 2 20.000
Vin_Good 2 20.000
SMBAlert 2 20.000
Load Vpp Noise Vpp Noise Vpp Noise
Name Max(mV) Min(mV) (mV)
------------- ------------ ------------ ------------
12V 120.000 0.000 9.250
12Vsb 120.000 0.000 6.820
PWOK ********* ********* 21.500
Vin_Good ********* ********* 21.710
SMBAlert ********* ********* 23.680
MCU Accuracy ---------------------------------------------
Spec Status Reading Status
----------- ------------- ----------------
Mcu Status 0 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Reading
-------- ---------
Vin_M 239.7500
Iin_M 4.4844
Pin_M 1072.0000
Vout_M 12.2266
Iout_M 80.6250
Pout_M 987.0000
Max Min Reading
--------------------- --------- --------- ---------
Mcu_Vin_VS_Vin (%) 2.000 * 0.0625
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 * 0.0397
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 * 0.0683
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 * 0.1015
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 * 0.1518
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 * 0.0745
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Max Min Reading
-------------- --------- --------- ---------
Temperature 1 200.00 0.00 57.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Max Min Reading
-------------- --------- --------- ---------
Temperature 2 200.00 0.00 80.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Max Min Reading
-------- --------- --------- ---------
Fan RPM 28000 ****** 10877
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
STEP.726(UUT Test seq.726) : Input Output Accuracy Multi or Single_S3(240Va PASS
ElapsedTime (S)= 6'287
Vin (V)= 240.00
Fin (Hz)= 60.00
Delay Time (ms)= 5000.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 64.600 ******* ******* 64.598
12Vsb 1.000 ******* ******* 1.000
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
------------Load--------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V ******* ******* 0.000
12Vsb ******* ******* 0.000
PWOK ******* ******* 0.000
Vin_Good ******* ******* 0.000
SMBAlert ******* ******* 0.000
-------34970----------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 12.350 11.590 12.224
12VSb 12.600 11.400 12.051
PWOK 3.460 2.500 3.240
Vin_Good 3.460 2.500 3.236
SMBAlert 3.460 2.500 3.223
IBUS ******* ******* 3.206
CR 0.400 ******* -0.007
Max Min Reading
------------- ---------- ---------- ----------
Vrms (V) ******** ******** 240.0106
PF 1.0000 ******** 0.9952
THDi (%) ******** * 2.9927
Irms (A) ******** ******** 3.5856
Pin (W) ******** ******** 856.4230
Pout (W) ******** ******** 801.6788
Eff (%) ******** ******** 93.6078
Load Noise Range Noise B.W
Name (V) (MHz)
------------- ----------- ---------
12V 2 20.000
12Vsb 2 20.000
PWOK 2 20.000
Vin_Good 2 20.000
SMBAlert 2 20.000
Load Vpp Noise Vpp Noise Vpp Noise
Name Max(mV) Min(mV) (mV)
------------- ------------ ------------ ------------
12V 120.000 0.000 8.850
12Vsb 120.000 0.000 5.340
PWOK ********* ********* 21.980
Vin_Good ********* ********* 20.890
SMBAlert ********* ********* 24.070
MCU Accuracy ---------------------------------------------
Spec Status Reading Status
----------- ------------- ----------------
Mcu Status 0 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Reading
-------- ---------
Vin_M 240.0000
Iin_M 3.5820
Pin_M 857.0000
Vout_M 12.2324
Iout_M 64.6250
Pout_M 791.0000
Max Min Reading
--------------------- --------- --------- ---------
Mcu_Vin_VS_Vin (%) 2.000 * 0.0044
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 * 0.0991
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 * 0.0674
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 * 0.0706
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 * 0.0424
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 * 0.1738
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Max Min Reading
-------------- --------- --------- ---------
Temperature 1 200.00 0.00 57.50
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Max Min Reading
-------------- --------- --------- ---------
Temperature 2 200.00 0.00 79.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Max Min Reading
-------- --------- --------- ---------
Fan RPM 28000 ****** 10798
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
STEP.727(UUT Test seq.727) : Input Output Accuracy Multi or Single_S3(240Va PASS
ElapsedTime (S)= 6'427
Vin (V)= 240.00
Fin (Hz)= 60.00
Delay Time (ms)= 5000.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 48.450 ******* ******* 48.448
12Vsb 0.750 ******* ******* 0.750
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
------------Load--------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V ******* ******* 0.000
12Vsb ******* ******* 0.000
PWOK ******* ******* 0.000
Vin_Good ******* ******* 0.000
SMBAlert ******* ******* 0.000
-------34970----------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 12.350 11.590 12.233
12VSb 12.600 11.400 12.065
PWOK 3.460 2.500 3.242
Vin_Good 3.460 2.500 3.238
SMBAlert 3.460 2.500 3.222
IBUS ******* ******* 2.406
CR 0.400 ******* -0.004
Max Min Reading
------------- ---------- ---------- ----------
Vrms (V) ******** ******** 240.0892
PF 1.0000 ******** 0.9925
THDi (%) ******** * 3.4275
Irms (A) ******** ******** 2.6974
Pin (W) ******** ******** 642.7928
Pout (W) ******** ******** 601.7284
Eff (%) ******** ******** 93.6116
Load Noise Range Noise B.W
Name (V) (MHz)
------------- ----------- ---------
12V 2 20.000
12Vsb 2 20.000
PWOK 2 20.000
Vin_Good 2 20.000
SMBAlert 2 20.000
Load Vpp Noise Vpp Noise Vpp Noise
Name Max(mV) Min(mV) (mV)
------------- ------------ ------------ ------------
12V 120.000 0.000 8.370
12Vsb 120.000 0.000 4.360
PWOK ********* ********* 21.720
Vin_Good ********* ********* 20.190
SMBAlert ********* ********* 23.520
MCU Accuracy ---------------------------------------------
Spec Status Reading Status
----------- ------------- ----------------
Mcu Status 0 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Reading
-------- ---------
Vin_M 240.0000
Iin_M 2.6914
Pin_M 643.0000
Vout_M 12.2363
Iout_M 48.5000
Pout_M 593.0000
Max Min Reading
--------------------- --------- --------- ---------
Mcu_Vin_VS_Vin (%) 2.000 * 0.0372
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 * 0.2233
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 * 0.0322
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 * 0.0238
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 * 0.1082
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 * 0.0541
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Max Min Reading
-------------- --------- --------- ---------
Temperature 1 200.00 0.00 58.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Max Min Reading
-------------- --------- --------- ---------
Temperature 2 200.00 0.00 78.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Max Min Reading
-------- --------- --------- ---------
Fan RPM 28000 ****** 9173
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
STEP.728(UUT Test seq.728) : Input Output Accuracy Multi or Single_S3(240Va PASS
ElapsedTime (S)= 6'412
Vin (V)= 240.00
Fin (Hz)= 60.00
Delay Time (ms)= 5000.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 32.300 ******* ******* 32.298
12Vsb 0.500 ******* ******* 0.500
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
------------Load--------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V ******* ******* 0.000
12Vsb ******* ******* 0.000
PWOK ******* ******* 0.000
Vin_Good ******* ******* 0.000
SMBAlert ******* ******* 0.000
-------34970----------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 12.350 11.590 12.243
12VSb 12.600 11.400 12.082
PWOK 3.460 2.500 3.247
Vin_Good 3.460 2.500 3.240
SMBAlert 3.460 2.500 3.220
IBUS 1.800 1.400 1.606
CR 0.400 ******* -0.002
Max Min Reading
------------- ---------- ---------- ----------
Vrms (V) ******** ******** 240.1657
PF 1.0000 ******** 0.9891
THDi (%) ******** * 6.7787
Irms (A) ******** ******** 1.8165
Pin (W) ******** ******** 431.5094
Pout (W) ******** ******** 401.4631
Eff (%) ******** ******** 93.0369
Load Noise Range Noise B.W
Name (V) (MHz)
------------- ----------- ---------
12V 2 20.000
12Vsb 2 20.000
PWOK 2 20.000
Vin_Good 2 20.000
SMBAlert 2 20.000
Load Vpp Noise Vpp Noise Vpp Noise
Name Max(mV) Min(mV) (mV)
------------- ------------ ------------ ------------
12V 120.000 0.000 7.580
12Vsb 120.000 0.000 3.730
PWOK ********* ********* 21.350
Vin_Good ********* ********* 20.370
SMBAlert ********* ********* 23.870
MCU Accuracy ---------------------------------------------
Spec Status Reading Status
----------- ------------- ----------------
Mcu Status 0 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Reading
-------- ---------
Vin_M 240.2500
Iin_M 1.8066
Pin_M 430.5000
Vout_M 12.2422
Iout_M 32.3750
Pout_M 396.0000
Max Min Reading
--------------------- --------- --------- ---------
Mcu_Vin_VS_Vin (%) 2.000 * 0.0351
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 * 0.5402
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 * 0.2339
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 * 0.0069
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 * 0.2393
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 * 0.1462
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Max Min Reading
-------------- --------- --------- ---------
Temperature 1 200.00 0.00 59.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Max Min Reading
-------------- --------- --------- ---------
Temperature 2 200.00 0.00 77.50
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Max Min Reading
-------- --------- --------- ---------
Fan RPM 28000 ****** 9051
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
STEP.729(UUT Test seq.729) : Input Output Accuracy Multi or Single_S3(240Va PASS
ElapsedTime (S)= 6'505
Vin (V)= 240.00
Fin (Hz)= 60.00
Delay Time (ms)= 5000.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 16.150 ******* ******* 16.148
12Vsb 0.250 ******* ******* 0.250
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
------------Load--------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V ******* ******* 0.000
12Vsb ******* ******* 0.000
PWOK ******* ******* 0.000
Vin_Good ******* ******* 0.000
SMBAlert ******* ******* 0.000
-------34970----------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 12.350 11.590 12.252
12VSb 12.600 11.400 12.108
PWOK 3.460 2.500 3.242
Vin_Good 3.460 2.500 3.249
SMBAlert 3.460 2.500 3.214
IBUS 1.000 0.600 0.811
CR 0.400 ******* 0.000
Max Min Reading
------------- ---------- ---------- ----------
Vrms (V) ******** ******** 240.2455
PF 1.0000 ******** 0.9730
THDi (%) ******** * 8.8202
Irms (A) ******** ******** 0.9451
Pin (W) ******** ******** 220.9205
Pout (W) ******** ******** 200.8666
Eff (%) ******** ******** 90.9226
Load Noise Range Noise B.W
Name (V) (MHz)
------------- ----------- ---------
12V 2 20.000
12Vsb 2 20.000
PWOK 2 20.000
Vin_Good 2 20.000
SMBAlert 2 20.000
Load Vpp Noise Vpp Noise Vpp Noise
Name Max(mV) Min(mV) (mV)
------------- ------------ ------------ ------------
12V 120.000 0.000 23.600
12Vsb 120.000 0.000 3.120
PWOK ********* ********* 20.020
Vin_Good ********* ********* 19.400
SMBAlert ********* ********* 22.050
MCU Accuracy ---------------------------------------------
Spec Status Reading Status
----------- ------------- ----------------
Mcu Status 0 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Reading
-------- ---------
Vin_M 240.2500
Iin_M 0.9492
Pin_M 219.0000
Vout_M 12.2480
Iout_M 16.2813
Pout_M 199.2500
Max Min Reading
--------------------- --------- --------- ---------
Mcu_Vin_VS_Vin (%) 5.000 * 0.0019
Mcu_Vin_VS_Vin (%) 5.000 *
Mcu_Vin_VS_Vin (%) 5.000 *
Mcu_Vin_VS_Vin (%) 5.000 *
Mcu_Vin_VS_Vin (%) 5.000 *
Mcu_Vin_VS_Vin (%) 5.000 *
Mcu_Vin_VS_Vin (%) 5.000 *
Mcu_Vin_VS_Vin (%) 5.000 *
Mcu_Iin_VS_Iin (%) 5.000 * 0.4405
Mcu_Iin_VS_Iin (%) 5.000 *
Mcu_Iin_VS_Iin (%) 5.000 *
Mcu_Iin_VS_Iin (%) 5.000 *
Mcu_Iin_VS_Iin (%) 5.000 *
Mcu_Iin_VS_Iin (%) 5.000 *
Mcu_Iin_VS_Iin (%) 5.000 *
Mcu_Iin_VS_Iin (%) 5.000 *
Mcu_Pin_VS_Pin (%) 5.000 * 0.8693
Mcu_Pin_VS_Pin (%) 5.000 *
Mcu_Pin_VS_Pin (%) 5.000 *
Mcu_Pin_VS_Pin (%) 5.000 *
Mcu_Pin_VS_Pin (%) 5.000 *
Mcu_Pin_VS_Pin (%) 5.000 *
Mcu_Pin_VS_Pin (%) 5.000 *
Mcu_Pin_VS_Pin (%) 5.000 *
Mcu_Vout_VS_Vout (%) 5.000 * 0.0316
Mcu_Vout_VS_Vout (%) 5.000 *
Mcu_Vout_VS_Vout (%) 5.000 *
Mcu_Vout_VS_Vout (%) 5.000 *
Mcu_Vout_VS_Vout (%) 5.000 *
Mcu_Vout_VS_Vout (%) 5.000 *
Mcu_Vout_VS_Vout (%) 5.000 *
Mcu_Vout_VS_Vout (%) 5.000 *
Mcu_Iout_VS_Iout (%) 5.000 * 0.8277
Mcu_Iout_VS_Iout (%) 5.000 *
Mcu_Iout_VS_Iout (%) 5.000 *
Mcu_Iout_VS_Iout (%) 5.000 *
Mcu_Iout_VS_Iout (%) 5.000 *
Mcu_Iout_VS_Iout (%) 5.000 *
Mcu_Iout_VS_Iout (%) 5.000 *
Mcu_Iout_VS_Iout (%) 5.000 *
Mcu_Pout_VS_Pout (%) 5.000 * 0.7132
Mcu_Pout_VS_Pout (%) 5.000 *
Mcu_Pout_VS_Pout (%) 5.000 *
Mcu_Pout_VS_Pout (%) 5.000 *
Mcu_Pout_VS_Pout (%) 5.000 *
Mcu_Pout_VS_Pout (%) 5.000 *
Mcu_Pout_VS_Pout (%) 5.000 *
Mcu_Pout_VS_Pout (%) 5.000 *
Max Min Reading
-------------- --------- --------- ---------
Temperature 1 200.00 0.00 59.50
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Max Min Reading
-------------- --------- --------- ---------
Temperature 2 200.00 0.00 75.50
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Max Min Reading
-------- --------- --------- ---------
Fan RPM 28000 ****** 8915
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
STEP.730(UUT Test seq.730) : Input Output Accuracy Multi or Single_S3(100Va PASS
ElapsedTime (S)= 6'505
Vin (V)= 100.00
Fin (Hz)= 60.00
Delay Time (ms)= 5000.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 79.500 ******* ******* 79.498
12Vsb 2.500 ******* ******* 2.500
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
------------Load--------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V ******* ******* 0.000
12Vsb ******* ******* 0.000
PWOK ******* ******* 0.000
Vin_Good ******* ******* 0.000
SMBAlert ******* ******* 0.000
-------34970----------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 12.350 11.590 12.215
12VSb 12.600 11.400 12.005
PWOK 3.460 2.500 3.238
Vin_Good 3.460 2.500 3.233
SMBAlert 3.460 2.500 3.219
IBUS ******* ******* 3.940
CR 0.400 ******* -0.010
Max Min Reading
------------- ---------- ---------- ----------
Vrms (V) ******** ******** 99.1521
PF 1.0000 ******** 0.9994
THDi (%) ******** * 2.8675
Irms (A) 13.0000 ******** 11.5909
Pin (W) ******** ******** 1148.5220
Pout (W) ******** ******** 1001.0655
Eff (%) ******** ******** 87.1612
Load Noise Range Noise B.W
Name (V) (MHz)
------------- ----------- ---------
12V 2 20.000
12Vsb 2 20.000
PWOK 2 20.000
Vin_Good 2 20.000
SMBAlert 2 20.000
Load Vpp Noise Vpp Noise Vpp Noise
Name Max(mV) Min(mV) (mV)
------------- ------------ ------------ ------------
12V 120.000 0.000 12.130
12Vsb 120.000 0.000 13.650
PWOK ********* ********* 25.740
Vin_Good ********* ********* 23.680
SMBAlert ********* ********* 26.820
MCU Accuracy ---------------------------------------------
Spec Status Reading Status
----------- ------------- ----------------
Mcu Status 0 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Reading
-------- ---------
Vin_M 98.0000
Iin_M 11.6250
Pin_M 1140.0000
Vout_M 12.2285
Iout_M 79.3750
Pout_M 971.0000
Max Min Reading
--------------------- --------- --------- ---------
Mcu_Vin_VS_Vin (%) 2.000 * 1.1620
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 * 0.2942
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 * 0.7420
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 * 0.1114
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 * 0.1542
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 * 0.0058
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Max Min Reading
-------------- --------- --------- ---------
Temperature 1 200.00 0.00 59.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Max Min Reading
-------------- --------- --------- ---------
Temperature 2 200.00 0.00 73.50
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Max Min Reading
-------- --------- --------- ---------
Fan RPM 28000 ****** 11115
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
STEP.731(UUT Test seq.731) : Harmonic Multi UUT_Test_S2 ---- (2'137) ------ PASS
Standard = 2 (1:IEC-1000-3-2, 2:Japan)
Class = 0 (0:A, 1:B, 2:C, 3:D, 4:A-1)
Delay Time (ms)= 2000
Load Loading
Name (A/Ohm/V)
------------- ----------
12V 79.500
12Vsb 2.500
PWOK 0.000
Vin_Good 0.000
SMBAlert 0.000
Max Min Reading
------------- --------- --------- ---------
Pin (W) ******* ******* 1149.35
THD (%) ******* ******* 2.94
Input Voltage Reading (V) = 99.15
Spectrum Limit Reading
------------- --------- ---------
1 ********* 11.590
2 2.484 0.140
3 5.290 0.201
4 0.989 0.032
5 2.622 0.048
6 0.690 0.043
7 1.771 0.023
8 0.529 0.042
9 0.920 0.048
10 0.423 0.034
11 0.759 0.029
12 0.353 0.012
13 0.483 0.008
14 0.302 0.015
15 0.345 0.031
16 0.264 0.016
17 0.304 0.019
18 0.235 0.006
19 0.272 0.036
20 0.212 0.018
21 0.246 0.045
22 0.192 0.016
23 0.225 0.039
24 0.176 0.012
25 0.207 0.030
26 0.163 0.007
27 0.192 0.034
28 0.151 0.012
29 0.178 0.029
30 0.141 0.012
31 0.167 0.042
32 0.132 0.012
33 0.157 0.073
34 0.124 0.028
35 0.148 0.061
36 0.118 0.030
37 0.140 0.026
38 0.111 0.009
39 0.133 0.039
40 0.106 0.022
STEP.732(UUT Test seq.732) : Input Output Accuracy Multi or Single_S3(100Va PASS
ElapsedTime (S)= 6'287
Vin (V)= 100.00
Fin (Hz)= 60.00
Delay Time (ms)= 5000.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 71.550 ******* ******* 71.548
12Vsb 2.250 ******* ******* 2.250
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
------------Load--------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V ******* ******* 0.000
12Vsb ******* ******* 0.000
PWOK ******* ******* 0.000
Vin_Good ******* ******* 0.000
SMBAlert ******* ******* 0.000
-------34970----------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 12.350 11.590 12.219
12VSb 12.600 11.400 12.011
PWOK 3.460 2.500 3.240
Vin_Good 3.460 2.500 3.235
SMBAlert 3.460 2.500 3.219
IBUS ******* ******* 3.544
CR 0.400 ******* -0.009
Max Min Reading
------------- ---------- ---------- ----------
Vrms (V) ******** ******** 99.2696
PF 1.0000 ******** 0.9995
THDi (%) ******** * 2.7417
Irms (A) ******** ******** 10.3856
Pin (W) ******** ******** 1030.4237
Pout (W) ******** ******** 901.2908
Eff (%) ******** ******** 87.4680
Load Noise Range Noise B.W
Name (V) (MHz)
------------- ----------- ---------
12V 2 20.000
12Vsb 2 20.000
PWOK 2 20.000
Vin_Good 2 20.000
SMBAlert 2 20.000
Load Vpp Noise Vpp Noise Vpp Noise
Name Max(mV) Min(mV) (mV)
------------- ------------ ------------ ------------
12V 120.000 0.000 11.950
12Vsb 120.000 0.000 12.900
PWOK ********* ********* 25.650
Vin_Good ********* ********* 23.750
SMBAlert ********* ********* 28.110
MCU Accuracy ---------------------------------------------
Spec Status Reading Status
----------- ------------- ----------------
Mcu Status 0 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Reading
-------- ---------
Vin_M 98.2500
Iin_M 10.4063
Pin_M 1023.0000
Vout_M 12.2305
Iout_M 71.5000
Pout_M 874.0000
Max Min Reading
--------------------- --------- --------- ---------
Mcu_Vin_VS_Vin (%) 2.000 * 1.0271
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 * 0.1987
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 * 0.7205
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 * 0.0910
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 * 0.0668
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 * 0.0306
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Max Min Reading
-------------- --------- --------- ---------
Temperature 1 200.00 0.00 58.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Max Min Reading
-------------- --------- --------- ---------
Temperature 2 200.00 0.00 73.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Max Min Reading
-------- --------- --------- ---------
Fan RPM 28000 ****** 11116
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
STEP.733(UUT Test seq.733) : Harmonic Multi UUT_Test_S2 ---- (2'122) ------ PASS
Standard = 2 (1:IEC-1000-3-2, 2:Japan)
Class = 0 (0:A, 1:B, 2:C, 3:D, 4:A-1)
Delay Time (ms)= 2000
Load Loading
Name (A/Ohm/V)
------------- ----------
12V 71.550
12Vsb 2.250
PWOK 0.000
Vin_Good 0.000
SMBAlert 0.000
Max Min Reading
------------- --------- --------- ---------
Pin (W) ******* ******* 1030.29
THD (%) ******* ******* 2.70
Input Voltage Reading (V) = 99.28
Spectrum Limit Reading
------------- --------- ---------
1 ********* 10.385
2 2.484 0.134
3 5.290 0.176
4 0.989 0.009
5 2.622 0.031
6 0.690 0.022
7 1.771 0.042
8 0.529 0.022
9 0.920 0.040
10 0.423 0.005
11 0.759 0.024
12 0.353 0.022
13 0.483 0.028
14 0.302 0.002
15 0.345 0.031
16 0.264 0.011
17 0.304 0.042
18 0.235 0.016
19 0.272 0.029
20 0.212 0.011
21 0.246 0.024
22 0.192 0.009
23 0.225 0.031
24 0.176 0.026
25 0.207 0.032
26 0.163 0.020
27 0.192 0.044
28 0.151 0.004
29 0.178 0.050
30 0.141 0.004
31 0.167 0.063
32 0.132 0.025
33 0.157 0.045
34 0.124 0.020
35 0.148 0.015
36 0.118 0.024
37 0.140 0.009
38 0.111 0.005
39 0.133 0.024
40 0.106 0.010
STEP.734(UUT Test seq.734) : Input Output Accuracy Multi or Single_S3(100Va PASS
ElapsedTime (S)= 6'318
Vin (V)= 100.00
Fin (Hz)= 60.00
Delay Time (ms)= 5000.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 63.600 ******* ******* 63.598
12Vsb 2.000 ******* ******* 2.000
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
------------Load--------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V ******* ******* 0.000
12Vsb ******* ******* 0.000
PWOK ******* ******* 0.000
Vin_Good ******* ******* 0.000
SMBAlert ******* ******* 0.000
-------34970----------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 12.350 11.590 12.224
12VSb 12.600 11.400 12.018
PWOK 3.460 2.500 3.238
Vin_Good 3.460 2.500 3.241
SMBAlert 3.460 2.500 3.215
IBUS ******* ******* 3.156
CR 0.400 ******* -0.008
Max Min Reading
------------- ---------- ---------- ----------
Vrms (V) ******** ******** 99.3953
PF 1.0000 ******** 0.9995
THDi (%) ******** * 2.7152
Irms (A) ******** ******** 9.1969
Pin (W) ******** ******** 913.6584
Pout (W) ******** ******** 801.4375
Eff (%) ******** ******** 87.7174
Load Noise Range Noise B.W
Name (V) (MHz)
------------- ----------- ---------
12V 2 20.000
12Vsb 2 20.000
PWOK 2 20.000
Vin_Good 2 20.000
SMBAlert 2 20.000
Load Vpp Noise Vpp Noise Vpp Noise
Name Max(mV) Min(mV) (mV)
------------- ------------ ------------ ------------
12V 120.000 0.000 12.330
12Vsb 120.000 0.000 12.310
PWOK ********* ********* 24.600
Vin_Good ********* ********* 23.340
SMBAlert ********* ********* 27.460
MCU Accuracy ---------------------------------------------
Spec Status Reading Status
----------- ------------- ----------------
Mcu Status 0 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Reading
-------- ---------
Vin_M 98.3750
Iin_M 9.2188
Pin_M 907.0000
Vout_M 12.2324
Iout_M 63.6250
Pout_M 778.0000
Max Min Reading
--------------------- --------- --------- ---------
Mcu_Vin_VS_Vin (%) 2.000 * 1.0265
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 * 0.2374
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 * 0.7288
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 * 0.0706
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 * 0.0431
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 * 0.0767
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Max Min Reading
-------------- --------- --------- ---------
Temperature 1 200.00 0.00 58.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Max Min Reading
-------------- --------- --------- ---------
Temperature 2 200.00 0.00 71.50
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Max Min Reading
-------- --------- --------- ---------
Fan RPM 28000 ****** 11115
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
STEP.735(UUT Test seq.735) : Harmonic Multi UUT_Test_S2 ---- (2'122) ------ PASS
Standard = 2 (1:IEC-1000-3-2, 2:Japan)
Class = 0 (0:A, 1:B, 2:C, 3:D, 4:A-1)
Delay Time (ms)= 2000
Load Loading
Name (A/Ohm/V)
------------- ----------
12V 63.600
12Vsb 2.000
PWOK 0.000
Vin_Good 0.000
SMBAlert 0.000
Max Min Reading
------------- --------- --------- ---------
Pin (W) ******* ******* 913.25
THD (%) ******* ******* 2.96
Input Voltage Reading (V) = 99.40
Spectrum Limit Reading
------------- --------- ---------
1 ********* 9.184
2 2.484 0.099
3 5.290 0.204
4 0.989 0.025
5 2.622 0.045
6 0.690 0.016
7 1.771 0.037
8 0.529 0.021
9 0.920 0.014
10 0.423 0.034
11 0.759 0.013
12 0.353 0.012
13 0.483 0.010
14 0.302 0.005
15 0.345 0.024
16 0.264 0.035
17 0.304 0.018
18 0.235 0.015
19 0.272 0.019
20 0.212 0.009
21 0.246 0.026
22 0.192 0.003
23 0.225 0.040
24 0.176 0.013
25 0.207 0.028
26 0.163 0.025
27 0.192 0.025
28 0.151 0.016
29 0.178 0.037
30 0.141 0.008
31 0.167 0.050
32 0.132 0.007
33 0.157 0.030
34 0.124 0.006
35 0.148 0.039
36 0.118 0.008
37 0.140 0.029
38 0.111 0.021
39 0.133 0.008
40 0.106 0.008
STEP.736(UUT Test seq.736) : Input Output Accuracy Multi or Single_S3(100Va PASS
ElapsedTime (S)= 6'334
Vin (V)= 100.00
Fin (Hz)= 60.00
Delay Time (ms)= 5000.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 55.650 ******* ******* 55.648
12Vsb 1.750 ******* ******* 1.750
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
------------Load--------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V ******* ******* 0.000
12Vsb ******* ******* 0.000
PWOK ******* ******* 0.000
Vin_Good ******* ******* 0.000
SMBAlert ******* ******* 0.000
-------34970----------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 12.350 11.590 12.229
12VSb 12.600 11.400 12.027
PWOK 3.460 2.500 3.236
Vin_Good 3.460 2.500 3.241
SMBAlert 3.460 2.500 3.217
IBUS ******* ******* 2.759
CR 0.400 ******* -0.006
Max Min Reading
------------- ---------- ---------- ----------
Vrms (V) ******** ******** 99.4802
PF 1.0000 ******** 0.9995
THDi (%) ******** * 2.8746
Irms (A) ******** ******** 8.0353
Pin (W) ******** ******** 798.9543
Pout (W) ******** ******** 701.5613
Eff (%) ******** ******** 87.8100
Load Noise Range Noise B.W
Name (V) (MHz)
------------- ----------- ---------
12V 2 20.000
12Vsb 2 20.000
PWOK 2 20.000
Vin_Good 2 20.000
SMBAlert 2 20.000
Load Vpp Noise Vpp Noise Vpp Noise
Name Max(mV) Min(mV) (mV)
------------- ------------ ------------ ------------
12V 120.000 0.000 11.480
12Vsb 120.000 0.000 11.740
PWOK ********* ********* 23.950
Vin_Good ********* ********* 22.350
SMBAlert ********* ********* 25.620
MCU Accuracy ---------------------------------------------
Spec Status Reading Status
----------- ------------- ----------------
Mcu Status 0 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Reading
-------- ---------
Vin_M 98.5000
Iin_M 8.0625
Pin_M 794.0000
Vout_M 12.2344
Iout_M 55.6875
Pout_M 681.0000
Max Min Reading
--------------------- --------- --------- ---------
Mcu_Vin_VS_Vin (%) 2.000 * 0.9854
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 * 0.3386
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 * 0.6201
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 * 0.0442
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 * 0.0713
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 * 0.0712
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Max Min Reading
-------------- --------- --------- ---------
Temperature 1 200.00 0.00 57.50
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Max Min Reading
-------------- --------- --------- ---------
Temperature 2 200.00 0.00 70.50
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Max Min Reading
-------- --------- --------- ---------
Fan RPM 28000 ****** 11115
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
STEP.737(UUT Test seq.737) : Harmonic Multi UUT_Test_S2 ---- (2'137) ------ PASS
Standard = 2 (1:IEC-1000-3-2, 2:Japan)
Class = 0 (0:A, 1:B, 2:C, 3:D, 4:A-1)
Delay Time (ms)= 2000
Load Loading
Name (A/Ohm/V)
------------- ----------
12V 55.650
12Vsb 1.750
PWOK 0.000
Vin_Good 0.000
SMBAlert 0.000
Max Min Reading
------------- --------- --------- ---------
Pin (W) ******* ******* 798.68
THD (%) ******* ******* 2.74
Input Voltage Reading (V) = 99.48
Spectrum Limit Reading
------------- --------- ---------
1 ********* 8.046
2 2.484 0.080
3 5.290 0.148
4 0.989 0.006
5 2.622 0.044
6 0.690 0.008
7 1.771 0.046
8 0.529 0.025
9 0.920 0.022
10 0.423 0.006
11 0.759 0.006
12 0.353 0.021
13 0.483 0.015
14 0.302 0.015
15 0.345 0.010
16 0.264 0.010
17 0.304 0.033
18 0.235 0.015
19 0.272 0.035
20 0.212 0.002
21 0.246 0.026
22 0.192 0.003
23 0.225 0.026
24 0.176 0.009
25 0.207 0.030
26 0.163 0.005
27 0.192 0.025
28 0.151 0.013
29 0.178 0.022
30 0.141 0.018
31 0.167 0.038
32 0.132 0.013
33 0.157 0.041
34 0.124 0.014
35 0.148 0.023
36 0.118 0.004
37 0.140 0.022
38 0.111 0.012
39 0.133 0.015
40 0.106 0.015
STEP.738(UUT Test seq.738) : Input Output Accuracy Multi or Single_S3(100Va PASS
ElapsedTime (S)= 6'428
Vin (V)= 100.00
Fin (Hz)= 60.00
Delay Time (ms)= 5000.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 47.700 ******* ******* 47.698
12Vsb 1.500 ******* ******* 1.500
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
------------Load--------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V ******* ******* 0.000
12Vsb ******* ******* 0.000
PWOK ******* ******* 0.000
Vin_Good ******* ******* 0.000
SMBAlert ******* ******* 0.000
-------34970----------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 12.350 11.590 12.235
12VSb 12.600 11.400 12.034
PWOK 3.460 2.500 3.243
Vin_Good 3.460 2.500 3.237
SMBAlert 3.460 2.500 3.221
IBUS ******* ******* 2.367
CR 0.400 ******* -0.005
Max Min Reading
------------- ---------- ---------- ----------
Vrms (V) ******** ******** 99.5837
PF 1.0000 ******** 0.9995
THDi (%) ******** * 2.9347
Irms (A) ******** ******** 6.8893
Pin (W) ******** ******** 685.6912
Pout (W) ******** ******** 601.6266
Eff (%) ******** ******** 87.7402
Load Noise Range Noise B.W
Name (V) (MHz)
------------- ----------- ---------
12V 2 20.000
12Vsb 2 20.000
PWOK 2 20.000
Vin_Good 2 20.000
SMBAlert 2 20.000
Load Vpp Noise Vpp Noise Vpp Noise
Name Max(mV) Min(mV) (mV)
------------- ------------ ------------ ------------
12V 120.000 0.000 11.310
12Vsb 120.000 0.000 9.960
PWOK ********* ********* 24.870
Vin_Good ********* ********* 23.170
SMBAlert ********* ********* 26.560
MCU Accuracy ---------------------------------------------
Spec Status Reading Status
----------- ------------- ----------------
Mcu Status 0 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Reading
-------- ---------
Vin_M 98.7500
Iin_M 6.8828
Pin_M 680.0000
Vout_M 12.2383
Iout_M 47.7500
Pout_M 584.0000
Max Min Reading
--------------------- --------- --------- ---------
Mcu_Vin_VS_Vin (%) 2.000 * 0.8372
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 * 0.0947
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 * 0.8300
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 * 0.0277
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 * 0.1096
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 * 0.0726
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Max Min Reading
-------------- --------- --------- ---------
Temperature 1 200.00 0.00 58.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Max Min Reading
-------------- --------- --------- ---------
Temperature 2 200.00 0.00 69.50
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Max Min Reading
-------- --------- --------- ---------
Fan RPM 28000 ****** 11075
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
STEP.739(UUT Test seq.739) : Harmonic Multi UUT_Test_S2 ---- (2'138) ------ PASS
Standard = 2 (1:IEC-1000-3-2, 2:Japan)
Class = 0 (0:A, 1:B, 2:C, 3:D, 4:A-1)
Delay Time (ms)= 2000
Load Loading
Name (A/Ohm/V)
------------- ----------
12V 47.700
12Vsb 1.500
PWOK 0.000
Vin_Good 0.000
SMBAlert 0.000
Max Min Reading
------------- --------- --------- ---------
Pin (W) ******* ******* 680.53
THD (%) ******* ******* 2.97
Input Voltage Reading (V) = 99.59
Spectrum Limit Reading
------------- --------- ---------
1 ********* 6.837
2 2.484 0.043
3 5.290 0.150
4 0.989 0.024
5 2.622 0.027
6 0.690 0.013
7 1.771 0.027
8 0.529 0.013
9 0.920 0.030
10 0.423 0.014
11 0.759 0.013
12 0.353 0.011
13 0.483 0.013
14 0.302 0.006
15 0.345 0.003
16 0.264 0.008
17 0.304 0.016
18 0.235 0.006
19 0.272 0.030
20 0.212 0.012
21 0.246 0.025
22 0.192 0.009
23 0.225 0.029
24 0.176 0.006
25 0.207 0.038
26 0.163 0.013
27 0.192 0.025
28 0.151 0.003
29 0.178 0.029
30 0.141 0.006
31 0.167 0.022
32 0.132 0.011
33 0.157 0.028
34 0.124 0.009
35 0.148 0.009
36 0.118 0.003
37 0.140 0.015
38 0.111 0.005
39 0.133 0.027
40 0.106 0.007
STEP.740(UUT Test seq.740) : Input Output Accuracy Multi or Single_S3(100Va PASS
ElapsedTime (S)= 6'411
Vin (V)= 100.00
Fin (Hz)= 60.00
Delay Time (ms)= 5000.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 39.750 ******* ******* 39.748
12Vsb 1.250 ******* ******* 1.250
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
------------Load--------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V ******* ******* 0.000
12Vsb ******* ******* 0.000
PWOK ******* ******* 0.000
Vin_Good ******* ******* 0.000
SMBAlert ******* ******* 0.000
-------34970----------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 12.350 11.590 12.239
12VSb 12.600 11.400 12.043
PWOK 3.460 2.500 3.245
Vin_Good 3.460 2.500 3.238
SMBAlert 3.460 2.500 3.221
IBUS ******* ******* 1.973
CR 0.400 ******* -0.004
Max Min Reading
------------- ---------- ---------- ----------
Vrms (V) ******** ******** 99.6633
PF 1.0000 ******** 0.9995
THDi (%) ******** * 2.7618
Irms (A) ******** ******** 5.6737
Pin (W) ******** ******** 565.1871
Pout (W) ******** ******** 501.5075
Eff (%) ******** ******** 88.7330
Load Noise Range Noise B.W
Name (V) (MHz)
------------- ----------- ---------
12V 2 20.000
12Vsb 2 20.000
PWOK 2 20.000
Vin_Good 2 20.000
SMBAlert 2 20.000
Load Vpp Noise Vpp Noise Vpp Noise
Name Max(mV) Min(mV) (mV)
------------- ------------ ------------ ------------
12V 120.000 0.000 10.940
12Vsb 120.000 0.000 7.080
PWOK ********* ********* 23.820
Vin_Good ********* ********* 22.730
SMBAlert ********* ********* 26.220
MCU Accuracy ---------------------------------------------
Spec Status Reading Status
----------- ------------- ----------------
Mcu Status 0 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Reading
-------- ---------
Vin_M 99.1250
Iin_M 5.6875
Pin_M 563.0000
Vout_M 12.2402
Iout_M 39.8125
Pout_M 487.0000
Max Min Reading
--------------------- --------- --------- ---------
Mcu_Vin_VS_Vin (%) 2.000 * 0.5401
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 * 0.2437
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 * 0.3870
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 * 0.0134
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 * 0.1633
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 * 0.1121
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Max Min Reading
-------------- --------- --------- ---------
Temperature 1 200.00 0.00 58.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Max Min Reading
-------------- --------- --------- ---------
Temperature 2 200.00 0.00 69.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Max Min Reading
-------- --------- --------- ---------
Fan RPM 28000 ****** 10919
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
STEP.741(UUT Test seq.741) : Harmonic Multi UUT_Test_S2 ---- (2'137) ------ PASS
Standard = 2 (1:IEC-1000-3-2, 2:Japan)
Class = 0 (0:A, 1:B, 2:C, 3:D, 4:A-1)
Delay Time (ms)= 2000
Load Loading
Name (A/Ohm/V)
------------- ----------
12V 39.750
12Vsb 1.250
PWOK 0.000
Vin_Good 0.000
SMBAlert 0.000
Max Min Reading
------------- --------- --------- ---------
Pin (W) ******* ******* 563.30
THD (%) ******* ******* 2.68
Input Voltage Reading (V) = 99.66
Spectrum Limit Reading
------------- --------- ---------
1 ********* 5.663
2 2.484 0.022
3 5.290 0.120
4 0.989 0.003
5 2.622 0.031
6 0.690 0.013
7 1.771 0.015
8 0.529 0.009
9 0.920 0.002
10 0.423 0.015
11 0.759 0.006
12 0.353 0.003
13 0.483 0.008
14 0.302 0.018
15 0.345 0.009
16 0.264 0.008
17 0.304 0.021
18 0.235 0.003
19 0.272 0.021
20 0.212 0.009
21 0.246 0.023
22 0.192 0.003
23 0.225 0.033
24 0.176 0.006
25 0.207 0.034
26 0.163 0.011
27 0.192 0.032
28 0.151 0.002
29 0.178 0.022
30 0.141 0.014
31 0.167 0.020
32 0.132 0.009
33 0.157 0.018
34 0.124 0.007
35 0.148 0.020
36 0.118 0.004
37 0.140 0.022
38 0.111 0.008
39 0.133 0.013
40 0.106 0.004
STEP.742(UUT Test seq.742) : Input Output Accuracy Multi or Single_S3(100Va PASS
ElapsedTime (S)= 6'287
Vin (V)= 100.00
Fin (Hz)= 60.00
Delay Time (ms)= 5000.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 31.800 ******* ******* 31.798
12Vsb 1.000 ******* ******* 1.000
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
------------Load--------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V ******* ******* 0.000
12Vsb ******* ******* 0.000
PWOK ******* ******* 0.000
Vin_Good ******* ******* 0.000
SMBAlert ******* ******* 0.000
-------34970----------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 12.350 11.590 12.242
12VSb 12.600 11.400 12.054
PWOK 3.460 2.500 3.245
Vin_Good 3.460 2.500 3.244
SMBAlert 3.460 2.500 3.214
IBUS ******* ******* 1.582
CR 0.400 ******* -0.002
Max Min Reading
------------- ---------- ---------- ----------
Vrms (V) ******** ******** 99.7508
PF 1.0000 ******** 0.9995
THDi (%) ******** * 2.9622
Irms (A) ******** ******** 4.5295
Pin (W) ******** ******** 451.5815
Pout (W) ******** ******** 401.3313
Eff (%) ******** ******** 88.8724
Load Noise Range Noise B.W
Name (V) (MHz)
------------- ----------- ---------
12V 2 20.000
12Vsb 2 20.000
PWOK 2 20.000
Vin_Good 2 20.000
SMBAlert 2 20.000
Load Vpp Noise Vpp Noise Vpp Noise
Name Max(mV) Min(mV) (mV)
------------- ------------ ------------ ------------
12V 120.000 0.000 9.820
12Vsb 120.000 0.000 5.370
PWOK ********* ********* 22.410
Vin_Good ********* ********* 21.180
SMBAlert ********* ********* 23.300
MCU Accuracy ---------------------------------------------
Spec Status Reading Status
----------- ------------- ----------------
Mcu Status 0 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Reading
-------- ---------
Vin_M 99.2500
Iin_M 4.5469
Pin_M 451.0000
Vout_M 12.2422
Iout_M 31.8750
Pout_M 390.0000
Max Min Reading
--------------------- --------- --------- ---------
Mcu_Vin_VS_Vin (%) 2.000 * 0.5020
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 * 0.3840
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 * 0.1288
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 * 0.0009
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 * 0.2428
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 * 0.1855
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Max Min Reading
-------------- --------- --------- ---------
Temperature 1 200.00 0.00 58.50
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Max Min Reading
-------------- --------- --------- ---------
Temperature 2 200.00 0.00 69.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Max Min Reading
-------- --------- --------- ---------
Fan RPM 28000 ****** 10806
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
STEP.743(UUT Test seq.743) : Harmonic Multi UUT_Test_S2 ---- (2'138) ------ PASS
Standard = 2 (1:IEC-1000-3-2, 2:Japan)
Class = 0 (0:A, 1:B, 2:C, 3:D, 4:A-1)
Delay Time (ms)= 2000
Load Loading
Name (A/Ohm/V)
------------- ----------
12V 31.800
12Vsb 1.000
PWOK 0.000
Vin_Good 0.000
SMBAlert 0.000
Max Min Reading
------------- --------- --------- ---------
Pin (W) ******* ******* 450.52
THD (%) ******* ******* 2.89
Input Voltage Reading (V) = 99.75
Spectrum Limit Reading
------------- --------- ---------
1 ********* 4.520
2 2.484 0.004
3 5.290 0.100
4 0.989 0.010
5 2.622 0.027
6 0.690 0.009
7 1.771 0.011
8 0.529 0.009
9 0.920 0.013
10 0.423 0.006
11 0.759 0.013
12 0.353 0.008
13 0.483 0.012
14 0.302 0.007
15 0.345 0.014
16 0.264 0.010
17 0.304 0.023
18 0.235 0.004
19 0.272 0.022
20 0.212 0.004
21 0.246 0.023
22 0.192 0.005
23 0.225 0.026
24 0.176 0.003
25 0.207 0.026
26 0.163 0.005
27 0.192 0.020
28 0.151 0.002
29 0.178 0.017
30 0.141 0.002
31 0.167 0.017
32 0.132 0.001
33 0.157 0.015
34 0.124 0.003
35 0.148 0.022
36 0.118 0.004
37 0.140 0.019
38 0.111 0.004
39 0.133 0.013
40 0.106 0.003
STEP.744(UUT Test seq.744) : Input Output Accuracy Multi or Single_S3(100Va PASS
ElapsedTime (S)= 6'412
Vin (V)= 100.00
Fin (Hz)= 60.00
Delay Time (ms)= 5000.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 23.850 ******* ******* 23.848
12Vsb 0.750 ******* ******* 0.750
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
------------Load--------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V ******* ******* 0.000
12Vsb ******* ******* 0.000
PWOK ******* ******* 0.000
Vin_Good ******* ******* 0.000
SMBAlert ******* ******* 0.000
-------34970----------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 12.350 11.590 12.247
12VSb 12.600 11.400 12.068
PWOK 3.460 2.500 3.243
Vin_Good 3.460 2.500 3.247
SMBAlert 3.460 2.500 3.213
IBUS ******* ******* 1.190
CR 0.400 ******* -0.001
Max Min Reading
------------- ---------- ---------- ----------
Vrms (V) ******** ******** 99.8536
PF 1.0000 ******** 0.9993
THDi (%) ******** * 3.3349
Irms (A) ******** ******** 3.3785
Pin (W) ******** ******** 337.1081
Pout (W) ******** ******** 301.1237
Eff (%) ******** ******** 89.3256
Load Noise Range Noise B.W
Name (V) (MHz)
------------- ----------- ---------
12V 2 20.000
12Vsb 2 20.000
PWOK 2 20.000
Vin_Good 2 20.000
SMBAlert 2 20.000
Load Vpp Noise Vpp Noise Vpp Noise
Name Max(mV) Min(mV) (mV)
------------- ------------ ------------ ------------
12V 120.000 0.000 10.050
12Vsb 120.000 0.000 4.660
PWOK ********* ********* 22.130
Vin_Good ********* ********* 21.790
SMBAlert ********* ********* 24.490
MCU Accuracy ---------------------------------------------
Spec Status Reading Status
----------- ------------- ----------------
Mcu Status 0 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Reading
-------- ---------
Vin_M 99.3750
Iin_M 3.4023
Pin_M 338.0000
Vout_M 12.2441
Iout_M 23.9688
Pout_M 293.5000
Max Min Reading
--------------------- --------- --------- ---------
Mcu_Vin_VS_Vin (%) 2.000 * 0.4793
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 * 0.7049
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 * 0.2646
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 * 0.0272
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 * 0.5080
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 * 0.4886
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Max Min Reading
-------------- --------- --------- ---------
Temperature 1 200.00 0.00 58.50
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Max Min Reading
-------------- --------- --------- ---------
Temperature 2 200.00 0.00 68.50
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Max Min Reading
-------- --------- --------- ---------
Fan RPM 28000 ****** 9144
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
STEP.745(UUT Test seq.745) : Harmonic Multi UUT_Test_S2 ---- (2'277) ------ PASS
Standard = 2 (1:IEC-1000-3-2, 2:Japan)
Class = 0 (0:A, 1:B, 2:C, 3:D, 4:A-1)
Delay Time (ms)= 2000
Load Loading
Name (A/Ohm/V)
------------- ----------
12V 23.850
12Vsb 0.750
PWOK 0.000
Vin_Good 0.000
SMBAlert 0.000
Max Min Reading
------------- --------- --------- ---------
Pin (W) ******* ******* 336.91
THD (%) ******* ******* 3.26
Input Voltage Reading (V) = 99.85
Spectrum Limit Reading
------------- --------- ---------
1 ********* 3.373
2 2.484 0.013
3 5.290 0.076
4 0.989 0.004
5 2.622 0.025
6 0.690 0.002
7 1.771 0.004
8 0.529 0.008
9 0.920 0.008
10 0.423 0.007
11 0.759 0.008
12 0.353 0.006
13 0.483 0.018
14 0.302 0.007
15 0.345 0.015
16 0.264 0.002
17 0.304 0.024
18 0.235 0.004
19 0.272 0.023
20 0.212 0.002
21 0.246 0.021
22 0.192 0.005
23 0.225 0.027
24 0.176 0.004
25 0.207 0.023
26 0.163 0.005
27 0.192 0.021
28 0.151 0.002
29 0.178 0.017
30 0.141 0.004
31 0.167 0.016
32 0.132 0.002
33 0.157 0.019
34 0.124 0.003
35 0.148 0.017
36 0.118 0.003
37 0.140 0.010
38 0.111 0.001
39 0.133 0.011
40 0.106 0.002
STEP.746(UUT Test seq.746) : Input Output Accuracy Multi or Single_S3(100Va PASS
ElapsedTime (S)= 6'318
Vin (V)= 100.00
Fin (Hz)= 60.00
Delay Time (ms)= 5000.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 15.900 ******* ******* 15.898
12Vsb 0.500 ******* ******* 0.500
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
------------Load--------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V ******* ******* 0.000
12Vsb ******* ******* 0.000
PWOK ******* ******* 0.000
Vin_Good ******* ******* 0.000
SMBAlert ******* ******* 0.000
-------34970----------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 12.350 11.590 12.250
12VSb 12.600 11.400 12.082
PWOK 3.460 2.500 3.242
Vin_Good 3.460 2.500 3.247
SMBAlert 3.460 2.500 3.219
IBUS ******* ******* 0.797
CR 0.400 ******* 0.000
Max Min Reading
------------- ---------- ---------- ----------
Vrms (V) ******** ******** 99.9725
PF 1.0000 ******** 0.9986
THDi (%) ******** * 4.2336
Irms (A) ******** ******** 2.3010
Pin (W) ******** ******** 229.7071
Pout (W) ******** ******** 200.7938
Eff (%) ******** ******** 87.4129
Load Noise Range Noise B.W
Name (V) (MHz)
------------- ----------- ---------
12V 2 20.000
12Vsb 2 20.000
PWOK 2 20.000
Vin_Good 2 20.000
SMBAlert 2 20.000
Load Vpp Noise Vpp Noise Vpp Noise
Name Max(mV) Min(mV) (mV)
------------- ------------ ------------ ------------
12V 120.000 0.000 18.720
12Vsb 120.000 0.000 3.920
PWOK ********* ********* 21.380
Vin_Good ********* ********* 20.980
SMBAlert ********* ********* 23.340
MCU Accuracy ---------------------------------------------
Spec Status Reading Status
----------- ------------- ----------------
Mcu Status 0 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Reading
-------- ---------
Vin_M 99.6250
Iin_M 2.3164
Pin_M 230.2500
Vout_M 12.2480
Iout_M 16.0313
Pout_M 196.2500
Max Min Reading
--------------------- --------- --------- ---------
Mcu_Vin_VS_Vin (%) 2.000 * 0.3476
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Vin_VS_Vin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 * 0.6685
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Iin_VS_Iin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 * 0.2363
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Pin_VS_Pin (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 * 0.0195
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Vout_VS_Vout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 * 0.8407
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Iout_VS_Iout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 * 0.7689
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Mcu_Pout_VS_Pout (%) 2.000 *
Max Min Reading
-------------- --------- --------- ---------
Temperature 1 200.00 0.00 59.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Max Min Reading
-------------- --------- --------- ---------
Temperature 2 200.00 0.00 67.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Max Min Reading
-------- --------- --------- ---------
Fan RPM 28000 ****** 8995
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
STEP.747(UUT Test seq.747) : Harmonic Multi UUT_Test_S2 ---- (2'168) ------ PASS
Standard = 2 (1:IEC-1000-3-2, 2:Japan)
Class = 0 (0:A, 1:B, 2:C, 3:D, 4:A-1)
Delay Time (ms)= 2000
Load Loading
Name (A/Ohm/V)
------------- ----------
12V 15.900
12Vsb 0.500
PWOK 0.000
Vin_Good 0.000
SMBAlert 0.000
Max Min Reading
------------- --------- --------- ---------
Pin (W) ******* ******* 229.80
THD (%) ******* ******* 4.18
Input Voltage Reading (V) = 99.97
Spectrum Limit Reading
------------- --------- ---------
1 ********* 2.298
2 2.484 0.002
3 5.290 0.065
4 0.989 0.005
5 2.622 0.026
6 0.690 0.006
7 1.771 0.010
8 0.529 0.003
9 0.920 0.011
10 0.423 0.004
11 0.759 0.010
12 0.353 0.003
13 0.483 0.011
14 0.302 0.005
15 0.345 0.016
16 0.264 0.003
17 0.304 0.022
18 0.235 0.001
19 0.272 0.022
20 0.212 0.002
21 0.246 0.024
22 0.192 0.002
23 0.225 0.020
24 0.176 0.003
25 0.207 0.019
26 0.163 0.001
27 0.192 0.019
28 0.151 0.004
29 0.178 0.013
30 0.141 0.003
31 0.167 0.013
32 0.132 0.001
33 0.157 0.012
34 0.124 0.003
35 0.148 0.011
36 0.118 0.001
37 0.140 0.012
38 0.111 0.002
39 0.133 0.007
40 0.106 0.002
STEP.748(UUT Test seq.748) : Input Output Accuracy Multi or Single_S3(100Va PASS
ElapsedTime (S)= 6'459
Vin (V)= 100.00
Fin (Hz)= 60.00
Delay Time (ms)= 5000.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 7.950 ******* ******* 7.948
12Vsb 0.250 ******* ******* 0.250
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
------------Load--------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V ******* ******* 0.000
12Vsb ******* ******* 0.000
PWOK ******* ******* 0.000
Vin_Good ******* ******* 0.000
SMBAlert ******* ******* 0.000
-------34970----------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 12.350 11.590 12.256
12VSb 12.600 11.400 12.105
PWOK 3.460 2.500 3.249
Vin_Good 3.460 2.500 3.243
SMBAlert 3.460 2.500 3.220
IBUS ******* ******* 0.407
CR 0.400 ******* 0.002
Max Min Reading
------------- ---------- ---------- ----------
Vrms (V) ******** ******** 100.0626
PF 1.0000 ******** 0.9939
THDi (%) ******** * 5.9188
Irms (A) ******** ******** 1.1962
Pin (W) ******** ******** 118.9721
Pout (W) ******** ******** 100.4357
Eff (%) ******** ******** 84.4195
Load Noise Range Noise B.W
Name (V) (MHz)
------------- ----------- ---------
12V 2 20.000
12Vsb 2 20.000
PWOK 2 20.000
Vin_Good 2 20.000
SMBAlert 2 20.000
Load Vpp Noise Vpp Noise Vpp Noise
Name Max(mV) Min(mV) (mV)
------------- ------------ ------------ ------------
12V 120.000 0.000 9.810
12Vsb 120.000 0.000 3.010
PWOK ********* ********* 20.500
Vin_Good ********* ********* 19.000
SMBAlert ********* ********* 22.370
MCU Accuracy ---------------------------------------------
Spec Status Reading Status
----------- ------------- ----------------
Mcu Status 0 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Reading
-------- ---------
Vin_M 99.7500
Iin_M 1.2207
Pin_M 121.2500
Vout_M 12.2500
Iout_M 8.1406
Pout_M 99.6250
Max Min Reading
--------------------- --------- --------- ---------
Mcu_Vin_VS_Vin (%) 5.000 * 0.3124
Mcu_Vin_VS_Vin (%) 5.000 *
Mcu_Vin_VS_Vin (%) 5.000 *
Mcu_Vin_VS_Vin (%) 5.000 *
Mcu_Vin_VS_Vin (%) 5.000 *
Mcu_Vin_VS_Vin (%) 5.000 *
Mcu_Vin_VS_Vin (%) 5.000 *
Mcu_Vin_VS_Vin (%) 5.000 *
Mcu_Iin_VS_Iin (%) 5.000 * 2.0464
Mcu_Iin_VS_Iin (%) 5.000 *
Mcu_Iin_VS_Iin (%) 5.000 *
Mcu_Iin_VS_Iin (%) 5.000 *
Mcu_Iin_VS_Iin (%) 5.000 *
Mcu_Iin_VS_Iin (%) 5.000 *
Mcu_Iin_VS_Iin (%) 5.000 *
Mcu_Iin_VS_Iin (%) 5.000 *
Mcu_Pin_VS_Pin (%) 5.000 * 1.9146
Mcu_Pin_VS_Pin (%) 5.000 *
Mcu_Pin_VS_Pin (%) 5.000 *
Mcu_Pin_VS_Pin (%) 5.000 *
Mcu_Pin_VS_Pin (%) 5.000 *
Mcu_Pin_VS_Pin (%) 5.000 *
Mcu_Pin_VS_Pin (%) 5.000 *
Mcu_Pin_VS_Pin (%) 5.000 *
Mcu_Vout_VS_Vout (%) 5.000 * 0.0519
Mcu_Vout_VS_Vout (%) 5.000 *
Mcu_Vout_VS_Vout (%) 5.000 *
Mcu_Vout_VS_Vout (%) 5.000 *
Mcu_Vout_VS_Vout (%) 5.000 *
Mcu_Vout_VS_Vout (%) 5.000 *
Mcu_Vout_VS_Vout (%) 5.000 *
Mcu_Vout_VS_Vout (%) 5.000 *
Mcu_Iout_VS_Iout (%) 5.000 * 2.4285
Mcu_Iout_VS_Iout (%) 5.000 *
Mcu_Iout_VS_Iout (%) 5.000 *
Mcu_Iout_VS_Iout (%) 5.000 *
Mcu_Iout_VS_Iout (%) 5.000 *
Mcu_Iout_VS_Iout (%) 5.000 *
Mcu_Iout_VS_Iout (%) 5.000 *
Mcu_Iout_VS_Iout (%) 5.000 *
Mcu_Pout_VS_Pout (%) 5.000 * 2.2751
Mcu_Pout_VS_Pout (%) 5.000 *
Mcu_Pout_VS_Pout (%) 5.000 *
Mcu_Pout_VS_Pout (%) 5.000 *
Mcu_Pout_VS_Pout (%) 5.000 *
Mcu_Pout_VS_Pout (%) 5.000 *
Mcu_Pout_VS_Pout (%) 5.000 *
Mcu_Pout_VS_Pout (%) 5.000 *
Max Min Reading
-------------- --------- --------- ---------
Temperature 1 200.00 0.00 60.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Max Min Reading
-------------- --------- --------- ---------
Temperature 2 200.00 0.00 67.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Max Min Reading
-------- --------- --------- ---------
Fan RPM 28000 ****** 8845
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
STEP.749(UUT Test seq.749) : Harmonic Multi UUT_Test_S2 ---- (2'137) ------ PASS
Standard = 2 (1:IEC-1000-3-2, 2:Japan)
Class = 0 (0:A, 1:B, 2:C, 3:D, 4:A-1)
Delay Time (ms)= 2000
Load Loading
Name (A/Ohm/V)
------------- ----------
12V 7.950
12Vsb 0.250
PWOK 0.000
Vin_Good 0.000
SMBAlert 0.000
Max Min Reading
------------- --------- --------- ---------
Pin (W) ******* ******* 119.25
THD (%) ******* ******* 6.80
Input Voltage Reading (V) = 100.06
Spectrum Limit Reading
------------- --------- ---------
1 ********* 1.196
2 2.484 0.004
3 5.290 0.050
4 0.989 0.008
5 2.622 0.022
6 0.690 0.010
7 1.771 0.019
8 0.529 0.012
9 0.920 0.005
10 0.423 0.010
11 0.759 0.008
12 0.353 0.006
13 0.483 0.015
14 0.302 0.005
15 0.345 0.019
16 0.264 0.003
17 0.304 0.022
18 0.235 0.002
19 0.272 0.019
20 0.212 0.001
21 0.246 0.018
22 0.192 0.000
23 0.225 0.016
24 0.176 0.001
25 0.207 0.013
26 0.163 0.001
27 0.192 0.011
28 0.151 0.001
29 0.178 0.010
30 0.141 0.001
31 0.167 0.008
32 0.132 0.001
33 0.157 0.007
34 0.124 0.002
35 0.148 0.006
36 0.118 0.001
37 0.140 0.006
38 0.111 0.001
39 0.133 0.004
40 0.106 0.001
STEP.750(UUT Test seq.750) : 61512 Ac Source ACDC Mode_Multi_S2 ---- (0'219 PASS
(The Report Format of this Sequence was not found)
STEP.751(UUT Test seq.751) : AC Source ON/OFF(input source)_Multi_S2 ---- ( PASS
(The Report Format of this Sequence was not found)
STEP.752(UUT Test seq.752) : Set Input Condition_Load_S4 ---- (0'016) ----- PASS
Vin (V)= 164.000
Fin (Hz)= 30.000
Load Loading
Name (A/Ohm/V)
------------- ----------
12V 90.0900
12Vsb 1.7500
PWOK 0.0000
Vin_Good 0.0000
SMBAlert 0.0000
STEP.753(UUT Test seq.753) : Set Drop Time ---- (0'000) ------------------- PASS
Drop Time= 10
STEP.754(UUT Test seq.754) : AC_DC Line Sag Surge 80611N-2_Multi_S2(DropOut PASS
ElapsedTime (S)= 3'931
Vin (V)= 164.00
Fin (Hz)= 30.00
Delay Time (ms)= 3000.00
Drop Time (ms)= 10.00
Drop Recovery Time(ms)= 500.00
Drop Voltage (v)= 0.00
Drop Frequency (Hz)= 30.00
Repeat Count = 1
Degree = 0
Duty cycle (%)= 100.000000
Load Loading Vpk Max Vpk Min Vpk High Vpk Low
Name (A/Ohm/V) (V) (V) (V) (V)
------------- ----------- --------- --------- --------- ---------
12V 90.090 12.810 11.590 12.229 12.207
12Vsb 1.750 12.600 11.400 12.053 12.042
PWOK 0.000 3.460 2.500 3.264 3.271
Vin_Good 0.000 3.460 ********* 3.259 0.057
SMBAlert 0.000 3.460 ********* 3.260 3.260
STEP.755(UUT Test seq.755) : I2C Read Status Multi_S6(DropOut H_164Vdc - 10 PASS
Adderss :B0
Command Page00 :060200
Command Page01 :060201
Status Word :79
Status Byte :78
Status VOUT :7A
Status IOUT :7B
Status INPUT :7C
Status TEMPERATURE :7D
Status CML :7E
Status FANS :81
---------------------------------
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
----------------------------------
Word_Page_00 : 0
Word_Page_01 : 0
Status_Byte_P00 : 0
Status_Byte_P01 : 0
Status_VOUT_P00 : 0
Status_VOUT_P01 : 0
Status_IOUT_P00 : 0
Status_IOUT_P01 : 0
Status_INPUT_P00 : 0
Status_INPUT_P01 : 0
Status_TEM_P00 : 0
Status_TEM_P01 : 0
Status_CML_P00 : 0
Status_CML_P01 : 0
Status_FANS_P00 : 0
Status_FANS_P01 : 0
STEP.756(UUT Test seq.756) : AC_DC Line Sag Surge 80611N-2_Multi_S2(DropOut PASS
ElapsedTime (S)= 3'884
Vin (V)= 164.00
Fin (Hz)= 30.00
Delay Time (ms)= 3000.00
Drop Time (ms)= 10.00
Drop Recovery Time(ms)= 500.00
Drop Voltage (v)= 0.00
Drop Frequency (Hz)= 30.00
Repeat Count = 1
Degree = 0
Duty cycle (%)= 100.000000
Load Loading Vpk Max Vpk Min Vpk High Vpk Low
Name (A/Ohm/V) (V) (V) (V) (V)
------------- ----------- --------- --------- --------- ---------
12V 90.090 12.810 11.590 12.230 12.211
12Vsb 1.750 12.600 11.400 12.052 12.044
PWOK 0.000 3.460 2.500 3.264 3.271
Vin_Good 0.000 3.460 ********* 3.259 0.060
SMBAlert 0.000 3.460 ********* 3.260 3.258
STEP.757(UUT Test seq.757) : I2C Read Status Multi_S6(DropOut H_164Vdc - 10 PASS
Adderss :B0
Command Page00 :060200
Command Page01 :060201
Status Word :79
Status Byte :78
Status VOUT :7A
Status IOUT :7B
Status INPUT :7C
Status TEMPERATURE :7D
Status CML :7E
Status FANS :81
---------------------------------
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
----------------------------------
Word_Page_00 : 0
Word_Page_01 : 0
Status_Byte_P00 : 0
Status_Byte_P01 : 0
Status_VOUT_P00 : 0
Status_VOUT_P01 : 0
Status_IOUT_P00 : 0
Status_IOUT_P01 : 0
Status_INPUT_P00 : 0
Status_INPUT_P01 : 0
Status_TEM_P00 : 0
Status_TEM_P01 : 0
Status_CML_P00 : 0
Status_CML_P01 : 0
Status_FANS_P00 : 0
Status_FANS_P01 : 0
STEP.758(UUT Test seq.758) : AC_DC Line Sag Surge 80611N-2_Multi_S2(DropOut PASS
ElapsedTime (S)= 3'869
Vin (V)= 164.00
Fin (Hz)= 30.00
Delay Time (ms)= 3000.00
Drop Time (ms)= 10.00
Drop Recovery Time(ms)= 500.00
Drop Voltage (v)= 0.00
Drop Frequency (Hz)= 30.00
Repeat Count = 1
Degree = 0
Duty cycle (%)= 100.000000
Load Loading Vpk Max Vpk Min Vpk High Vpk Low
Name (A/Ohm/V) (V) (V) (V) (V)
------------- ----------- --------- --------- --------- ---------
12V 90.090 12.810 11.590 12.230 12.209
12Vsb 1.750 12.600 11.400 12.052 12.044
PWOK 0.000 3.460 2.500 3.264 3.272
Vin_Good 0.000 3.460 ********* 3.257 0.058
SMBAlert 0.000 3.460 ********* 3.259 3.258
STEP.759(UUT Test seq.759) : I2C Read Status Multi_S6(DropOut H_164Vdc - 10 PASS
Adderss :B0
Command Page00 :060200
Command Page01 :060201
Status Word :79
Status Byte :78
Status VOUT :7A
Status IOUT :7B
Status INPUT :7C
Status TEMPERATURE :7D
Status CML :7E
Status FANS :81
---------------------------------
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
----------------------------------
Word_Page_00 : 0
Word_Page_01 : 0
Status_Byte_P00 : 0
Status_Byte_P01 : 0
Status_VOUT_P00 : 0
Status_VOUT_P01 : 0
Status_IOUT_P00 : 0
Status_IOUT_P01 : 0
Status_INPUT_P00 : 0
Status_INPUT_P01 : 0
Status_TEM_P00 : 0
Status_TEM_P01 : 0
Status_CML_P00 : 0
Status_CML_P01 : 0
Status_FANS_P00 : 0
Status_FANS_P01 : 0
STEP.760(UUT Test seq.760) : AC_DC Line Sag Surge 80611N-2_Multi_S2(DropOut PASS
ElapsedTime (S)= 3'884
Vin (V)= 164.00
Fin (Hz)= 30.00
Delay Time (ms)= 3000.00
Drop Time (ms)= 10.00
Drop Recovery Time(ms)= 500.00
Drop Voltage (v)= 0.00
Drop Frequency (Hz)= 30.00
Repeat Count = 1
Degree = 0
Duty cycle (%)= 100.000000
Load Loading Vpk Max Vpk Min Vpk High Vpk Low
Name (A/Ohm/V) (V) (V) (V) (V)
------------- ----------- --------- --------- --------- ---------
12V 90.090 12.810 11.590 12.229 12.209
12Vsb 1.750 12.600 11.400 12.052 12.044
PWOK 0.000 3.460 2.500 3.265 3.273
Vin_Good 0.000 3.460 ********* 3.257 0.060
SMBAlert 0.000 3.460 ********* 3.260 3.257
STEP.761(UUT Test seq.761) : I2C Read Status Multi_S6(DropOut H_164Vdc - 10 PASS
Adderss :B0
Command Page00 :060200
Command Page01 :060201
Status Word :79
Status Byte :78
Status VOUT :7A
Status IOUT :7B
Status INPUT :7C
Status TEMPERATURE :7D
Status CML :7E
Status FANS :81
---------------------------------
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
----------------------------------
Word_Page_00 : 0
Word_Page_01 : 0
Status_Byte_P00 : 0
Status_Byte_P01 : 0
Status_VOUT_P00 : 0
Status_VOUT_P01 : 0
Status_IOUT_P00 : 0
Status_IOUT_P01 : 0
Status_INPUT_P00 : 0
Status_INPUT_P01 : 0
Status_TEM_P00 : 0
Status_TEM_P01 : 0
Status_CML_P00 : 0
Status_CML_P01 : 0
Status_FANS_P00 : 0
Status_FANS_P01 : 0
STEP.762(UUT Test seq.762) : AC_DC Line Sag Surge 80611N-2_Multi_S2(DropOut PASS
ElapsedTime (S)= 3'884
Vin (V)= 164.00
Fin (Hz)= 30.00
Delay Time (ms)= 3000.00
Drop Time (ms)= 10.00
Drop Recovery Time(ms)= 500.00
Drop Voltage (v)= 0.00
Drop Frequency (Hz)= 30.00
Repeat Count = 1
Degree = 0
Duty cycle (%)= 100.000000
Load Loading Vpk Max Vpk Min Vpk High Vpk Low
Name (A/Ohm/V) (V) (V) (V) (V)
------------- ----------- --------- --------- --------- ---------
12V 90.090 12.810 11.590 12.229 12.209
12Vsb 1.750 12.600 11.400 12.052 12.044
PWOK 0.000 3.460 2.500 3.265 3.271
Vin_Good 0.000 3.460 ********* 3.259 0.056
SMBAlert 0.000 3.460 ********* 3.260 3.259
STEP.763(UUT Test seq.763) : I2C Read Status Multi_S6(DropOut H_164Vdc - 10 PASS
Adderss :B0
Command Page00 :060200
Command Page01 :060201
Status Word :79
Status Byte :78
Status VOUT :7A
Status IOUT :7B
Status INPUT :7C
Status TEMPERATURE :7D
Status CML :7E
Status FANS :81
---------------------------------
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
----------------------------------
Word_Page_00 : 0
Word_Page_01 : 0
Status_Byte_P00 : 0
Status_Byte_P01 : 0
Status_VOUT_P00 : 0
Status_VOUT_P01 : 0
Status_IOUT_P00 : 0
Status_IOUT_P01 : 0
Status_INPUT_P00 : 0
Status_INPUT_P01 : 0
Status_TEM_P00 : 0
Status_TEM_P01 : 0
Status_CML_P00 : 0
Status_CML_P01 : 0
Status_FANS_P00 : 0
Status_FANS_P01 : 0
STEP.764(UUT Test seq.764) : AC_DC Line Sag Surge 80611N-2_Multi_S2(DropOut PASS
ElapsedTime (S)= 3'869
Vin (V)= 164.00
Fin (Hz)= 30.00
Delay Time (ms)= 3000.00
Drop Time (ms)= 10.00
Drop Recovery Time(ms)= 500.00
Drop Voltage (v)= 0.00
Drop Frequency (Hz)= 30.00
Repeat Count = 1
Degree = 0
Duty cycle (%)= 100.000000
Load Loading Vpk Max Vpk Min Vpk High Vpk Low
Name (A/Ohm/V) (V) (V) (V) (V)
------------- ----------- --------- --------- --------- ---------
12V 90.090 12.810 11.590 12.229 12.211
12Vsb 1.750 12.600 11.400 12.052 12.042
PWOK 0.000 3.460 2.500 3.266 3.271
Vin_Good 0.000 3.460 ********* 3.257 0.058
SMBAlert 0.000 3.460 ********* 3.260 3.258
STEP.765(UUT Test seq.765) : I2C Read Status Multi_S6(DropOut H_164Vdc - 10 PASS
Adderss :B0
Command Page00 :060200
Command Page01 :060201
Status Word :79
Status Byte :78
Status VOUT :7A
Status IOUT :7B
Status INPUT :7C
Status TEMPERATURE :7D
Status CML :7E
Status FANS :81
---------------------------------
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
----------------------------------
Word_Page_00 : 0
Word_Page_01 : 0
Status_Byte_P00 : 0
Status_Byte_P01 : 0
Status_VOUT_P00 : 0
Status_VOUT_P01 : 0
Status_IOUT_P00 : 0
Status_IOUT_P01 : 0
Status_INPUT_P00 : 0
Status_INPUT_P01 : 0
Status_TEM_P00 : 0
Status_TEM_P01 : 0
Status_CML_P00 : 0
Status_CML_P01 : 0
Status_FANS_P00 : 0
Status_FANS_P01 : 0
STEP.766(UUT Test seq.766) : AC_DC Line Sag Surge 80611N-2_Multi_S2(DropOut PASS
ElapsedTime (S)= 3'869
Vin (V)= 164.00
Fin (Hz)= 30.00
Delay Time (ms)= 3000.00
Drop Time (ms)= 10.00
Drop Recovery Time(ms)= 500.00
Drop Voltage (v)= 0.00
Drop Frequency (Hz)= 30.00
Repeat Count = 1
Degree = 0
Duty cycle (%)= 100.000000
Load Loading Vpk Max Vpk Min Vpk High Vpk Low
Name (A/Ohm/V) (V) (V) (V) (V)
------------- ----------- --------- --------- --------- ---------
12V 90.090 12.810 11.590 12.228 12.209
12Vsb 1.750 12.600 11.400 12.050 12.042
PWOK 0.000 3.460 2.500 3.265 3.271
Vin_Good 0.000 3.460 ********* 3.257 0.058
SMBAlert 0.000 3.460 ********* 3.260 3.259
STEP.767(UUT Test seq.767) : I2C Read Status Multi_S6(DropOut H_164Vdc - 10 PASS
Adderss :B0
Command Page00 :060200
Command Page01 :060201
Status Word :79
Status Byte :78
Status VOUT :7A
Status IOUT :7B
Status INPUT :7C
Status TEMPERATURE :7D
Status CML :7E
Status FANS :81
---------------------------------
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
----------------------------------
Word_Page_00 : 0
Word_Page_01 : 0
Status_Byte_P00 : 0
Status_Byte_P01 : 0
Status_VOUT_P00 : 0
Status_VOUT_P01 : 0
Status_IOUT_P00 : 0
Status_IOUT_P01 : 0
Status_INPUT_P00 : 0
Status_INPUT_P01 : 0
Status_TEM_P00 : 0
Status_TEM_P01 : 0
Status_CML_P00 : 0
Status_CML_P01 : 0
Status_FANS_P00 : 0
Status_FANS_P01 : 0
STEP.768(UUT Test seq.768) : AC_DC Line Sag Surge 80611N-2_Multi_S2(DropOut PASS
ElapsedTime (S)= 3'869
Vin (V)= 164.00
Fin (Hz)= 30.00
Delay Time (ms)= 3000.00
Drop Time (ms)= 10.00
Drop Recovery Time(ms)= 500.00
Drop Voltage (v)= 0.00
Drop Frequency (Hz)= 30.00
Repeat Count = 1
Degree = 0
Duty cycle (%)= 100.000000
Load Loading Vpk Max Vpk Min Vpk High Vpk Low
Name (A/Ohm/V) (V) (V) (V) (V)
------------- ----------- --------- --------- --------- ---------
12V 90.090 12.810 11.590 12.228 12.208
12Vsb 1.750 12.600 11.400 12.052 12.043
PWOK 0.000 3.460 2.500 3.264 3.270
Vin_Good 0.000 3.460 ********* 3.257 0.057
SMBAlert 0.000 3.460 ********* 3.259 3.257
STEP.769(UUT Test seq.769) : I2C Read Status Multi_S6(DropOut H_164Vdc - 10 PASS
Adderss :B0
Command Page00 :060200
Command Page01 :060201
Status Word :79
Status Byte :78
Status VOUT :7A
Status IOUT :7B
Status INPUT :7C
Status TEMPERATURE :7D
Status CML :7E
Status FANS :81
---------------------------------
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
----------------------------------
Word_Page_00 : 0
Word_Page_01 : 0
Status_Byte_P00 : 0
Status_Byte_P01 : 0
Status_VOUT_P00 : 0
Status_VOUT_P01 : 0
Status_IOUT_P00 : 0
Status_IOUT_P01 : 0
Status_INPUT_P00 : 0
Status_INPUT_P01 : 0
Status_TEM_P00 : 0
Status_TEM_P01 : 0
Status_CML_P00 : 0
Status_CML_P01 : 0
Status_FANS_P00 : 0
Status_FANS_P01 : 0
STEP.770(UUT Test seq.770) : AC_DC Line Sag Surge 80611N-2_Multi_S2(DropOut PASS
ElapsedTime (S)= 3'962
Vin (V)= 164.00
Fin (Hz)= 30.00
Delay Time (ms)= 3000.00
Drop Time (ms)= 10.00
Drop Recovery Time(ms)= 500.00
Drop Voltage (v)= 0.00
Drop Frequency (Hz)= 30.00
Repeat Count = 1
Degree = 0
Duty cycle (%)= 100.000000
Load Loading Vpk Max Vpk Min Vpk High Vpk Low
Name (A/Ohm/V) (V) (V) (V) (V)
------------- ----------- --------- --------- --------- ---------
12V 90.090 12.810 11.590 12.229 12.208
12Vsb 1.750 12.600 11.400 12.051 12.043
PWOK 0.000 3.460 2.500 3.265 3.271
Vin_Good 0.000 3.460 ********* 3.257 0.056
SMBAlert 0.000 3.460 ********* 3.260 3.258
STEP.771(UUT Test seq.771) : I2C Read Status Multi_S6(DropOut H_164Vdc - 10 PASS
Adderss :B0
Command Page00 :060200
Command Page01 :060201
Status Word :79
Status Byte :78
Status VOUT :7A
Status IOUT :7B
Status INPUT :7C
Status TEMPERATURE :7D
Status CML :7E
Status FANS :81
---------------------------------
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
----------------------------------
Word_Page_00 : 0
Word_Page_01 : 0
Status_Byte_P00 : 0
Status_Byte_P01 : 0
Status_VOUT_P00 : 0
Status_VOUT_P01 : 0
Status_IOUT_P00 : 0
Status_IOUT_P01 : 0
Status_INPUT_P00 : 0
Status_INPUT_P01 : 0
Status_TEM_P00 : 0
Status_TEM_P01 : 0
Status_CML_P00 : 0
Status_CML_P01 : 0
Status_FANS_P00 : 0
Status_FANS_P01 : 0
STEP.772(UUT Test seq.772) : AC_DC Line Sag Surge 80611N-2_Multi_S2(DropOut PASS
ElapsedTime (S)= 3'884
Vin (V)= 164.00
Fin (Hz)= 30.00
Delay Time (ms)= 3000.00
Drop Time (ms)= 10.00
Drop Recovery Time(ms)= 500.00
Drop Voltage (v)= 0.00
Drop Frequency (Hz)= 30.00
Repeat Count = 1
Degree = 0
Duty cycle (%)= 100.000000
Load Loading Vpk Max Vpk Min Vpk High Vpk Low
Name (A/Ohm/V) (V) (V) (V) (V)
------------- ----------- --------- --------- --------- ---------
12V 90.090 12.810 11.590 12.228 12.209
12Vsb 1.750 12.600 11.400 12.052 12.044
PWOK 0.000 3.460 2.500 3.264 3.271
Vin_Good 0.000 3.460 ********* 3.259 0.061
SMBAlert 0.000 3.460 ********* 3.259 3.258
STEP.773(UUT Test seq.773) : I2C Read Status Multi_S6(DropOut H_164Vdc - 10 PASS
Adderss :B0
Command Page00 :060200
Command Page01 :060201
Status Word :79
Status Byte :78
Status VOUT :7A
Status IOUT :7B
Status INPUT :7C
Status TEMPERATURE :7D
Status CML :7E
Status FANS :81
---------------------------------
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
----------------------------------
Word_Page_00 : 0
Word_Page_01 : 0
Status_Byte_P00 : 0
Status_Byte_P01 : 0
Status_VOUT_P00 : 0
Status_VOUT_P01 : 0
Status_IOUT_P00 : 0
Status_IOUT_P01 : 0
Status_INPUT_P00 : 0
Status_INPUT_P01 : 0
Status_TEM_P00 : 0
Status_TEM_P01 : 0
Status_CML_P00 : 0
Status_CML_P01 : 0
Status_FANS_P00 : 0
Status_FANS_P01 : 0
STEP.774(UUT Test seq.774) : AC Source ON/OFF(input source)_Multi_S2 ---- ( PASS
(The Report Format of this Sequence was not found)
STEP.775(UUT Test seq.775) : Input Output Accuracy Multi or Single_S3(240Vd PASS
ElapsedTime (S)= 6'458
Vin (V)= 240.00
Fin (Hz)= 30.00
Delay Time (ms)= 5000.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 161.500 ******* ******* 161.497
12Vsb 2.500 ******* ******* 2.500
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
------------Load--------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V ******* ******* 0.000
12Vsb ******* ******* 0.000
PWOK ******* ******* 0.000
Vin_Good ******* ******* 0.000
SMBAlert ******* ******* 0.000
-------34970----------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 12.350 11.590 12.165
12VSb 12.600 11.400 11.996
PWOK 3.460 2.500 3.222
Vin_Good 3.460 2.500 3.222
SMBAlert 3.460 2.500 3.226
IBUS 8.200 7.800 8.003
CR 0.400 ******* -0.022
Max Min Reading
------------- ---------- ---------- ----------
Vrms (V) ******** ******** 239.5874
PF 1.0000 ******** 1.0000
THDi (%) ******** * 479.5569
Irms (A) 9.3000 ******** 9.1933
Pin (W) ******** ******** 2202.5737
Pout (W) ******** ******** 1994.5308
Eff (%) 99.0000 89.0000 90.5546
Load Noise Range Noise B.W
Name (V) (MHz)
------------- ----------- ---------
12V 2 20.000
12Vsb 2 20.000
PWOK 2 20.000
Vin_Good 2 20.000
SMBAlert 2 20.000
Load Vpp Noise Vpp Noise Vpp Noise
Name Max(mV) Min(mV) (mV)
------------- ------------ ------------ ------------
12V 120.000 0.000 14.750
12Vsb 120.000 0.000 15.880
PWOK ********* ********* 23.740
Vin_Good ********* ********* 24.640
SMBAlert ********* ********* 25.300
MCU Accuracy ---------------------------------------------
Spec Status Reading Status
----------- ------------- ----------------
Mcu Status 0 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Reading
-------- ---------
Vin_M 240.0000
Iin_M 9.2031
Pin_M 2208.0000
Vout_M 12.2012
Iout_M 161.2500
Pout_M 1968.0000
Max Min Reading
--------------------- --------- --------- ---------
Mcu_Vin_VS_Vin (%) ******* * 0.1722
Mcu_Vin_VS_Vin (%) ******* *
Mcu_Vin_VS_Vin (%) ******* *
Mcu_Vin_VS_Vin (%) ******* *
Mcu_Vin_VS_Vin (%) ******* *
Mcu_Vin_VS_Vin (%) ******* *
Mcu_Vin_VS_Vin (%) ******* *
Mcu_Vin_VS_Vin (%) ******* *
Mcu_Iin_VS_Iin (%) ******* * 0.1063
Mcu_Iin_VS_Iin (%) ******* *
Mcu_Iin_VS_Iin (%) ******* *
Mcu_Iin_VS_Iin (%) ******* *
Mcu_Iin_VS_Iin (%) ******* *
Mcu_Iin_VS_Iin (%) ******* *
Mcu_Iin_VS_Iin (%) ******* *
Mcu_Iin_VS_Iin (%) ******* *
Mcu_Pin_VS_Pin (%) ******* * 0.2464
Mcu_Pin_VS_Pin (%) ******* *
Mcu_Pin_VS_Pin (%) ******* *
Mcu_Pin_VS_Pin (%) ******* *
Mcu_Pin_VS_Pin (%) ******* *
Mcu_Pin_VS_Pin (%) ******* *
Mcu_Pin_VS_Pin (%) ******* *
Mcu_Pin_VS_Pin (%) ******* *
Mcu_Vout_VS_Vout (%) ******* * 0.3008
Mcu_Vout_VS_Vout (%) ******* *
Mcu_Vout_VS_Vout (%) ******* *
Mcu_Vout_VS_Vout (%) ******* *
Mcu_Vout_VS_Vout (%) ******* *
Mcu_Vout_VS_Vout (%) ******* *
Mcu_Vout_VS_Vout (%) ******* *
Mcu_Vout_VS_Vout (%) ******* *
Mcu_Iout_VS_Iout (%) ******* * 0.1529
Mcu_Iout_VS_Iout (%) ******* *
Mcu_Iout_VS_Iout (%) ******* *
Mcu_Iout_VS_Iout (%) ******* *
Mcu_Iout_VS_Iout (%) ******* *
Mcu_Iout_VS_Iout (%) ******* *
Mcu_Iout_VS_Iout (%) ******* *
Mcu_Iout_VS_Iout (%) ******* *
Mcu_Pout_VS_Pout (%) ******* * 0.1759
Mcu_Pout_VS_Pout (%) ******* *
Mcu_Pout_VS_Pout (%) ******* *
Mcu_Pout_VS_Pout (%) ******* *
Mcu_Pout_VS_Pout (%) ******* *
Mcu_Pout_VS_Pout (%) ******* *
Mcu_Pout_VS_Pout (%) ******* *
Mcu_Pout_VS_Pout (%) ******* *
Max Min Reading
-------------- --------- --------- ---------
Temperature 1 200.00 0.00 56.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Max Min Reading
-------------- --------- --------- ---------
Temperature 2 200.00 0.00 73.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Max Min Reading
-------- --------- --------- ---------
Fan RPM 28000 ****** 11115
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
STEP.776(UUT Test seq.776) : Input Output Accuracy Multi or Single_S3(240Vd PASS
ElapsedTime (S)= 6'567
Vin (V)= 240.00
Fin (Hz)= 30.00
Delay Time (ms)= 5000.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 80.750 ******* ******* 80.748
12Vsb 1.250 ******* ******* 1.250
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
------------Load--------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V ******* ******* 0.000
12Vsb ******* ******* 0.000
PWOK ******* ******* 0.000
Vin_Good ******* ******* 0.000
SMBAlert ******* ******* 0.000
-------34970----------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 12.350 11.590 12.213
12VSb 12.600 11.400 12.040
PWOK 3.460 2.500 3.238
Vin_Good 3.460 2.500 3.235
SMBAlert 3.460 2.500 3.220
IBUS 4.200 3.800 4.000
CR 0.400 ******* -0.010
Max Min Reading
------------- ---------- ---------- ----------
Vrms (V) ******** ******** 239.9818
PF 1.0000 ******** 1.0000
THDi (%) ******** * 1068.5067
Irms (A) ******** ******** 4.5217
Pin (W) ******** ******** 1085.1234
Pout (W) ******** ******** 1001.2533
Eff (%) 99.0000 92.0000 92.2709
Load Noise Range Noise B.W
Name (V) (MHz)
------------- ----------- ---------
12V 2 20.000
12Vsb 2 20.000
PWOK 2 20.000
Vin_Good 2 20.000
SMBAlert 2 20.000
Load Vpp Noise Vpp Noise Vpp Noise
Name Max(mV) Min(mV) (mV)
------------- ------------ ------------ ------------
12V 120.000 0.000 9.200
12Vsb 120.000 0.000 10.630
PWOK ********* ********* 21.320
Vin_Good ********* ********* 21.500
SMBAlert ********* ********* 22.970
MCU Accuracy ---------------------------------------------
Spec Status Reading Status
----------- ------------- ----------------
Mcu Status 0 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Reading
-------- ---------
Vin_M 240.5000
Iin_M 4.5234
Pin_M 1086.0000
Vout_M 12.2266
Iout_M 80.6250
Pout_M 987.0000
Max Min Reading
--------------------- --------- --------- ---------
Mcu_Vin_VS_Vin (%) ******* * 0.2159
Mcu_Vin_VS_Vin (%) ******* *
Mcu_Vin_VS_Vin (%) ******* *
Mcu_Vin_VS_Vin (%) ******* *
Mcu_Vin_VS_Vin (%) ******* *
Mcu_Vin_VS_Vin (%) ******* *
Mcu_Vin_VS_Vin (%) ******* *
Mcu_Vin_VS_Vin (%) ******* *
Mcu_Iin_VS_Iin (%) ******* * 0.0374
Mcu_Iin_VS_Iin (%) ******* *
Mcu_Iin_VS_Iin (%) ******* *
Mcu_Iin_VS_Iin (%) ******* *
Mcu_Iin_VS_Iin (%) ******* *
Mcu_Iin_VS_Iin (%) ******* *
Mcu_Iin_VS_Iin (%) ******* *
Mcu_Iin_VS_Iin (%) ******* *
Mcu_Pin_VS_Pin (%) ******* * 0.0808
Mcu_Pin_VS_Pin (%) ******* *
Mcu_Pin_VS_Pin (%) ******* *
Mcu_Pin_VS_Pin (%) ******* *
Mcu_Pin_VS_Pin (%) ******* *
Mcu_Pin_VS_Pin (%) ******* *
Mcu_Pin_VS_Pin (%) ******* *
Mcu_Pin_VS_Pin (%) ******* *
Mcu_Vout_VS_Vout (%) ******* * 0.1075
Mcu_Vout_VS_Vout (%) ******* *
Mcu_Vout_VS_Vout (%) ******* *
Mcu_Vout_VS_Vout (%) ******* *
Mcu_Vout_VS_Vout (%) ******* *
Mcu_Vout_VS_Vout (%) ******* *
Mcu_Vout_VS_Vout (%) ******* *
Mcu_Vout_VS_Vout (%) ******* *
Mcu_Iout_VS_Iout (%) ******* * 0.1518
Mcu_Iout_VS_Iout (%) ******* *
Mcu_Iout_VS_Iout (%) ******* *
Mcu_Iout_VS_Iout (%) ******* *
Mcu_Iout_VS_Iout (%) ******* *
Mcu_Iout_VS_Iout (%) ******* *
Mcu_Iout_VS_Iout (%) ******* *
Mcu_Iout_VS_Iout (%) ******* *
Mcu_Pout_VS_Pout (%) ******* * 0.0806
Mcu_Pout_VS_Pout (%) ******* *
Mcu_Pout_VS_Pout (%) ******* *
Mcu_Pout_VS_Pout (%) ******* *
Mcu_Pout_VS_Pout (%) ******* *
Mcu_Pout_VS_Pout (%) ******* *
Mcu_Pout_VS_Pout (%) ******* *
Mcu_Pout_VS_Pout (%) ******* *
Max Min Reading
-------------- --------- --------- ---------
Temperature 1 200.00 0.00 55.50
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Max Min Reading
-------------- --------- --------- ---------
Temperature 2 200.00 0.00 74.50
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Max Min Reading
-------- --------- --------- ---------
Fan RPM 28000 ****** 11114
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
STEP.777(UUT Test seq.777) : Input Output Accuracy Multi or Single_S3(240Vd FAIL
ElapsedTime (S)= 6'380
Vin (V)= 240.00
Fin (Hz)= 30.00
Delay Time (ms)= 5000.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 32.300 ******* ******* 32.298
12Vsb 0.500 ******* ******* 0.500
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
------------Load--------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V ******* ******* 0.000
12Vsb ******* ******* 0.000
PWOK ******* ******* 0.000
Vin_Good ******* ******* 0.000
SMBAlert ******* ******* 0.000
-------34970----------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 12.350 11.590 12.243
12VSb 12.600 11.400 12.079
PWOK 3.460 2.500 3.245
Vin_Good 3.460 2.500 3.240
SMBAlert 3.460 2.500 3.221
IBUS 1.800 1.400 1.606
CR 0.400 ******* -0.002
Max Min Reading
------------- ---------- ---------- ----------
Vrms (V) ******** ******** 240.1945
PF 1.0000 ******** 1.0000
THDi (%) ******** * 776.9016
Irms (A) ******** ******** 1.8384
Pin (W) ******** ******** 441.5715
Pout (W) ******** ******** 401.4616
Eff (%) 99.0000 91.0000 90.9165
Load Noise Range Noise B.W
Name (V) (MHz)
------------- ----------- ---------
12V 2 20.000
12Vsb 2 20.000
PWOK 2 20.000
Vin_Good 2 20.000
SMBAlert 2 20.000
Load Vpp Noise Vpp Noise Vpp Noise
Name Max(mV) Min(mV) (mV)
------------- ------------ ------------ ------------
12V 120.000 0.000 8.700
12Vsb 120.000 0.000 5.850
PWOK ********* ********* 20.570
Vin_Good ********* ********* 20.630
SMBAlert ********* ********* 22.600
MCU Accuracy ---------------------------------------------
Spec Status Reading Status
----------- ------------- ----------------
Mcu Status 0 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Reading
-------- ---------
Vin_M 240.5000
Iin_M 1.8262
Pin_M 439.5000
Vout_M 12.2422
Iout_M 32.3125
Pout_M 396.0000
Max Min Reading
--------------------- --------- --------- ---------
Mcu_Vin_VS_Vin (%) ******* * 0.1272
Mcu_Vin_VS_Vin (%) ******* *
Mcu_Vin_VS_Vin (%) ******* *
Mcu_Vin_VS_Vin (%) ******* *
Mcu_Vin_VS_Vin (%) ******* *
Mcu_Vin_VS_Vin (%) ******* *
Mcu_Vin_VS_Vin (%) ******* *
Mcu_Vin_VS_Vin (%) ******* *
Mcu_Iin_VS_Iin (%) ******* * 0.6664
Mcu_Iin_VS_Iin (%) ******* *
Mcu_Iin_VS_Iin (%) ******* *
Mcu_Iin_VS_Iin (%) ******* *
Mcu_Iin_VS_Iin (%) ******* *
Mcu_Iin_VS_Iin (%) ******* *
Mcu_Iin_VS_Iin (%) ******* *
Mcu_Iin_VS_Iin (%) ******* *
Mcu_Pin_VS_Pin (%) ******* * 0.4691
Mcu_Pin_VS_Pin (%) ******* *
Mcu_Pin_VS_Pin (%) ******* *
Mcu_Pin_VS_Pin (%) ******* *
Mcu_Pin_VS_Pin (%) ******* *
Mcu_Pin_VS_Pin (%) ******* *
Mcu_Pin_VS_Pin (%) ******* *
Mcu_Pin_VS_Pin (%) ******* *
Mcu_Vout_VS_Vout (%) ******* * 0.0069
Mcu_Vout_VS_Vout (%) ******* *
Mcu_Vout_VS_Vout (%) ******* *
Mcu_Vout_VS_Vout (%) ******* *
Mcu_Vout_VS_Vout (%) ******* *
Mcu_Vout_VS_Vout (%) ******* *
Mcu_Vout_VS_Vout (%) ******* *
Mcu_Vout_VS_Vout (%) ******* *
Mcu_Iout_VS_Iout (%) ******* * 0.0458
Mcu_Iout_VS_Iout (%) ******* *
Mcu_Iout_VS_Iout (%) ******* *
Mcu_Iout_VS_Iout (%) ******* *
Mcu_Iout_VS_Iout (%) ******* *
Mcu_Iout_VS_Iout (%) ******* *
Mcu_Iout_VS_Iout (%) ******* *
Mcu_Iout_VS_Iout (%) ******* *
Mcu_Pout_VS_Pout (%) ******* * 0.1462
Mcu_Pout_VS_Pout (%) ******* *
Mcu_Pout_VS_Pout (%) ******* *
Mcu_Pout_VS_Pout (%) ******* *
Mcu_Pout_VS_Pout (%) ******* *
Mcu_Pout_VS_Pout (%) ******* *
Mcu_Pout_VS_Pout (%) ******* *
Mcu_Pout_VS_Pout (%) ******* *
Max Min Reading
-------------- --------- --------- ---------
Temperature 1 200.00 0.00 56.50
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Max Min Reading
-------------- --------- --------- ---------
Temperature 2 200.00 0.00 73.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Max Min Reading
-------- --------- --------- ---------
Fan RPM 28000 ****** 10962
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
STEP.778(UUT Test seq.778) : Input Output Accuracy Multi or Single_S3(240Vd PASS
ElapsedTime (S)= 6'427
Vin (V)= 240.00
Fin (Hz)= 30.00
Delay Time (ms)= 5000.00
Load Loading Iout Iout Iout
Name (A/Ohm/V) Max Min (A)
------------- ---------- ------- ------- -------
12V 16.150 ******* ******* 16.148
12Vsb 0.250 ******* ******* 0.250
PWOK 0.000 ******* ******* 0.000
Vin_Good 0.000 ******* ******* 0.000
SMBAlert 0.000 ******* ******* 0.000
------------Load--------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V ******* ******* 0.000
12Vsb ******* ******* 0.000
PWOK ******* ******* 0.000
Vin_Good ******* ******* 0.000
SMBAlert ******* ******* 0.000
-------34970----------------------------
Load Vout Vout Vout
Name Max Min (V)
------------ ------- ------- -------
12V 12.350 11.590 12.251
12VSb 12.600 11.400 12.105
PWOK 3.460 2.500 3.243
Vin_Good 3.460 2.500 3.246
SMBAlert 3.460 2.500 3.217
IBUS 1.000 0.600 0.809
CR 0.400 ******* 0.000
Max Min Reading
------------- ---------- ---------- ----------
Vrms (V) ******** ******** 240.2638
PF 1.0000 ******** 1.0000
THDi (%) ******** * 2013.4318
Irms (A) ******** ******** 0.9429
Pin (W) ******** ******** 226.5428
Pout (W) ******** ******** 200.8562
Eff (%) 99.0000 88.0000 88.6615
Load Noise Range Noise B.W
Name (V) (MHz)
------------- ----------- ---------
12V 2 20.000
12Vsb 2 20.000
PWOK 2 20.000
Vin_Good 2 20.000
SMBAlert 2 20.000
Load Vpp Noise Vpp Noise Vpp Noise
Name Max(mV) Min(mV) (mV)
------------- ------------ ------------ ------------
12V 120.000 0.000 30.750
12Vsb 120.000 0.000 4.350
PWOK ********* ********* 19.760
Vin_Good ********* ********* 18.200
SMBAlert ********* ********* 21.720
MCU Accuracy ---------------------------------------------
Spec Status Reading Status
----------- ------------- ----------------
Mcu Status 0 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Mcu Status 0
Reading
-------- ---------
Vin_M 240.7500
Iin_M 0.9355
Pin_M 224.7500
Vout_M 12.2480
Iout_M 16.2500
Pout_M 199.2500
Max Min Reading
--------------------- --------- --------- ---------
Mcu_Vin_VS_Vin (%) ******* * 0.2024
Mcu_Vin_VS_Vin (%) ******* *
Mcu_Vin_VS_Vin (%) ******* *
Mcu_Vin_VS_Vin (%) ******* *
Mcu_Vin_VS_Vin (%) ******* *
Mcu_Vin_VS_Vin (%) ******* *
Mcu_Vin_VS_Vin (%) ******* *
Mcu_Vin_VS_Vin (%) ******* *
Mcu_Iin_VS_Iin (%) ******* * 0.7808
Mcu_Iin_VS_Iin (%) ******* *
Mcu_Iin_VS_Iin (%) ******* *
Mcu_Iin_VS_Iin (%) ******* *
Mcu_Iin_VS_Iin (%) ******* *
Mcu_Iin_VS_Iin (%) ******* *
Mcu_Iin_VS_Iin (%) ******* *
Mcu_Iin_VS_Iin (%) ******* *
Mcu_Pin_VS_Pin (%) ******* * 0.7914
Mcu_Pin_VS_Pin (%) ******* *
Mcu_Pin_VS_Pin (%) ******* *
Mcu_Pin_VS_Pin (%) ******* *
Mcu_Pin_VS_Pin (%) ******* *
Mcu_Pin_VS_Pin (%) ******* *
Mcu_Pin_VS_Pin (%) ******* *
Mcu_Pin_VS_Pin (%) ******* *
Mcu_Vout_VS_Vout (%) ******* * 0.0255
Mcu_Vout_VS_Vout (%) ******* *
Mcu_Vout_VS_Vout (%) ******* *
Mcu_Vout_VS_Vout (%) ******* *
Mcu_Vout_VS_Vout (%) ******* *
Mcu_Vout_VS_Vout (%) ******* *
Mcu_Vout_VS_Vout (%) ******* *
Mcu_Vout_VS_Vout (%) ******* *
Mcu_Iout_VS_Iout (%) ******* * 0.6329
Mcu_Iout_VS_Iout (%) ******* *
Mcu_Iout_VS_Iout (%) ******* *
Mcu_Iout_VS_Iout (%) ******* *
Mcu_Iout_VS_Iout (%) ******* *
Mcu_Iout_VS_Iout (%) ******* *
Mcu_Iout_VS_Iout (%) ******* *
Mcu_Iout_VS_Iout (%) ******* *
Mcu_Pout_VS_Pout (%) ******* * 0.7180
Mcu_Pout_VS_Pout (%) ******* *
Mcu_Pout_VS_Pout (%) ******* *
Mcu_Pout_VS_Pout (%) ******* *
Mcu_Pout_VS_Pout (%) ******* *
Mcu_Pout_VS_Pout (%) ******* *
Mcu_Pout_VS_Pout (%) ******* *
Mcu_Pout_VS_Pout (%) ******* *
Max Min Reading
-------------- --------- --------- ---------
Temperature 1 200.00 0.00 57.50
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Temperature 1 200.00 0.00
Max Min Reading
-------------- --------- --------- ---------
Temperature 2 200.00 0.00 70.50
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Temperature 2 200.00 0.00
Max Min Reading
-------- --------- --------- ---------
Fan RPM 28000 ****** 10842
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
Fan RPM 28000 ******
STEP.779(UUT Test seq.779) : AC Source ON/OFF(input source)_Multi_S2 ---- ( PASS
(The Report Format of this Sequence was not found)
STEP.780(UUT Test seq.780) : Set Input Condition_Load_S4 ---- (0'015) ----- PASS
Vin (V)= 200.000
Fin (Hz)= 30.000
Load Loading
Name (A/Ohm/V)
------------- ----------
12V 101.5700
12Vsb 1.7500
PWOK 0.0000
Vin_Good 0.0000
SMBAlert 0.0000
STEP.781(UUT Test seq.781) : Set Drop Time ---- (0'000) ------------------- PASS
Drop Time= 10
STEP.782(UUT Test seq.782) : AC_DC Line Sag Surge 80611N-2_Multi_S2(DropOut PASS
ElapsedTime (S)= 3'932
Vin (V)= 200.00
Fin (Hz)= 30.00
Delay Time (ms)= 3000.00
Drop Time (ms)= 10.00
Drop Recovery Time(ms)= 500.00
Drop Voltage (v)= 0.00
Drop Frequency (Hz)= 30.00
Repeat Count = 1
Degree = 0
Duty cycle (%)= 100.000000
Load Loading Vpk Max Vpk Min Vpk High Vpk Low
Name (A/Ohm/V) (V) (V) (V) (V)
------------- ----------- --------- --------- --------- ---------
12V 101.570 12.810 11.590 12.221 12.200
12Vsb 1.750 12.600 11.400 12.051 12.040
PWOK 0.000 3.460 2.500 3.263 3.270
Vin_Good 0.000 3.460 ********* 3.257 0.057
SMBAlert 0.000 3.460 ********* 3.260 3.258
STEP.783(UUT Test seq.783) : I2C Read Status Multi_S6(DropOut H_200Vdc - 10 PASS
Adderss :B0
Command Page00 :060200
Command Page01 :060201
Status Word :79
Status Byte :78
Status VOUT :7A
Status IOUT :7B
Status INPUT :7C
Status TEMPERATURE :7D
Status CML :7E
Status FANS :81
---------------------------------
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
----------------------------------
Word_Page_00 : 0
Word_Page_01 : 0
Status_Byte_P00 : 0
Status_Byte_P01 : 0
Status_VOUT_P00 : 0
Status_VOUT_P01 : 0
Status_IOUT_P00 : 0
Status_IOUT_P01 : 0
Status_INPUT_P00 : 0
Status_INPUT_P01 : 0
Status_TEM_P00 : 0
Status_TEM_P01 : 0
Status_CML_P00 : 0
Status_CML_P01 : 0
Status_FANS_P00 : 0
Status_FANS_P01 : 0
STEP.784(UUT Test seq.784) : AC_DC Line Sag Surge 80611N-2_Multi_S2(DropOut PASS
ElapsedTime (S)= 3'869
Vin (V)= 200.00
Fin (Hz)= 30.00
Delay Time (ms)= 3000.00
Drop Time (ms)= 10.00
Drop Recovery Time(ms)= 500.00
Drop Voltage (v)= 0.00
Drop Frequency (Hz)= 30.00
Repeat Count = 1
Degree = 0
Duty cycle (%)= 100.000000
Load Loading Vpk Max Vpk Min Vpk High Vpk Low
Name (A/Ohm/V) (V) (V) (V) (V)
------------- ----------- --------- --------- --------- ---------
12V 101.570 12.810 11.590 12.221 12.203
12Vsb 1.750 12.600 11.400 12.049 12.044
PWOK 0.000 3.460 2.500 3.263 3.269
Vin_Good 0.000 3.460 ********* 3.257 0.057
SMBAlert 0.000 3.460 ********* 3.260 3.259
STEP.785(UUT Test seq.785) : I2C Read Status Multi_S6(DropOut H_200Vdc - 10 PASS
Adderss :B0
Command Page00 :060200
Command Page01 :060201
Status Word :79
Status Byte :78
Status VOUT :7A
Status IOUT :7B
Status INPUT :7C
Status TEMPERATURE :7D
Status CML :7E
Status FANS :81
---------------------------------
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
----------------------------------
Word_Page_00 : 0
Word_Page_01 : 0
Status_Byte_P00 : 0
Status_Byte_P01 : 0
Status_VOUT_P00 : 0
Status_VOUT_P01 : 0
Status_IOUT_P00 : 0
Status_IOUT_P01 : 0
Status_INPUT_P00 : 0
Status_INPUT_P01 : 0
Status_TEM_P00 : 0
Status_TEM_P01 : 0
Status_CML_P00 : 0
Status_CML_P01 : 0
Status_FANS_P00 : 0
Status_FANS_P01 : 0
STEP.786(UUT Test seq.786) : AC_DC Line Sag Surge 80611N-2_Multi_S2(DropOut PASS
ElapsedTime (S)= 3'869
Vin (V)= 200.00
Fin (Hz)= 30.00
Delay Time (ms)= 3000.00
Drop Time (ms)= 10.00
Drop Recovery Time(ms)= 500.00
Drop Voltage (v)= 0.00
Drop Frequency (Hz)= 30.00
Repeat Count = 1
Degree = 0
Duty cycle (%)= 100.000000
Load Loading Vpk Max Vpk Min Vpk High Vpk Low
Name (A/Ohm/V) (V) (V) (V) (V)
------------- ----------- --------- --------- --------- ---------
12V 101.570 12.810 11.590 12.221 12.204
12Vsb 1.750 12.600 11.400 12.049 12.042
PWOK 0.000 3.460 2.500 3.263 3.270
Vin_Good 0.000 3.460 ********* 3.256 0.057
SMBAlert 0.000 3.460 ********* 3.260 3.259
STEP.787(UUT Test seq.787) : I2C Read Status Multi_S6(DropOut H_200Vdc - 10 PASS
Adderss :B0
Command Page00 :060200
Command Page01 :060201
Status Word :79
Status Byte :78
Status VOUT :7A
Status IOUT :7B
Status INPUT :7C
Status TEMPERATURE :7D
Status CML :7E
Status FANS :81
---------------------------------
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
----------------------------------
Word_Page_00 : 0
Word_Page_01 : 0
Status_Byte_P00 : 0
Status_Byte_P01 : 0
Status_VOUT_P00 : 0
Status_VOUT_P01 : 0
Status_IOUT_P00 : 0
Status_IOUT_P01 : 0
Status_INPUT_P00 : 0
Status_INPUT_P01 : 0
Status_TEM_P00 : 0
Status_TEM_P01 : 0
Status_CML_P00 : 0
Status_CML_P01 : 0
Status_FANS_P00 : 0
Status_FANS_P01 : 0
STEP.788(UUT Test seq.788) : AC_DC Line Sag Surge 80611N-2_Multi_S2(DropOut PASS
ElapsedTime (S)= 3'900
Vin (V)= 200.00
Fin (Hz)= 30.00
Delay Time (ms)= 3000.00
Drop Time (ms)= 10.00
Drop Recovery Time(ms)= 500.00
Drop Voltage (v)= 0.00
Drop Frequency (Hz)= 30.00
Repeat Count = 1
Degree = 0
Duty cycle (%)= 100.000000
Load Loading Vpk Max Vpk Min Vpk High Vpk Low
Name (A/Ohm/V) (V) (V) (V) (V)
------------- ----------- --------- --------- --------- ---------
12V 101.570 12.810 11.590 12.221 12.203
12Vsb 1.750 12.600 11.400 12.049 12.043
PWOK 0.000 3.460 2.500 3.263 3.270
Vin_Good 0.000 3.460 ********* 3.257 0.057
SMBAlert 0.000 3.460 ********* 3.260 3.260
STEP.789(UUT Test seq.789) : I2C Read Status Multi_S6(DropOut H_200Vdc - 10 PASS
Adderss :B0
Command Page00 :060200
Command Page01 :060201
Status Word :79
Status Byte :78
Status VOUT :7A
Status IOUT :7B
Status INPUT :7C
Status TEMPERATURE :7D
Status CML :7E
Status FANS :81
---------------------------------
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
----------------------------------
Word_Page_00 : 0
Word_Page_01 : 0
Status_Byte_P00 : 0
Status_Byte_P01 : 0
Status_VOUT_P00 : 0
Status_VOUT_P01 : 0
Status_IOUT_P00 : 0
Status_IOUT_P01 : 0
Status_INPUT_P00 : 0
Status_INPUT_P01 : 0
Status_TEM_P00 : 0
Status_TEM_P01 : 0
Status_CML_P00 : 0
Status_CML_P01 : 0
Status_FANS_P00 : 0
Status_FANS_P01 : 0
STEP.790(UUT Test seq.790) : AC_DC Line Sag Surge 80611N-2_Multi_S2(DropOut PASS
ElapsedTime (S)= 3'853
Vin (V)= 200.00
Fin (Hz)= 30.00
Delay Time (ms)= 3000.00
Drop Time (ms)= 10.00
Drop Recovery Time(ms)= 500.00
Drop Voltage (v)= 0.00
Drop Frequency (Hz)= 30.00
Repeat Count = 1
Degree = 0
Duty cycle (%)= 100.000000
Load Loading Vpk Max Vpk Min Vpk High Vpk Low
Name (A/Ohm/V) (V) (V) (V) (V)
------------- ----------- --------- --------- --------- ---------
12V 101.570 12.810 11.590 12.221 12.202
12Vsb 1.750 12.600 11.400 12.050 12.044
PWOK 0.000 3.460 2.500 3.263 3.270
Vin_Good 0.000 3.460 ********* 3.256 0.055
SMBAlert 0.000 3.460 ********* 3.260 3.260
STEP.791(UUT Test seq.791) : I2C Read Status Multi_S6(DropOut H_200Vdc - 10 PASS
Adderss :B0
Command Page00 :060200
Command Page01 :060201
Status Word :79
Status Byte :78
Status VOUT :7A
Status IOUT :7B
Status INPUT :7C
Status TEMPERATURE :7D
Status CML :7E
Status FANS :81
---------------------------------
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
----------------------------------
Word_Page_00 : 0
Word_Page_01 : 0
Status_Byte_P00 : 0
Status_Byte_P01 : 0
Status_VOUT_P00 : 0
Status_VOUT_P01 : 0
Status_IOUT_P00 : 0
Status_IOUT_P01 : 0
Status_INPUT_P00 : 0
Status_INPUT_P01 : 0
Status_TEM_P00 : 0
Status_TEM_P01 : 0
Status_CML_P00 : 0
Status_CML_P01 : 0
Status_FANS_P00 : 0
Status_FANS_P01 : 0
STEP.792(UUT Test seq.792) : AC_DC Line Sag Surge 80611N-2_Multi_S2(DropOut PASS
ElapsedTime (S)= 3'884
Vin (V)= 200.00
Fin (Hz)= 30.00
Delay Time (ms)= 3000.00
Drop Time (ms)= 10.00
Drop Recovery Time(ms)= 500.00
Drop Voltage (v)= 0.00
Drop Frequency (Hz)= 30.00
Repeat Count = 1
Degree = 0
Duty cycle (%)= 100.000000
Load Loading Vpk Max Vpk Min Vpk High Vpk Low
Name (A/Ohm/V) (V) (V) (V) (V)
------------- ----------- --------- --------- --------- ---------
12V 101.570 12.810 11.590 12.221 12.203
12Vsb 1.750 12.600 11.400 12.050 12.043
PWOK 0.000 3.460 2.500 3.263 3.269
Vin_Good 0.000 3.460 ********* 3.256 0.056
SMBAlert 0.000 3.460 ********* 3.262 3.258
STEP.793(UUT Test seq.793) : I2C Read Status Multi_S6(DropOut H_200Vdc - 10 PASS
Adderss :B0
Command Page00 :060200
Command Page01 :060201
Status Word :79
Status Byte :78
Status VOUT :7A
Status IOUT :7B
Status INPUT :7C
Status TEMPERATURE :7D
Status CML :7E
Status FANS :81
---------------------------------
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
----------------------------------
Word_Page_00 : 0
Word_Page_01 : 0
Status_Byte_P00 : 0
Status_Byte_P01 : 0
Status_VOUT_P00 : 0
Status_VOUT_P01 : 0
Status_IOUT_P00 : 0
Status_IOUT_P01 : 0
Status_INPUT_P00 : 0
Status_INPUT_P01 : 0
Status_TEM_P00 : 0
Status_TEM_P01 : 0
Status_CML_P00 : 0
Status_CML_P01 : 0
Status_FANS_P00 : 0
Status_FANS_P01 : 0
STEP.794(UUT Test seq.794) : AC_DC Line Sag Surge 80611N-2_Multi_S2(DropOut PASS
ElapsedTime (S)= 3'885
Vin (V)= 200.00
Fin (Hz)= 30.00
Delay Time (ms)= 3000.00
Drop Time (ms)= 10.00
Drop Recovery Time(ms)= 500.00
Drop Voltage (v)= 0.00
Drop Frequency (Hz)= 30.00
Repeat Count = 1
Degree = 0
Duty cycle (%)= 100.000000
Load Loading Vpk Max Vpk Min Vpk High Vpk Low
Name (A/Ohm/V) (V) (V) (V) (V)
------------- ----------- --------- --------- --------- ---------
12V 101.570 12.810 11.590 12.221 12.202
12Vsb 1.750 12.600 11.400 12.050 12.044
PWOK 0.000 3.460 2.500 3.263 3.270
Vin_Good 0.000 3.460 ********* 3.257 0.058
SMBAlert 0.000 3.460 ********* 3.260 3.260
STEP.795(UUT Test seq.795) : I2C Read Status Multi_S6(DropOut H_200Vdc - 10 PASS
Adderss :B0
Command Page00 :060200
Command Page01 :060201
Status Word :79
Status Byte :78
Status VOUT :7A
Status IOUT :7B
Status INPUT :7C
Status TEMPERATURE :7D
Status CML :7E
Status FANS :81
---------------------------------
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
----------------------------------
Word_Page_00 : 0
Word_Page_01 : 0
Status_Byte_P00 : 0
Status_Byte_P01 : 0
Status_VOUT_P00 : 0
Status_VOUT_P01 : 0
Status_IOUT_P00 : 0
Status_IOUT_P01 : 0
Status_INPUT_P00 : 0
Status_INPUT_P01 : 0
Status_TEM_P00 : 0
Status_TEM_P01 : 0
Status_CML_P00 : 0
Status_CML_P01 : 0
Status_FANS_P00 : 0
Status_FANS_P01 : 0
STEP.796(UUT Test seq.796) : AC_DC Line Sag Surge 80611N-2_Multi_S2(DropOut PASS
ElapsedTime (S)= 3'884
Vin (V)= 200.00
Fin (Hz)= 30.00
Delay Time (ms)= 3000.00
Drop Time (ms)= 10.00
Drop Recovery Time(ms)= 500.00
Drop Voltage (v)= 0.00
Drop Frequency (Hz)= 30.00
Repeat Count = 1
Degree = 0
Duty cycle (%)= 100.000000
Load Loading Vpk Max Vpk Min Vpk High Vpk Low
Name (A/Ohm/V) (V) (V) (V) (V)
------------- ----------- --------- --------- --------- ---------
12V 101.570 12.810 11.590 12.221 12.202
12Vsb 1.750 12.600 11.400 12.051 12.044
PWOK 0.000 3.460 2.500 3.263 3.270
Vin_Good 0.000 3.460 ********* 3.257 0.058
SMBAlert 0.000 3.460 ********* 3.260 3.259
STEP.797(UUT Test seq.797) : I2C Read Status Multi_S6(DropOut H_200Vdc - 10 PASS
Adderss :B0
Command Page00 :060200
Command Page01 :060201
Status Word :79
Status Byte :78
Status VOUT :7A
Status IOUT :7B
Status INPUT :7C
Status TEMPERATURE :7D
Status CML :7E
Status FANS :81
---------------------------------
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
----------------------------------
Word_Page_00 : 0
Word_Page_01 : 0
Status_Byte_P00 : 0
Status_Byte_P01 : 0
Status_VOUT_P00 : 0
Status_VOUT_P01 : 0
Status_IOUT_P00 : 0
Status_IOUT_P01 : 0
Status_INPUT_P00 : 0
Status_INPUT_P01 : 0
Status_TEM_P00 : 0
Status_TEM_P01 : 0
Status_CML_P00 : 0
Status_CML_P01 : 0
Status_FANS_P00 : 0
Status_FANS_P01 : 0
STEP.798(UUT Test seq.798) : AC_DC Line Sag Surge 80611N-2_Multi_S2(DropOut PASS
ElapsedTime (S)= 3'869
Vin (V)= 200.00
Fin (Hz)= 30.00
Delay Time (ms)= 3000.00
Drop Time (ms)= 10.00
Drop Recovery Time(ms)= 500.00
Drop Voltage (v)= 0.00
Drop Frequency (Hz)= 30.00
Repeat Count = 1
Degree = 0
Duty cycle (%)= 100.000000
Load Loading Vpk Max Vpk Min Vpk High Vpk Low
Name (A/Ohm/V) (V) (V) (V) (V)
------------- ----------- --------- --------- --------- ---------
12V 101.570 12.810 11.590 12.223 12.201
12Vsb 1.750 12.600 11.400 12.050 12.044
PWOK 0.000 3.460 2.500 3.263 3.270
Vin_Good 0.000 3.460 ********* 3.257 0.057
SMBAlert 0.000 3.460 ********* 3.262 3.260
STEP.799(UUT Test seq.799) : I2C Read Status Multi_S6(DropOut H_200Vdc - 10 PASS
Adderss :B0
Command Page00 :060200
Command Page01 :060201
Status Word :79
Status Byte :78
Status VOUT :7A
Status IOUT :7B
Status INPUT :7C
Status TEMPERATURE :7D
Status CML :7E
Status FANS :81
---------------------------------
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
----------------------------------
Word_Page_00 : 0
Word_Page_01 : 0
Status_Byte_P00 : 0
Status_Byte_P01 : 0
Status_VOUT_P00 : 0
Status_VOUT_P01 : 0
Status_IOUT_P00 : 0
Status_IOUT_P01 : 0
Status_INPUT_P00 : 0
Status_INPUT_P01 : 0
Status_TEM_P00 : 0
Status_TEM_P01 : 0
Status_CML_P00 : 0
Status_CML_P01 : 0
Status_FANS_P00 : 0
Status_FANS_P01 : 0
STEP.800(UUT Test seq.800) : AC_DC Line Sag Surge 80611N-2_Multi_S2(DropOut PASS
ElapsedTime (S)= 3'853
Vin (V)= 200.00
Fin (Hz)= 30.00
Delay Time (ms)= 3000.00
Drop Time (ms)= 10.00
Drop Recovery Time(ms)= 500.00
Drop Voltage (v)= 0.00
Drop Frequency (Hz)= 30.00
Repeat Count = 1
Degree = 0
Duty cycle (%)= 100.000000
Load Loading Vpk Max Vpk Min Vpk High Vpk Low
Name (A/Ohm/V) (V) (V) (V) (V)
------------- ----------- --------- --------- --------- ---------
12V 101.570 12.810 11.590 12.221 12.203
12Vsb 1.750 12.600 11.400 12.050 12.044
PWOK 0.000 3.460 2.500 3.263 3.270
Vin_Good 0.000 3.460 ********* 3.257 0.057
SMBAlert 0.000 3.460 ********* 3.260 3.260
STEP.801(UUT Test seq.801) : I2C Read Status Multi_S6(DropOut H_200Vdc - 10 PASS
Adderss :B0
Command Page00 :060200
Command Page01 :060201
Status Word :79
Status Byte :78
Status VOUT :7A
Status IOUT :7B
Status INPUT :7C
Status TEMPERATURE :7D
Status CML :7E
Status FANS :81
---------------------------------
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
----------------------------------
Word_Page_00 : 0
Word_Page_01 : 0
Status_Byte_P00 : 0
Status_Byte_P01 : 0
Status_VOUT_P00 : 0
Status_VOUT_P01 : 0
Status_IOUT_P00 : 0
Status_IOUT_P01 : 0
Status_INPUT_P00 : 0
Status_INPUT_P01 : 0
Status_TEM_P00 : 0
Status_TEM_P01 : 0
Status_CML_P00 : 0
Status_CML_P01 : 0
Status_FANS_P00 : 0
Status_FANS_P01 : 0
STEP.802(UUT Test seq.802) : AC Source ON/OFF(input source)_Multi_S2 ---- ( PASS
(The Report Format of this Sequence was not found)
STEP.803(UUT Test seq.803) : Set Input Condition_Load_S4 ---- (0'016) ----- PASS
Vin (V)= 220.000
Fin (Hz)= 30.000
Load Loading
Name (A/Ohm/V)
------------- ----------
12V 113.0500
12Vsb 1.7500
PWOK 0.0000
Vin_Good 0.0000
SMBAlert 0.0000
STEP.804(UUT Test seq.804) : Set Drop Time ---- (0'000) ------------------- PASS
Drop Time= 10
STEP.805(UUT Test seq.805) : AC_DC Line Sag Surge 80611N-2_Multi_S2(DropOut PASS
ElapsedTime (S)= 3'900
Vin (V)= 220.00
Fin (Hz)= 30.00
Delay Time (ms)= 3000.00
Drop Time (ms)= 10.00
Drop Recovery Time(ms)= 500.00
Drop Voltage (v)= 0.00
Drop Frequency (Hz)= 30.00
Repeat Count = 1
Degree = 0
Duty cycle (%)= 100.000000
Load Loading Vpk Max Vpk Min Vpk High Vpk Low
Name (A/Ohm/V) (V) (V) (V) (V)
------------- ----------- --------- --------- --------- ---------
12V 113.050 12.810 11.590 12.215 12.196
12Vsb 1.750 12.600 11.400 12.049 12.040
PWOK 0.000 3.460 2.500 3.261 3.268
Vin_Good 0.000 3.460 ********* 3.254 0.055
SMBAlert 0.000 3.460 ********* 3.262 3.260
STEP.806(UUT Test seq.806) : I2C Read Status Multi_S6(DropOut H_220Vdc - 10 PASS
Adderss :B0
Command Page00 :060200
Command Page01 :060201
Status Word :79
Status Byte :78
Status VOUT :7A
Status IOUT :7B
Status INPUT :7C
Status TEMPERATURE :7D
Status CML :7E
Status FANS :81
---------------------------------
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
----------------------------------
Word_Page_00 : 0
Word_Page_01 : 0
Status_Byte_P00 : 0
Status_Byte_P01 : 0
Status_VOUT_P00 : 0
Status_VOUT_P01 : 0
Status_IOUT_P00 : 0
Status_IOUT_P01 : 0
Status_INPUT_P00 : 0
Status_INPUT_P01 : 0
Status_TEM_P00 : 0
Status_TEM_P01 : 0
Status_CML_P00 : 0
Status_CML_P01 : 0
Status_FANS_P00 : 0
Status_FANS_P01 : 0
STEP.807(UUT Test seq.807) : AC_DC Line Sag Surge 80611N-2_Multi_S2(DropOut PASS
ElapsedTime (S)= 3'900
Vin (V)= 220.00
Fin (Hz)= 30.00
Delay Time (ms)= 3000.00
Drop Time (ms)= 10.00
Drop Recovery Time(ms)= 500.00
Drop Voltage (v)= 0.00
Drop Frequency (Hz)= 30.00
Repeat Count = 1
Degree = 0
Duty cycle (%)= 100.000000
Load Loading Vpk Max Vpk Min Vpk High Vpk Low
Name (A/Ohm/V) (V) (V) (V) (V)
------------- ----------- --------- --------- --------- ---------
12V 113.050 12.810 11.590 12.215 12.196
12Vsb 1.750 12.600 11.400 12.049 12.040
PWOK 0.000 3.460 2.500 3.262 3.268
Vin_Good 0.000 3.460 ********* 3.254 0.055
SMBAlert 0.000 3.460 ********* 3.262 3.261
STEP.808(UUT Test seq.808) : I2C Read Status Multi_S6(DropOut H_220Vdc - 10 PASS
Adderss :B0
Command Page00 :060200
Command Page01 :060201
Status Word :79
Status Byte :78
Status VOUT :7A
Status IOUT :7B
Status INPUT :7C
Status TEMPERATURE :7D
Status CML :7E
Status FANS :81
---------------------------------
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
----------------------------------
Word_Page_00 : 0
Word_Page_01 : 0
Status_Byte_P00 : 0
Status_Byte_P01 : 0
Status_VOUT_P00 : 0
Status_VOUT_P01 : 0
Status_IOUT_P00 : 0
Status_IOUT_P01 : 0
Status_INPUT_P00 : 0
Status_INPUT_P01 : 0
Status_TEM_P00 : 0
Status_TEM_P01 : 0
Status_CML_P00 : 0
Status_CML_P01 : 0
Status_FANS_P00 : 0
Status_FANS_P01 : 0
STEP.809(UUT Test seq.809) : AC_DC Line Sag Surge 80611N-2_Multi_S2(DropOut PASS
ElapsedTime (S)= 3'900
Vin (V)= 220.00
Fin (Hz)= 30.00
Delay Time (ms)= 3000.00
Drop Time (ms)= 10.00
Drop Recovery Time(ms)= 500.00
Drop Voltage (v)= 0.00
Drop Frequency (Hz)= 30.00
Repeat Count = 1
Degree = 0
Duty cycle (%)= 100.000000
Load Loading Vpk Max Vpk Min Vpk High Vpk Low
Name (A/Ohm/V) (V) (V) (V) (V)
------------- ----------- --------- --------- --------- ---------
12V 113.050 12.810 11.590 12.215 12.194
12Vsb 1.750 12.600 11.400 12.049 12.042
PWOK 0.000 3.460 2.500 3.261 3.266
Vin_Good 0.000 3.460 ********* 3.254 0.053
SMBAlert 0.000 3.460 ********* 3.260 3.258
STEP.810(UUT Test seq.810) : I2C Read Status Multi_S6(DropOut H_220Vdc - 10 PASS
Adderss :B0
Command Page00 :060200
Command Page01 :060201
Status Word :79
Status Byte :78
Status VOUT :7A
Status IOUT :7B
Status INPUT :7C
Status TEMPERATURE :7D
Status CML :7E
Status FANS :81
---------------------------------
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
----------------------------------
Word_Page_00 : 0
Word_Page_01 : 0
Status_Byte_P00 : 0
Status_Byte_P01 : 0
Status_VOUT_P00 : 0
Status_VOUT_P01 : 0
Status_IOUT_P00 : 0
Status_IOUT_P01 : 0
Status_INPUT_P00 : 0
Status_INPUT_P01 : 0
Status_TEM_P00 : 0
Status_TEM_P01 : 0
Status_CML_P00 : 0
Status_CML_P01 : 0
Status_FANS_P00 : 0
Status_FANS_P01 : 0
STEP.811(UUT Test seq.811) : AC_DC Line Sag Surge 80611N-2_Multi_S2(DropOut PASS
ElapsedTime (S)= 3'915
Vin (V)= 220.00
Fin (Hz)= 30.00
Delay Time (ms)= 3000.00
Drop Time (ms)= 10.00
Drop Recovery Time(ms)= 500.00
Drop Voltage (v)= 0.00
Drop Frequency (Hz)= 30.00
Repeat Count = 1
Degree = 0
Duty cycle (%)= 100.000000
Load Loading Vpk Max Vpk Min Vpk High Vpk Low
Name (A/Ohm/V) (V) (V) (V) (V)
------------- ----------- --------- --------- --------- ---------
12V 113.050 12.810 11.590 12.215 12.196
12Vsb 1.750 12.600 11.400 12.049 12.042
PWOK 0.000 3.460 2.500 3.261 3.268
Vin_Good 0.000 3.460 ********* 3.255 0.056
SMBAlert 0.000 3.460 ********* 3.260 3.259
STEP.812(UUT Test seq.812) : I2C Read Status Multi_S6(DropOut H_220Vdc - 10 PASS
Adderss :B0
Command Page00 :060200
Command Page01 :060201
Status Word :79
Status Byte :78
Status VOUT :7A
Status IOUT :7B
Status INPUT :7C
Status TEMPERATURE :7D
Status CML :7E
Status FANS :81
---------------------------------
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
----------------------------------
Word_Page_00 : 0
Word_Page_01 : 0
Status_Byte_P00 : 0
Status_Byte_P01 : 0
Status_VOUT_P00 : 0
Status_VOUT_P01 : 0
Status_IOUT_P00 : 0
Status_IOUT_P01 : 0
Status_INPUT_P00 : 0
Status_INPUT_P01 : 0
Status_TEM_P00 : 0
Status_TEM_P01 : 0
Status_CML_P00 : 0
Status_CML_P01 : 0
Status_FANS_P00 : 0
Status_FANS_P01 : 0
STEP.813(UUT Test seq.813) : AC_DC Line Sag Surge 80611N-2_Multi_S2(DropOut PASS
ElapsedTime (S)= 3'884
Vin (V)= 220.00
Fin (Hz)= 30.00
Delay Time (ms)= 3000.00
Drop Time (ms)= 10.00
Drop Recovery Time(ms)= 500.00
Drop Voltage (v)= 0.00
Drop Frequency (Hz)= 30.00
Repeat Count = 1
Degree = 0
Duty cycle (%)= 100.000000
Load Loading Vpk Max Vpk Min Vpk High Vpk Low
Name (A/Ohm/V) (V) (V) (V) (V)
------------- ----------- --------- --------- --------- ---------
12V 113.050 12.810 11.590 12.215 12.194
12Vsb 1.750 12.600 11.400 12.049 12.040
PWOK 0.000 3.460 2.500 3.262 3.268
Vin_Good 0.000 3.460 ********* 3.255 0.056
SMBAlert 0.000 3.460 ********* 3.260 3.258
STEP.814(UUT Test seq.814) : I2C Read Status Multi_S6(DropOut H_220Vdc - 10 PASS
Adderss :B0
Command Page00 :060200
Command Page01 :060201
Status Word :79
Status Byte :78
Status VOUT :7A
Status IOUT :7B
Status INPUT :7C
Status TEMPERATURE :7D
Status CML :7E
Status FANS :81
---------------------------------
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
----------------------------------
Word_Page_00 : 0
Word_Page_01 : 0
Status_Byte_P00 : 0
Status_Byte_P01 : 0
Status_VOUT_P00 : 0
Status_VOUT_P01 : 0
Status_IOUT_P00 : 0
Status_IOUT_P01 : 0
Status_INPUT_P00 : 0
Status_INPUT_P01 : 0
Status_TEM_P00 : 0
Status_TEM_P01 : 0
Status_CML_P00 : 0
Status_CML_P01 : 0
Status_FANS_P00 : 0
Status_FANS_P01 : 0
STEP.815(UUT Test seq.815) : AC_DC Line Sag Surge 80611N-2_Multi_S2(DropOut PASS
ElapsedTime (S)= 3'884
Vin (V)= 220.00
Fin (Hz)= 30.00
Delay Time (ms)= 3000.00
Drop Time (ms)= 10.00
Drop Recovery Time(ms)= 500.00
Drop Voltage (v)= 0.00
Drop Frequency (Hz)= 30.00
Repeat Count = 1
Degree = 0
Duty cycle (%)= 100.000000
Load Loading Vpk Max Vpk Min Vpk High Vpk Low
Name (A/Ohm/V) (V) (V) (V) (V)
------------- ----------- --------- --------- --------- ---------
12V 113.050 12.810 11.590 12.215 12.196
12Vsb 1.750 12.600 11.400 12.049 12.042
PWOK 0.000 3.460 2.500 3.261 3.268
Vin_Good 0.000 3.460 ********* 3.255 0.055
SMBAlert 0.000 3.460 ********* 3.260 3.260
STEP.816(UUT Test seq.816) : I2C Read Status Multi_S6(DropOut H_220Vdc - 10 PASS
Adderss :B0
Command Page00 :060200
Command Page01 :060201
Status Word :79
Status Byte :78
Status VOUT :7A
Status IOUT :7B
Status INPUT :7C
Status TEMPERATURE :7D
Status CML :7E
Status FANS :81
---------------------------------
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
----------------------------------
Word_Page_00 : 0
Word_Page_01 : 0
Status_Byte_P00 : 0
Status_Byte_P01 : 0
Status_VOUT_P00 : 0
Status_VOUT_P01 : 0
Status_IOUT_P00 : 0
Status_IOUT_P01 : 0
Status_INPUT_P00 : 0
Status_INPUT_P01 : 0
Status_TEM_P00 : 0
Status_TEM_P01 : 0
Status_CML_P00 : 0
Status_CML_P01 : 0
Status_FANS_P00 : 0
Status_FANS_P01 : 0
STEP.817(UUT Test seq.817) : AC_DC Line Sag Surge 80611N-2_Multi_S2(DropOut PASS
ElapsedTime (S)= 3'869
Vin (V)= 220.00
Fin (Hz)= 30.00
Delay Time (ms)= 3000.00
Drop Time (ms)= 10.00
Drop Recovery Time(ms)= 500.00
Drop Voltage (v)= 0.00
Drop Frequency (Hz)= 30.00
Repeat Count = 1
Degree = 0
Duty cycle (%)= 100.000000
Load Loading Vpk Max Vpk Min Vpk High Vpk Low
Name (A/Ohm/V) (V) (V) (V) (V)
------------- ----------- --------- --------- --------- ---------
12V 113.050 12.810 11.590 12.215 12.194
12Vsb 1.750 12.600 11.400 12.049 12.042
PWOK 0.000 3.460 2.500 3.262 3.268
Vin_Good 0.000 3.460 ********* 3.254 0.056
SMBAlert 0.000 3.460 ********* 3.260 3.260
STEP.818(UUT Test seq.818) : I2C Read Status Multi_S6(DropOut H_220Vdc - 10 PASS
Adderss :B0
Command Page00 :060200
Command Page01 :060201
Status Word :79
Status Byte :78
Status VOUT :7A
Status IOUT :7B
Status INPUT :7C
Status TEMPERATURE :7D
Status CML :7E
Status FANS :81
---------------------------------
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
----------------------------------
Word_Page_00 : 0
Word_Page_01 : 0
Status_Byte_P00 : 0
Status_Byte_P01 : 0
Status_VOUT_P00 : 0
Status_VOUT_P01 : 0
Status_IOUT_P00 : 0
Status_IOUT_P01 : 0
Status_INPUT_P00 : 0
Status_INPUT_P01 : 0
Status_TEM_P00 : 0
Status_TEM_P01 : 0
Status_CML_P00 : 0
Status_CML_P01 : 0
Status_FANS_P00 : 0
Status_FANS_P01 : 0
STEP.819(UUT Test seq.819) : AC_DC Line Sag Surge 80611N-2_Multi_S2(DropOut PASS
ElapsedTime (S)= 3'885
Vin (V)= 220.00
Fin (Hz)= 30.00
Delay Time (ms)= 3000.00
Drop Time (ms)= 10.00
Drop Recovery Time(ms)= 500.00
Drop Voltage (v)= 0.00
Drop Frequency (Hz)= 30.00
Repeat Count = 1
Degree = 0
Duty cycle (%)= 100.000000
Load Loading Vpk Max Vpk Min Vpk High Vpk Low
Name (A/Ohm/V) (V) (V) (V) (V)
------------- ----------- --------- --------- --------- ---------
12V 113.050 12.810 11.590 12.214 12.194
12Vsb 1.750 12.600 11.400 12.049 12.041
PWOK 0.000 3.460 2.500 3.261 3.270
Vin_Good 0.000 3.460 ********* 3.253 0.052
SMBAlert 0.000 3.460 ********* 3.262 3.260
STEP.820(UUT Test seq.820) : I2C Read Status Multi_S6(DropOut H_220Vdc - 10 PASS
Adderss :B0
Command Page00 :060200
Command Page01 :060201
Status Word :79
Status Byte :78
Status VOUT :7A
Status IOUT :7B
Status INPUT :7C
Status TEMPERATURE :7D
Status CML :7E
Status FANS :81
---------------------------------
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
----------------------------------
Word_Page_00 : 0
Word_Page_01 : 0
Status_Byte_P00 : 0
Status_Byte_P01 : 0
Status_VOUT_P00 : 0
Status_VOUT_P01 : 0
Status_IOUT_P00 : 0
Status_IOUT_P01 : 0
Status_INPUT_P00 : 0
Status_INPUT_P01 : 0
Status_TEM_P00 : 0
Status_TEM_P01 : 0
Status_CML_P00 : 0
Status_CML_P01 : 0
Status_FANS_P00 : 0
Status_FANS_P01 : 0
STEP.821(UUT Test seq.821) : AC_DC Line Sag Surge 80611N-2_Multi_S2(DropOut PASS
ElapsedTime (S)= 3'885
Vin (V)= 220.00
Fin (Hz)= 30.00
Delay Time (ms)= 3000.00
Drop Time (ms)= 10.00
Drop Recovery Time(ms)= 500.00
Drop Voltage (v)= 0.00
Drop Frequency (Hz)= 30.00
Repeat Count = 1
Degree = 0
Duty cycle (%)= 100.000000
Load Loading Vpk Max Vpk Min Vpk High Vpk Low
Name (A/Ohm/V) (V) (V) (V) (V)
------------- ----------- --------- --------- --------- ---------
12V 113.050 12.810 11.590 12.214 12.194
12Vsb 1.750 12.600 11.400 12.049 12.042
PWOK 0.000 3.460 2.500 3.260 3.270
Vin_Good 0.000 3.460 ********* 3.253 0.055
SMBAlert 0.000 3.460 ********* 3.260 3.258
STEP.822(UUT Test seq.822) : I2C Read Status Multi_S6(DropOut H_220Vdc - 10 PASS
Adderss :B0
Command Page00 :060200
Command Page01 :060201
Status Word :79
Status Byte :78
Status VOUT :7A
Status IOUT :7B
Status INPUT :7C
Status TEMPERATURE :7D
Status CML :7E
Status FANS :81
---------------------------------
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
----------------------------------
Word_Page_00 : 0
Word_Page_01 : 0
Status_Byte_P00 : 0
Status_Byte_P01 : 0
Status_VOUT_P00 : 0
Status_VOUT_P01 : 0
Status_IOUT_P00 : 0
Status_IOUT_P01 : 0
Status_INPUT_P00 : 0
Status_INPUT_P01 : 0
Status_TEM_P00 : 0
Status_TEM_P01 : 0
Status_CML_P00 : 0
Status_CML_P01 : 0
Status_FANS_P00 : 0
Status_FANS_P01 : 0
STEP.823(UUT Test seq.823) : AC_DC Line Sag Surge 80611N-2_Multi_S2(DropOut PASS
ElapsedTime (S)= 3'900
Vin (V)= 220.00
Fin (Hz)= 30.00
Delay Time (ms)= 3000.00
Drop Time (ms)= 10.00
Drop Recovery Time(ms)= 500.00
Drop Voltage (v)= 0.00
Drop Frequency (Hz)= 30.00
Repeat Count = 1
Degree = 0
Duty cycle (%)= 100.000000
Load Loading Vpk Max Vpk Min Vpk High Vpk Low
Name (A/Ohm/V) (V) (V) (V) (V)
------------- ----------- --------- --------- --------- ---------
12V 113.050 12.810 11.590 12.214 12.196
12Vsb 1.750 12.600 11.400 12.050 12.041
PWOK 0.000 3.460 2.500 3.261 3.268
Vin_Good 0.000 3.460 ********* 3.256 0.057
SMBAlert 0.000 3.460 ********* 3.260 3.260
STEP.824(UUT Test seq.824) : I2C Read Status Multi_S6(DropOut H_220Vdc - 10 PASS
Adderss :B0
Command Page00 :060200
Command Page01 :060201
Status Word :79
Status Byte :78
Status VOUT :7A
Status IOUT :7B
Status INPUT :7C
Status TEMPERATURE :7D
Status CML :7E
Status FANS :81
---------------------------------
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
----------------------------------
Word_Page_00 : 0
Word_Page_01 : 0
Status_Byte_P00 : 0
Status_Byte_P01 : 0
Status_VOUT_P00 : 0
Status_VOUT_P01 : 0
Status_IOUT_P00 : 0
Status_IOUT_P01 : 0
Status_INPUT_P00 : 0
Status_INPUT_P01 : 0
Status_TEM_P00 : 0
Status_TEM_P01 : 0
Status_CML_P00 : 0
Status_CML_P01 : 0
Status_FANS_P00 : 0
Status_FANS_P01 : 0
STEP.825(UUT Test seq.825) : AC Source ON/OFF(input source)_Multi_S2 ---- ( PASS
(The Report Format of this Sequence was not found)
STEP.826(UUT Test seq.826) : Set Input Condition_Load_S4 ---- (0'015) ----- PASS
Vin (V)= 300.000
Fin (Hz)= 30.000
Load Loading
Name (A/Ohm/V)
------------- ----------
12V 113.0500
12Vsb 1.7500
PWOK 0.0000
Vin_Good 0.0000
SMBAlert 0.0000
STEP.827(UUT Test seq.827) : Set Drop Time ---- (0'000) ------------------- PASS
Drop Time= 10
STEP.828(UUT Test seq.828) : AC_DC Line Sag Surge 80611N-2_Multi_S2(DropOut PASS
ElapsedTime (S)= 3'962
Vin (V)= 300.00
Fin (Hz)= 30.00
Delay Time (ms)= 3000.00
Drop Time (ms)= 10.00
Drop Recovery Time(ms)= 500.00
Drop Voltage (v)= 0.00
Drop Frequency (Hz)= 30.00
Repeat Count = 1
Degree = 0
Duty cycle (%)= 100.000000
Load Loading Vpk Max Vpk Min Vpk High Vpk Low
Name (A/Ohm/V) (V) (V) (V) (V)
------------- ----------- --------- --------- --------- ---------
12V 113.050 12.810 11.590 12.213 12.194
12Vsb 1.750 12.600 11.400 12.049 12.040
PWOK 0.000 3.460 2.500 3.260 3.269
Vin_Good 0.000 3.460 ********* 3.255 0.056
SMBAlert 0.000 3.460 ********* 3.262 3.260
STEP.829(UUT Test seq.829) : I2C Read Status Multi_S6(DropOut H_300Vdc - 10 PASS
Adderss :B0
Command Page00 :060200
Command Page01 :060201
Status Word :79
Status Byte :78
Status VOUT :7A
Status IOUT :7B
Status INPUT :7C
Status TEMPERATURE :7D
Status CML :7E
Status FANS :81
---------------------------------
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
----------------------------------
Word_Page_00 : 0
Word_Page_01 : 0
Status_Byte_P00 : 0
Status_Byte_P01 : 0
Status_VOUT_P00 : 0
Status_VOUT_P01 : 0
Status_IOUT_P00 : 0
Status_IOUT_P01 : 0
Status_INPUT_P00 : 0
Status_INPUT_P01 : 0
Status_TEM_P00 : 0
Status_TEM_P01 : 0
Status_CML_P00 : 0
Status_CML_P01 : 0
Status_FANS_P00 : 0
Status_FANS_P01 : 0
STEP.830(UUT Test seq.830) : AC_DC Line Sag Surge 80611N-2_Multi_S2(DropOut PASS
ElapsedTime (S)= 3'900
Vin (V)= 300.00
Fin (Hz)= 30.00
Delay Time (ms)= 3000.00
Drop Time (ms)= 10.00
Drop Recovery Time(ms)= 500.00
Drop Voltage (v)= 0.00
Drop Frequency (Hz)= 30.00
Repeat Count = 1
Degree = 0
Duty cycle (%)= 100.000000
Load Loading Vpk Max Vpk Min Vpk High Vpk Low
Name (A/Ohm/V) (V) (V) (V) (V)
------------- ----------- --------- --------- --------- ---------
12V 113.050 12.810 11.590 12.214 12.194
12Vsb 1.750 12.600 11.400 12.049 12.040
PWOK 0.000 3.460 2.500 3.261 3.268
Vin_Good 0.000 3.460 ********* 3.255 0.055
SMBAlert 0.000 3.460 ********* 3.262 3.260
STEP.831(UUT Test seq.831) : I2C Read Status Multi_S6(DropOut H_300Vdc - 10 PASS
Adderss :B0
Command Page00 :060200
Command Page01 :060201
Status Word :79
Status Byte :78
Status VOUT :7A
Status IOUT :7B
Status INPUT :7C
Status TEMPERATURE :7D
Status CML :7E
Status FANS :81
---------------------------------
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
----------------------------------
Word_Page_00 : 0
Word_Page_01 : 0
Status_Byte_P00 : 0
Status_Byte_P01 : 0
Status_VOUT_P00 : 0
Status_VOUT_P01 : 0
Status_IOUT_P00 : 0
Status_IOUT_P01 : 0
Status_INPUT_P00 : 0
Status_INPUT_P01 : 0
Status_TEM_P00 : 0
Status_TEM_P01 : 0
Status_CML_P00 : 0
Status_CML_P01 : 0
Status_FANS_P00 : 0
Status_FANS_P01 : 0
STEP.832(UUT Test seq.832) : AC_DC Line Sag Surge 80611N-2_Multi_S2(DropOut PASS
ElapsedTime (S)= 3'884
Vin (V)= 300.00
Fin (Hz)= 30.00
Delay Time (ms)= 3000.00
Drop Time (ms)= 10.00
Drop Recovery Time(ms)= 500.00
Drop Voltage (v)= 0.00
Drop Frequency (Hz)= 30.00
Repeat Count = 1
Degree = 0
Duty cycle (%)= 100.000000
Load Loading Vpk Max Vpk Min Vpk High Vpk Low
Name (A/Ohm/V) (V) (V) (V) (V)
------------- ----------- --------- --------- --------- ---------
12V 113.050 12.810 11.590 12.213 12.193
12Vsb 1.750 12.600 11.400 12.049 12.041
PWOK 0.000 3.460 2.500 3.261 3.268
Vin_Good 0.000 3.460 ********* 3.255 0.054
SMBAlert 0.000 3.460 ********* 3.262 3.260
STEP.833(UUT Test seq.833) : I2C Read Status Multi_S6(DropOut H_300Vdc - 10 PASS
Adderss :B0
Command Page00 :060200
Command Page01 :060201
Status Word :79
Status Byte :78
Status VOUT :7A
Status IOUT :7B
Status INPUT :7C
Status TEMPERATURE :7D
Status CML :7E
Status FANS :81
---------------------------------
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
----------------------------------
Word_Page_00 : 0
Word_Page_01 : 0
Status_Byte_P00 : 0
Status_Byte_P01 : 0
Status_VOUT_P00 : 0
Status_VOUT_P01 : 0
Status_IOUT_P00 : 0
Status_IOUT_P01 : 0
Status_INPUT_P00 : 0
Status_INPUT_P01 : 0
Status_TEM_P00 : 0
Status_TEM_P01 : 0
Status_CML_P00 : 0
Status_CML_P01 : 0
Status_FANS_P00 : 0
Status_FANS_P01 : 0
STEP.834(UUT Test seq.834) : AC_DC Line Sag Surge 80611N-2_Multi_S2(DropOut PASS
ElapsedTime (S)= 3'900
Vin (V)= 300.00
Fin (Hz)= 30.00
Delay Time (ms)= 3000.00
Drop Time (ms)= 10.00
Drop Recovery Time(ms)= 500.00
Drop Voltage (v)= 0.00
Drop Frequency (Hz)= 30.00
Repeat Count = 1
Degree = 0
Duty cycle (%)= 100.000000
Load Loading Vpk Max Vpk Min Vpk High Vpk Low
Name (A/Ohm/V) (V) (V) (V) (V)
------------- ----------- --------- --------- --------- ---------
12V 113.050 12.810 11.590 12.214 12.194
12Vsb 1.750 12.600 11.400 12.047 12.040
PWOK 0.000 3.460 2.500 3.263 3.270
Vin_Good 0.000 3.460 ********* 3.256 0.055
SMBAlert 0.000 3.460 ********* 3.262 3.260
STEP.835(UUT Test seq.835) : I2C Read Status Multi_S6(DropOut H_300Vdc - 10 PASS
Adderss :B0
Command Page00 :060200
Command Page01 :060201
Status Word :79
Status Byte :78
Status VOUT :7A
Status IOUT :7B
Status INPUT :7C
Status TEMPERATURE :7D
Status CML :7E
Status FANS :81
---------------------------------
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
----------------------------------
Word_Page_00 : 0
Word_Page_01 : 0
Status_Byte_P00 : 0
Status_Byte_P01 : 0
Status_VOUT_P00 : 0
Status_VOUT_P01 : 0
Status_IOUT_P00 : 0
Status_IOUT_P01 : 0
Status_INPUT_P00 : 0
Status_INPUT_P01 : 0
Status_TEM_P00 : 0
Status_TEM_P01 : 0
Status_CML_P00 : 0
Status_CML_P01 : 0
Status_FANS_P00 : 0
Status_FANS_P01 : 0
STEP.836(UUT Test seq.836) : AC_DC Line Sag Surge 80611N-2_Multi_S2(DropOut PASS
ElapsedTime (S)= 3'900
Vin (V)= 300.00
Fin (Hz)= 30.00
Delay Time (ms)= 3000.00
Drop Time (ms)= 10.00
Drop Recovery Time(ms)= 500.00
Drop Voltage (v)= 0.00
Drop Frequency (Hz)= 30.00
Repeat Count = 1
Degree = 0
Duty cycle (%)= 100.000000
Load Loading Vpk Max Vpk Min Vpk High Vpk Low
Name (A/Ohm/V) (V) (V) (V) (V)
------------- ----------- --------- --------- --------- ---------
12V 113.050 12.810 11.590 12.215 12.194
12Vsb 1.750 12.600 11.400 12.049 12.041
PWOK 0.000 3.460 2.500 3.262 3.268
Vin_Good 0.000 3.460 ********* 3.254 0.053
SMBAlert 0.000 3.460 ********* 3.260 3.261
STEP.837(UUT Test seq.837) : I2C Read Status Multi_S6(DropOut H_300Vdc - 10 PASS
Adderss :B0
Command Page00 :060200
Command Page01 :060201
Status Word :79
Status Byte :78
Status VOUT :7A
Status IOUT :7B
Status INPUT :7C
Status TEMPERATURE :7D
Status CML :7E
Status FANS :81
---------------------------------
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
----------------------------------
Word_Page_00 : 0
Word_Page_01 : 0
Status_Byte_P00 : 0
Status_Byte_P01 : 0
Status_VOUT_P00 : 0
Status_VOUT_P01 : 0
Status_IOUT_P00 : 0
Status_IOUT_P01 : 0
Status_INPUT_P00 : 0
Status_INPUT_P01 : 0
Status_TEM_P00 : 0
Status_TEM_P01 : 0
Status_CML_P00 : 0
Status_CML_P01 : 0
Status_FANS_P00 : 0
Status_FANS_P01 : 0
STEP.838(UUT Test seq.838) : AC_DC Line Sag Surge 80611N-2_Multi_S2(DropOut PASS
ElapsedTime (S)= 3'884
Vin (V)= 300.00
Fin (Hz)= 30.00
Delay Time (ms)= 3000.00
Drop Time (ms)= 10.00
Drop Recovery Time(ms)= 500.00
Drop Voltage (v)= 0.00
Drop Frequency (Hz)= 30.00
Repeat Count = 1
Degree = 0
Duty cycle (%)= 100.000000
Load Loading Vpk Max Vpk Min Vpk High Vpk Low
Name (A/Ohm/V) (V) (V) (V) (V)
------------- ----------- --------- --------- --------- ---------
12V 113.050 12.810 11.590 12.215 12.194
12Vsb 1.750 12.600 11.400 12.049 12.041
PWOK 0.000 3.460 2.500 3.260 3.270
Vin_Good 0.000 3.460 ********* 3.256 0.055
SMBAlert 0.000 3.460 ********* 3.262 3.261
STEP.839(UUT Test seq.839) : I2C Read Status Multi_S6(DropOut H_300Vdc - 10 PASS
Adderss :B0
Command Page00 :060200
Command Page01 :060201
Status Word :79
Status Byte :78
Status VOUT :7A
Status IOUT :7B
Status INPUT :7C
Status TEMPERATURE :7D
Status CML :7E
Status FANS :81
---------------------------------
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
----------------------------------
Word_Page_00 : 0
Word_Page_01 : 0
Status_Byte_P00 : 0
Status_Byte_P01 : 0
Status_VOUT_P00 : 0
Status_VOUT_P01 : 0
Status_IOUT_P00 : 0
Status_IOUT_P01 : 0
Status_INPUT_P00 : 0
Status_INPUT_P01 : 0
Status_TEM_P00 : 0
Status_TEM_P01 : 0
Status_CML_P00 : 0
Status_CML_P01 : 0
Status_FANS_P00 : 0
Status_FANS_P01 : 0
STEP.840(UUT Test seq.840) : AC_DC Line Sag Surge 80611N-2_Multi_S2(DropOut PASS
ElapsedTime (S)= 3'869
Vin (V)= 300.00
Fin (Hz)= 30.00
Delay Time (ms)= 3000.00
Drop Time (ms)= 10.00
Drop Recovery Time(ms)= 500.00
Drop Voltage (v)= 0.00
Drop Frequency (Hz)= 30.00
Repeat Count = 1
Degree = 0
Duty cycle (%)= 100.000000
Load Loading Vpk Max Vpk Min Vpk High Vpk Low
Name (A/Ohm/V) (V) (V) (V) (V)
------------- ----------- --------- --------- --------- ---------
12V 113.050 12.810 11.590 12.214 12.193
12Vsb 1.750 12.600 11.400 12.049 12.040
PWOK 0.000 3.460 2.500 3.260 3.269
Vin_Good 0.000 3.460 ********* 3.254 0.056
SMBAlert 0.000 3.460 ********* 3.260 3.260
STEP.841(UUT Test seq.841) : I2C Read Status Multi_S6(DropOut H_300Vdc - 10 PASS
Adderss :B0
Command Page00 :060200
Command Page01 :060201
Status Word :79
Status Byte :78
Status VOUT :7A
Status IOUT :7B
Status INPUT :7C
Status TEMPERATURE :7D
Status CML :7E
Status FANS :81
---------------------------------
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
----------------------------------
Word_Page_00 : 0
Word_Page_01 : 0
Status_Byte_P00 : 0
Status_Byte_P01 : 0
Status_VOUT_P00 : 0
Status_VOUT_P01 : 0
Status_IOUT_P00 : 0
Status_IOUT_P01 : 0
Status_INPUT_P00 : 0
Status_INPUT_P01 : 0
Status_TEM_P00 : 0
Status_TEM_P01 : 0
Status_CML_P00 : 0
Status_CML_P01 : 0
Status_FANS_P00 : 0
Status_FANS_P01 : 0
STEP.842(UUT Test seq.842) : AC_DC Line Sag Surge 80611N-2_Multi_S2(DropOut PASS
ElapsedTime (S)= 3'900
Vin (V)= 300.00
Fin (Hz)= 30.00
Delay Time (ms)= 3000.00
Drop Time (ms)= 10.00
Drop Recovery Time(ms)= 500.00
Drop Voltage (v)= 0.00
Drop Frequency (Hz)= 30.00
Repeat Count = 1
Degree = 0
Duty cycle (%)= 100.000000
Load Loading Vpk Max Vpk Min Vpk High Vpk Low
Name (A/Ohm/V) (V) (V) (V) (V)
------------- ----------- --------- --------- --------- ---------
12V 113.050 12.810 11.590 12.213 12.194
12Vsb 1.750 12.600 11.400 12.049 12.042
PWOK 0.000 3.460 2.500 3.261 3.268
Vin_Good 0.000 3.460 ********* 3.255 0.053
SMBAlert 0.000 3.460 ********* 3.262 3.260
STEP.843(UUT Test seq.843) : I2C Read Status Multi_S6(DropOut H_300Vdc - 10 PASS
Adderss :B0
Command Page00 :060200
Command Page01 :060201
Status Word :79
Status Byte :78
Status VOUT :7A
Status IOUT :7B
Status INPUT :7C
Status TEMPERATURE :7D
Status CML :7E
Status FANS :81
---------------------------------
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
----------------------------------
Word_Page_00 : 0
Word_Page_01 : 0
Status_Byte_P00 : 0
Status_Byte_P01 : 0
Status_VOUT_P00 : 0
Status_VOUT_P01 : 0
Status_IOUT_P00 : 0
Status_IOUT_P01 : 0
Status_INPUT_P00 : 0
Status_INPUT_P01 : 0
Status_TEM_P00 : 0
Status_TEM_P01 : 0
Status_CML_P00 : 0
Status_CML_P01 : 0
Status_FANS_P00 : 0
Status_FANS_P01 : 0
STEP.844(UUT Test seq.844) : AC_DC Line Sag Surge 80611N-2_Multi_S2(DropOut PASS
ElapsedTime (S)= 3'869
Vin (V)= 300.00
Fin (Hz)= 30.00
Delay Time (ms)= 3000.00
Drop Time (ms)= 10.00
Drop Recovery Time(ms)= 500.00
Drop Voltage (v)= 0.00
Drop Frequency (Hz)= 30.00
Repeat Count = 1
Degree = 0
Duty cycle (%)= 100.000000
Load Loading Vpk Max Vpk Min Vpk High Vpk Low
Name (A/Ohm/V) (V) (V) (V) (V)
------------- ----------- --------- --------- --------- ---------
12V 113.050 12.810 11.590 12.214 12.196
12Vsb 1.750 12.600 11.400 12.049 12.040
PWOK 0.000 3.460 2.500 3.263 3.268
Vin_Good 0.000 3.460 ********* 3.255 0.053
SMBAlert 0.000 3.460 ********* 3.262 3.261
STEP.845(UUT Test seq.845) : I2C Read Status Multi_S6(DropOut H_300Vdc - 10 PASS
Adderss :B0
Command Page00 :060200
Command Page01 :060201
Status Word :79
Status Byte :78
Status VOUT :7A
Status IOUT :7B
Status INPUT :7C
Status TEMPERATURE :7D
Status CML :7E
Status FANS :81
---------------------------------
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
----------------------------------
Word_Page_00 : 0
Word_Page_01 : 0
Status_Byte_P00 : 0
Status_Byte_P01 : 0
Status_VOUT_P00 : 0
Status_VOUT_P01 : 0
Status_IOUT_P00 : 0
Status_IOUT_P01 : 0
Status_INPUT_P00 : 0
Status_INPUT_P01 : 0
Status_TEM_P00 : 0
Status_TEM_P01 : 0
Status_CML_P00 : 0
Status_CML_P01 : 0
Status_FANS_P00 : 0
Status_FANS_P01 : 0
STEP.846(UUT Test seq.846) : AC_DC Line Sag Surge 80611N-2_Multi_S2(DropOut PASS
ElapsedTime (S)= 3'994
Vin (V)= 300.00
Fin (Hz)= 30.00
Delay Time (ms)= 3000.00
Drop Time (ms)= 10.00
Drop Recovery Time(ms)= 500.00
Drop Voltage (v)= 0.00
Drop Frequency (Hz)= 30.00
Repeat Count = 1
Degree = 0
Duty cycle (%)= 100.000000
Load Loading Vpk Max Vpk Min Vpk High Vpk Low
Name (A/Ohm/V) (V) (V) (V) (V)
------------- ----------- --------- --------- --------- ---------
12V 113.050 12.810 11.590 12.215 12.194
12Vsb 1.750 12.600 11.400 12.049 12.040
PWOK 0.000 3.460 2.500 3.261 3.268
Vin_Good 0.000 3.460 ********* 3.254 0.056
SMBAlert 0.000 3.460 ********* 3.260 3.259
STEP.847(UUT Test seq.847) : I2C Read Status Multi_S6(DropOut H_300Vdc - 10 PASS
Adderss :B0
Command Page00 :060200
Command Page01 :060201
Status Word :79
Status Byte :78
Status VOUT :7A
Status IOUT :7B
Status INPUT :7C
Status TEMPERATURE :7D
Status CML :7E
Status FANS :81
---------------------------------
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Word SPEC_Page1: 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
Byte SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
VOUT SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Iout SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Input SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
Temperature SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
CML SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
FAN SPEC : 0
----------------------------------
Word_Page_00 : 0
Word_Page_01 : 0
Status_Byte_P00 : 0
Status_Byte_P01 : 0
Status_VOUT_P00 : 0
Status_VOUT_P01 : 0
Status_IOUT_P00 : 0
Status_IOUT_P01 : 0
Status_INPUT_P00 : 0
Status_INPUT_P01 : 0
Status_TEM_P00 : 0
Status_TEM_P01 : 0
Status_CML_P00 : 0
Status_CML_P01 : 0
Status_FANS_P00 : 0
Status_FANS_P01 : 0
STEP.848(UUT Test seq.848) : SUB20-Relay ---- (0'514) --------------------- PASS
Relay State 1: 00
Relay State 2: 00
Relay Change State Delay Time(ms): 500
STEP.849(UUT Test seq.849) : UUT Off_Multi_S2 ---- (1'076) ---------------- PASS
STEP.850(UUT Test seq.850) : 61512 Ac Source ACDC Mode_Multi_S2 ---- (0'171 PASS
(The Report Format of this Sequence was not found)

## TurnOn
---------------------------------------
Tac_on_delay_CapLoad
SEQ | Vin | Fin | Main_Load(A) | Vsb_Load(A) | SPEC_Max | SPEC_Min | Value | Result | Ext
18 | 90 | 47 | 1 | 0.1 | 3000 | 1 | 1480.94 | PASS | 90V_47Hz_LL
27 | 90 | 47 | 71.3 | 2.5 | 3000 | 1 | 1374.46 | PASS | 90V_47Hz_HH
36 | 100 | 60 | 79.5 | 2.5 | 3000 | 1 | 1281.22 | PASS | 100V_60Hz_HH
45 | 180 | 47 | 128.7 | 2.5 | 3000 | 1 | 1118.21 | PASS | 180V_47Hz_HH
54 | 200 | 50 | 145.1 | 2.5 | 3000 | 1 | 1064.22 | PASS | 200V_50Hz_HH
63 | 220 | 50 | 161.5 | 2.5 | 3000 | 1 | 1032.4 | PASS | 220V_50Hz_HH
72 | 264 | 63 | 1 | 0.1 | 3000 | 1 | 1005.77 | PASS | 264V_63Hz_LL
81 | 264 | 63 | 161.5 | 2.5 | 3000 | 1 | 1554.59 | PASS | 264V_63Hz_HH
91 | 164 | 30 | 1 | 0.1 | 3000 | 1 | 1269.02 | PASS | 164VDC_LL
100 | 164 | 30 | 128.7 | 2.5 | 3000 | 1 | 1263.99 | PASS | 164VDC_HH
109 | 200 | 30 | 145.1 | 2.5 | 3000 | 1 | 1180.26 | PASS | 200VDC_HH
117 | 220 | 30 | 161.5 | 2.5 | 3000 | 1 | 1140.04 | PASS | 220VDC_HH
126 | 300 | 30 | 1 | 0.1 | 3000 | 1 | 979.96 | PASS | 300VDC_LL
135 | 300 | 30 | 161.5 | 2.5 | 3000 | 1 | 986.88 | PASS | 300VDC_HH
---------------------------------------
Tsb_on_delay_CapLoad
SEQ | Vin | Fin | Main_Load(A) | Vsb_Load(A) | SPEC_Max | SPEC_Min | Value | Result | Ext
18 | 90 | 47 | 1 | 0.1 | 1500 | 1 | 1236.31 | PASS | 90V_47Hz_LL
27 | 90 | 47 | 71.3 | 2.5 | 1500 | 1 | 1129.26 | PASS | 90V_47Hz_HH
36 | 100 | 60 | 79.5 | 2.5 | 1500 | 1 | 1036.03 | PASS | 100V_60Hz_HH
45 | 180 | 47 | 128.7 | 2.5 | 1500 | 1 | 872.88 | PASS | 180V_47Hz_HH
54 | 200 | 50 | 145.1 | 2.5 | 1500 | 1 | 818.65 | PASS | 200V_50Hz_HH
63 | 220 | 50 | 161.5 | 2.5 | 1500 | 1 | 786.78 | PASS | 220V_50Hz_HH
72 | 264 | 63 | 1 | 0.1 | 1500 | 1 | 761.36 | PASS | 264V_63Hz_LL
81 | 264 | 63 | 161.5 | 2.5 | 1500 | 1 | 1309.1 | PASS | 264V_63Hz_HH
91 | 164 | 30 | 1 | 0.1 | 1500 | 1 | 1024.6 | PASS | 164VDC_LL
100 | 164 | 30 | 128.7 | 2.5 | 1500 | 1 | 1018.59 | PASS | 164VDC_HH
109 | 200 | 30 | 145.1 | 2.5 | 1500 | 1 | 934.75 | PASS | 200VDC_HH
117 | 220 | 30 | 161.5 | 2.5 | 1500 | 1 | 894.46 | PASS | 220VDC_HH
126 | 300 | 30 | 1 | 0.1 | 1500 | 1 | 735.5 | PASS | 300VDC_LL
135 | 300 | 30 | 161.5 | 2.5 | 1500 | 1 | 741.37 | PASS | 300VDC_HH
---------------------------------------
Tpwok_on_delay_CapLoad
SEQ | Vin | Fin | Main_Load(A) | Vsb_Load(A) | SPEC_Max | SPEC_Min | Value | Result | Ext
18 | 90 | 47 | 1 | 0.1 | 500 | 100 | 206.02 | PASS | 90V_47Hz_LL
27 | 90 | 47 | 71.3 | 2.5 | 500 | 100 | 205.76 | PASS | 90V_47Hz_HH
36 | 100 | 60 | 79.5 | 2.5 | 500 | 100 | 205.71 | PASS | 100V_60Hz_HH
45 | 180 | 47 | 128.7 | 2.5 | 500 | 100 | 205.55 | PASS | 180V_47Hz_HH
54 | 200 | 50 | 145.1 | 2.5 | 500 | 100 | 205.56 | PASS | 200V_50Hz_HH
63 | 220 | 50 | 161.5 | 2.5 | 500 | 100 | 205.46 | PASS | 220V_50Hz_HH
72 | 264 | 63 | 1 | 0.1 | 500 | 100 | 205.9 | PASS | 264V_63Hz_LL
81 | 264 | 63 | 161.5 | 2.5 | 500 | 100 | 205.51 | PASS | 264V_63Hz_HH
91 | 164 | 30 | 1 | 0.1 | 500 | 100 | 205.91 | PASS | 164VDC_LL
100 | 164 | 30 | 128.7 | 2.5 | 500 | 100 | 205.7 | PASS | 164VDC_HH
109 | 200 | 30 | 145.1 | 2.5 | 500 | 100 | 205.5 | PASS | 200VDC_HH
117 | 220 | 30 | 161.5 | 2.5 | 500 | 100 | 205.51 | PASS | 220VDC_HH
126 | 300 | 30 | 1 | 0.1 | 500 | 100 | 205.95 | PASS | 300VDC_LL
135 | 300 | 30 | 161.5 | 2.5 | 500 | 100 | 205.43 | PASS | 300VDC_HH
---------------------------------------
Tac on delay
SEQ | Vin | Fin | Main_Load(A) | Vsb_Load(A) | SPEC_Max | SPEC_Min | Value | Result | Ext
8 | 264 | 63 | 161.5 | 2.5 | 3000 | 1 | 1047.66 | PASS | 264V_63Hz_HH
147 | 90 | 47 | 1 | 0.1 | 3000 | 1 | 1449.24 | PASS | 90V_47Hz_LL
175 | 90 | 47 | 71.3 | 2.5 | 3000 | 1 | 1352.78 | PASS | 90V_47Hz_HH
203 | 100 | 60 | 79.5 | 2.5 | 3000 | 1 | 1256.65 | PASS | 100V_60Hz_HH
233 | 180 | 47 | 128.7 | 2.5 | 3000 | 1 | 1075.81 | PASS | 180V_47Hz_HH
263 | 200 | 50 | 145.1 | 2.5 | 3000 | 1 | 1023.15 | PASS | 200V_50Hz_HH
293 | 220 | 50 | 161.5 | 2.5 | 3000 | 1 | 996.92 | PASS | 220V_50Hz_HH
327 | 264 | 63 | 1 | 0.1 | 3000 | 1 | 927.59 | PASS | 264V_63Hz_LL
358 | 264 | 63 | 161.5 | 2.5 | 3000 | 1 | 974.47 | PASS | 264V_63Hz_HH
393 | 164 | 30 | 1 | 0.1 | 3000 | 1 | 1217.25 | PASS | 164VDC_LL
426 | 164 | 30 | 128.7 | 2.5 | 3000 | 1 | 1230.17 | PASS | 164VDC_HH
447 | 200 | 30 | 145.1 | 2.5 | 3000 | 1 | 1158.44 | PASS | 200Vdc_HH
466 | 220 | 30 | 161.5 | 2.5 | 3000 | 1 | 1117.93 | PASS | 220VDC_HH
486 | 300 | 30 | 1 | 0.1 | 3000 | 1 | 947.6 | PASS | 300VDC_LL
519 | 300 | 30 | 161.5 | 2.5 | 3000 | 1 | 952.16 | PASS | 300VDC_HH
---------------------------------------
Tsb on delay
SEQ | Vin | Fin | Main_Load(A) | Vsb_Load(A) | SPEC_Max | SPEC_Min | Value | Result | Ext
8 | 264 | 63 | 161.5 | 2.5 | 1500 | 1 | 802.18 | PASS | 264V_63Hz_HH
147 | 90 | 47 | 1 | 0.1 | 1500 | 1 | 1204.82 | PASS | 90V_47Hz_LL
175 | 90 | 47 | 71.3 | 2.5 | 1500 | 1 | 1107.66 | PASS | 90V_47Hz_HH
203 | 100 | 60 | 79.5 | 2.5 | 1500 | 1 | 1011.4 | PASS | 100V_60Hz_HH
233 | 180 | 47 | 128.7 | 2.5 | 1500 | 1 | 830.41 | PASS | 180V_47Hz_HH
263 | 200 | 50 | 145.1 | 2.5 | 1500 | 1 | 777.67 | PASS | 200V_50Hz_HH
293 | 220 | 50 | 161.5 | 2.5 | 1500 | 1 | 751.19 | PASS | 220V_50Hz_HH
327 | 264 | 63 | 1 | 0.1 | 1500 | 1 | 683.05 | PASS | 264V_63Hz_LL
358 | 264 | 63 | 161.5 | 2.5 | 1500 | 1 | 728.82 | PASS | 264V_63Hz_HH
393 | 164 | 30 | 1 | 0.1 | 1500 | 1 | 972.72 | PASS | 164VDC_LL
426 | 164 | 30 | 128.7 | 2.5 | 1500 | 1 | 984.63 | PASS | 164VDC_HH
447 | 200 | 30 | 145.1 | 2.5 | 1500 | 1 | 912.87 | PASS | 200Vdc_HH
466 | 220 | 30 | 161.5 | 2.5 | 1500 | 1 | 872.3 | PASS | 220VDC_HH
486 | 300 | 30 | 1 | 0.1 | 1500 | 1 | 703.04 | PASS | 300VDC_LL
519 | 300 | 30 | 161.5 | 2.5 | 1500 | 1 | 706.5 | PASS | 300VDC_HH
---------------------------------------
Tpwok on delay
SEQ | Vin | Fin | Main_Load(A) | Vsb_Load(A) | SPEC_Max | SPEC_Min | Value | Result | Ext
8 | 264 | 63 | 161.5 | 2.5 | 500 | 100 | 205.74 | PASS | 264V_63Hz_HH
147 | 90 | 47 | 1 | 0.1 | 500 | 100 | 205.84 | PASS | 90V_47Hz_LL
175 | 90 | 47 | 71.3 | 2.5 | 500 | 100 | 205.8 | PASS | 90V_47Hz_HH
203 | 100 | 60 | 79.5 | 2.5 | 500 | 100 | 205.83 | PASS | 100V_60Hz_HH
233 | 180 | 47 | 128.7 | 2.5 | 500 | 100 | 205.75 | PASS | 180V_47Hz_HH
263 | 200 | 50 | 145.1 | 2.5 | 500 | 100 | 205.57 | PASS | 200V_50Hz_HH
293 | 220 | 50 | 161.5 | 2.5 | 500 | 100 | 205.67 | PASS | 220V_50Hz_HH
327 | 264 | 63 | 1 | 0.1 | 500 | 100 | 205.94 | PASS | 264V_63Hz_LL
358 | 264 | 63 | 161.5 | 2.5 | 500 | 100 | 205.51 | PASS | 264V_63Hz_HH
393 | 164 | 30 | 1 | 0.1 | 500 | 100 | 205.85 | PASS | 164VDC_LL
426 | 164 | 30 | 128.7 | 2.5 | 500 | 100 | 205.58 | PASS | 164VDC_HH
447 | 200 | 30 | 145.1 | 2.5 | 500 | 100 | 205.58 | PASS | 200Vdc_HH
466 | 220 | 30 | 161.5 | 2.5 | 500 | 100 | 205.41 | PASS | 220VDC_HH
486 | 300 | 30 | 1 | 0.1 | 500 | 100 | 205.86 | PASS | 300VDC_LL
519 | 300 | 30 | 161.5 | 2.5 | 500 | 100 | 205.54 | PASS | 300VDC_HH
---------------------------------------
MainRiseTime_CapLoad
SEQ | Vin | Fin | Main_Load(A) | Vsb_Load(A) | SPEC_Max | SPEC_Min | Value | Result | Ext
21 | 90 | 47 | 1 | 0.1 | 70 | 5 | 51.27 | PASS | 90V_47Hz_LL_Tac_12V_12Vsb_Rise
30 | 90 | 47 | 71.3 | 2.5 | 70 | 5 | 51.3 | PASS | 90V_47Hz_HH_Tac_12V_12Vsb_Rise
39 | 100 | 60 | 79.5 | 2.5 | 70 | 5 | 51.27 | PASS | 100V_60Hz_HH_Tac_12V_12Vsb_Rise
48 | 180 | 47 | 128.7 | 2.5 | 70 | 5 | 51.28 | PASS | 180V_47Hz_HH_Tac_12V_12Vsb_Rise
57 | 200 | 50 | 145.1 | 2.5 | 70 | 5 | 51.29 | PASS | 200V_50Hz_HH_Tac_12V_12Vsb_Rise
66 | 220 | 50 | 161.5 | 2.5 | 70 | 5 | 51.29 | PASS | 220V_50Hz_HH_Tac_12V_12Vsb_Rise
75 | 264 | 63 | 1 | 0.1 | 70 | 5 | 51.28 | PASS | 264V_63Hz_LL_Tac_12V_12Vsb_Rise
84 | 264 | 63 | 161.5 | 2.5 | 70 | 5 | 51.28 | PASS | 264V_63Hz_HH_Tac_12V_12Vsb_Rise
94 | 164 | 30 | 1 | 0.1 | 70 | 5 | 51.3 | PASS | 164VDC_LL_Tac_12V_12Vsb_Rise
103 | 164 | 30 | 128.7 | 2.5 | 70 | 5 | 51.24 | PASS | 164VDC_HH_Tac_12V_12Vsb_Rise
112 | 200 | 30 | 145.1 | 2.5 | 70 | 5 | 51.28 | PASS | 200VDC_HH_Tac_12V_12Vsb_Rise
120 | 220 | 30 | 161.5 | 2.5 | 70 | 5 | 51.28 | PASS | 220VDC_HH_Tac_12V_12Vsb_Rise
129 | 300 | 30 | 1 | 0.1 | 70 | 5 | 51.26 | PASS | 300VDC_LL_Tac_12V_12Vsb_Rise
138 | 300 | 30 | 161.5 | 2.5 | 70 | 5 | 51.27 | PASS | 300VDC_HH_Tac_12V_12Vsb_Rise
---------------------------------------
VsbRiseTime_CapLoad
SEQ | Vin | Fin | Main_Load(A) | Vsb_Load(A) | SPEC_Max | SPEC_Min | Value | Result | Ext
21 | 90 | 47 | 1 | 0.1 | 70 | 1 | 12.9 | PASS | 90V_47Hz_LL_Tac_12V_12Vsb_Rise
30 | 90 | 47 | 71.3 | 2.5 | 70 | 1 | 11.97 | PASS | 90V_47Hz_HH_Tac_12V_12Vsb_Rise
39 | 100 | 60 | 79.5 | 2.5 | 70 | 1 | 11.97 | PASS | 100V_60Hz_HH_Tac_12V_12Vsb_Rise
48 | 180 | 47 | 128.7 | 2.5 | 70 | 1 | 11.94 | PASS | 180V_47Hz_HH_Tac_12V_12Vsb_Rise
57 | 200 | 50 | 145.1 | 2.5 | 70 | 1 | 11.92 | PASS | 200V_50Hz_HH_Tac_12V_12Vsb_Rise
66 | 220 | 50 | 161.5 | 2.5 | 70 | 1 | 11.9 | PASS | 220V_50Hz_HH_Tac_12V_12Vsb_Rise
75 | 264 | 63 | 1 | 0.1 | 70 | 1 | 12.81 | PASS | 264V_63Hz_LL_Tac_12V_12Vsb_Rise
84 | 264 | 63 | 161.5 | 2.5 | 70 | 1 | 11.89 | PASS | 264V_63Hz_HH_Tac_12V_12Vsb_Rise
94 | 164 | 30 | 1 | 0.1 | 70 | 1 | 12.79 | PASS | 164VDC_LL_Tac_12V_12Vsb_Rise
103 | 164 | 30 | 128.7 | 2.5 | 70 | 1 | 11.89 | PASS | 164VDC_HH_Tac_12V_12Vsb_Rise
112 | 200 | 30 | 145.1 | 2.5 | 70 | 1 | 11.88 | PASS | 200VDC_HH_Tac_12V_12Vsb_Rise
120 | 220 | 30 | 161.5 | 2.5 | 70 | 1 | 11.87 | PASS | 220VDC_HH_Tac_12V_12Vsb_Rise
129 | 300 | 30 | 1 | 0.1 | 70 | 1 | 12.76 | PASS | 300VDC_LL_Tac_12V_12Vsb_Rise
138 | 300 | 30 | 161.5 | 2.5 | 70 | 1 | 11.85 | PASS | 300VDC_HH_Tac_12V_12Vsb_Rise
---------------------------------------
PG_RiseTime_CapLoad
SEQ | Vin | Fin | Main_Load(A) | Vsb_Load(A) | SPEC_Max | SPEC_Min | Value | Result | Ext
21 | 90 | 47 | 1 | 0.1 | ******** | ******** | 0.06 | PASS | 90V_47Hz_LL_Tac_12V_12Vsb_Rise
30 | 90 | 47 | 71.3 | 2.5 | ******** | ******** | 0.06 | PASS | 90V_47Hz_HH_Tac_12V_12Vsb_Rise
39 | 100 | 60 | 79.5 | 2.5 | ******** | ******** | 0.06 | PASS | 100V_60Hz_HH_Tac_12V_12Vsb_Rise
48 | 180 | 47 | 128.7 | 2.5 | ******** | ******** | 0.06 | PASS | 180V_47Hz_HH_Tac_12V_12Vsb_Rise
57 | 200 | 50 | 145.1 | 2.5 | ******** | ******** | 0.06 | PASS | 200V_50Hz_HH_Tac_12V_12Vsb_Rise
66 | 220 | 50 | 161.5 | 2.5 | ******** | ******** | 0.06 | PASS | 220V_50Hz_HH_Tac_12V_12Vsb_Rise
75 | 264 | 63 | 1 | 0.1 | ******** | ******** | 0.06 | PASS | 264V_63Hz_LL_Tac_12V_12Vsb_Rise
84 | 264 | 63 | 161.5 | 2.5 | ******** | ******** | 0.06 | PASS | 264V_63Hz_HH_Tac_12V_12Vsb_Rise
94 | 164 | 30 | 1 | 0.1 | ******** | ******** | 0.06 | PASS | 164VDC_LL_Tac_12V_12Vsb_Rise
103 | 164 | 30 | 128.7 | 2.5 | ******** | ******** | 0.06 | PASS | 164VDC_HH_Tac_12V_12Vsb_Rise
112 | 200 | 30 | 145.1 | 2.5 | ******** | ******** | 0.06 | PASS | 200VDC_HH_Tac_12V_12Vsb_Rise
120 | 220 | 30 | 161.5 | 2.5 | ******** | ******** | 0.06 | PASS | 220VDC_HH_Tac_12V_12Vsb_Rise
129 | 300 | 30 | 1 | 0.1 | ******** | ******** | 0.06 | PASS | 300VDC_LL_Tac_12V_12Vsb_Rise
138 | 300 | 30 | 161.5 | 2.5 | ******** | ******** | 0.06 | PASS | 300VDC_HH_Tac_12V_12Vsb_Rise
---------------------------------------
MainRiseTime
SEQ | Vin | Fin | Main_Load(A) | Vsb_Load(A) | SPEC_Max | SPEC_Min | Value | Result | Ext
158 | 90 | 47 | 1 | 0.1 | 70 | 5 | 51.26 | PASS | 90V_47Hz_LL_Tac_12V_12Vsb_Rise
184 | 90 | 47 | 71.3 | 2.5 | 70 | 5 | 51.25 | PASS | 90V_47Hz_HH_Tac_12V_12Vsb_Rise
207 | 100 | 60 | 79.5 | 2.5 | 70 | 5 | 51.27 | PASS | 100V_60Hz_HH_Tac_12V_12Vsb_Rise
237 | 180 | 47 | 128.7 | 2.5 | 70 | 5 | 51.28 | PASS | 180V_47Hz_HH_Tac_12V_12Vsb_Rise
267 | 200 | 50 | 145.1 | 2.5 | 70 | 5 | 51.26 | PASS | 200V_50Hz_HH_Tac_12V_12Vsb_Rise
298 | 220 | 50 | 161.5 | 2.5 | 70 | 5 | 51.25 | PASS | 220V_50Hz_HH_Tac_12V_12Vsb_Rise
337 | 264 | 63 | 1 | 0.1 | 70 | 5 | 51.29 | PASS | 264V_63Hz_LL_Tac_12V_12Vsb_Rise
363 | 264 | 63 | 161.5 | 2.5 | 70 | 5 | 51.26 | PASS | 264V_63Hz_HH_Tac_12V_12Vsb_Rise
405 | 164 | 30 | 1 | 0.1 | 70 | 5 | 51.26 | PASS | 164VDC_LL_Tac_12V_12Vsb_Rise
431 | 164 | 30 | 128.7 | 2.5 | 70 | 5 | 51.24 | PASS | 164VDC_HH_Tac_12V_12Vsb_Rise
451 | 200 | 30 | 145.1 | 2.5 | 70 | 5 | 51.28 | PASS | 200Vdc_HH_Tac_12V_12Vsb_Rise
471 | 220 | 30 | 161.5 | 2.5 | 70 | 5 | 51.24 | PASS | 220VDC_HH_Tac_12V_12Vsb_Rise
497 | 300 | 30 | 1 | 0.1 | 70 | 5 | 51.32 | PASS | 300VDC_LL_Tac_12V_12Vsb_Rise
524 | 300 | 30 | 161.5 | 2.5 | 70 | 5 | 51.23 | PASS | 300VDC_HH_Tac_12V_12Vsb_Rise
---------------------------------------
VsbRiseTime
SEQ | Vin | Fin | Main_Load(A) | Vsb_Load(A) | SPEC_Max | SPEC_Min | Value | Result | Ext
158 | 90 | 47 | 1 | 0.1 | 70 | 1 | 12.74 | PASS | 90V_47Hz_LL_Tac_12V_12Vsb_Rise
184 | 90 | 47 | 71.3 | 2.5 | 70 | 1 | 11.88 | PASS | 90V_47Hz_HH_Tac_12V_12Vsb_Rise
207 | 100 | 60 | 79.5 | 2.5 | 70 | 1 | 11.89 | PASS | 100V_60Hz_HH_Tac_12V_12Vsb_Rise
237 | 180 | 47 | 128.7 | 2.5 | 70 | 1 | 11.89 | PASS | 180V_47Hz_HH_Tac_12V_12Vsb_Rise
267 | 200 | 50 | 145.1 | 2.5 | 70 | 1 | 11.81 | PASS | 200V_50Hz_HH_Tac_12V_12Vsb_Rise
298 | 220 | 50 | 161.5 | 2.5 | 70 | 1 | 11.74 | PASS | 220V_50Hz_HH_Tac_12V_12Vsb_Rise
337 | 264 | 63 | 1 | 0.1 | 70 | 1 | 12.52 | PASS | 264V_63Hz_LL_Tac_12V_12Vsb_Rise
363 | 264 | 63 | 161.5 | 2.5 | 70 | 1 | 11.71 | PASS | 264V_63Hz_HH_Tac_12V_12Vsb_Rise
405 | 164 | 30 | 1 | 0.1 | 70 | 1 | 12.5 | PASS | 164VDC_LL_Tac_12V_12Vsb_Rise
431 | 164 | 30 | 128.7 | 2.5 | 70 | 1 | 11.7 | PASS | 164VDC_HH_Tac_12V_12Vsb_Rise
451 | 200 | 30 | 145.1 | 2.5 | 70 | 1 | 11.7 | PASS | 200Vdc_HH_Tac_12V_12Vsb_Rise
471 | 220 | 30 | 161.5 | 2.5 | 70 | 1 | 11.68 | PASS | 220VDC_HH_Tac_12V_12Vsb_Rise
497 | 300 | 30 | 1 | 0.1 | 70 | 1 | 12.51 | PASS | 300VDC_LL_Tac_12V_12Vsb_Rise
524 | 300 | 30 | 161.5 | 2.5 | 70 | 1 | 11.68 | PASS | 300VDC_HH_Tac_12V_12Vsb_Rise
---------------------------------------
PG_RiseTime
SEQ | Vin | Fin | Main_Load(A) | Vsb_Load(A) | SPEC_Max | SPEC_Min | Value | Result | Ext
158 | 90 | 47 | 1 | 0.1 | ******** | ******** | 0.06 | PASS | 90V_47Hz_LL_Tac_12V_12Vsb_Rise
184 | 90 | 47 | 71.3 | 2.5 | ******** | ******** | 0.06 | PASS | 90V_47Hz_HH_Tac_12V_12Vsb_Rise
207 | 100 | 60 | 79.5 | 2.5 | ******** | ******** | 0.06 | PASS | 100V_60Hz_HH_Tac_12V_12Vsb_Rise
237 | 180 | 47 | 128.7 | 2.5 | ******** | ******** | 0.06 | PASS | 180V_47Hz_HH_Tac_12V_12Vsb_Rise
267 | 200 | 50 | 145.1 | 2.5 | ******** | ******** | 0.06 | PASS | 200V_50Hz_HH_Tac_12V_12Vsb_Rise
298 | 220 | 50 | 161.5 | 2.5 | ******** | ******** | 0.06 | PASS | 220V_50Hz_HH_Tac_12V_12Vsb_Rise
337 | 264 | 63 | 1 | 0.1 | ******** | ******** | 0.06 | PASS | 264V_63Hz_LL_Tac_12V_12Vsb_Rise
363 | 264 | 63 | 161.5 | 2.5 | ******** | ******** | 0.06 | PASS | 264V_63Hz_HH_Tac_12V_12Vsb_Rise
405 | 164 | 30 | 1 | 0.1 | ******** | ******** | 0.06 | PASS | 164VDC_LL_Tac_12V_12Vsb_Rise
431 | 164 | 30 | 128.7 | 2.5 | ******** | ******** | 0.06 | PASS | 164VDC_HH_Tac_12V_12Vsb_Rise
451 | 200 | 30 | 145.1 | 2.5 | ******** | ******** | 0.06 | PASS | 200Vdc_HH_Tac_12V_12Vsb_Rise
471 | 220 | 30 | 161.5 | 2.5 | ******** | ******** | 0.06 | PASS | 220VDC_HH_Tac_12V_12Vsb_Rise
497 | 300 | 30 | 1 | 0.1 | ******** | ******** | 0.06 | PASS | 300VDC_LL_Tac_12V_12Vsb_Rise
524 | 300 | 30 | 161.5 | 2.5 | ******** | ******** | 0.06 | PASS | 300VDC_HH_Tac_12V_12Vsb_Rise

## HoldUp
---------------------------------------
Tvout Holdup CapLoad
SEQ | Vin | Fin | Main_Load(A) | Vsb_Load(A) | SPEC_Max | SPEC_Min | Value | Result | Ext
24 | 90 | 47 | 1 | 0.1 | 1000 | 10 | 64 | PASS | 90V_47Hz_LL
33 | 90 | 47 | 49.91 | 1.75 | 1000 | 10 | 36.76 | PASS | 90V_47Hz_70%
42 | 100 | 60 | 55.65 | 1.75 | 1000 | 10 | 33.43 | PASS | 100V_60Hz_70%
51 | 180 | 47 | 90.09 | 1.75 | 1000 | 10 | 26.83 | PASS | 180V_47Hz_70%
60 | 200 | 50 | 101.57 | 1.75 | 1000 | 10 | 24.15 | PASS | 200V_50Hz_70%
69 | 220 | 50 | 113.05 | 1.75 | 1000 | 10 | 21.75 | PASS | 220V_50Hz_70%
78 | 264 | 63 | 1 | 0.1 | 1000 | 10 | 64.28 | PASS | 264V_63Hz_LL
87 | 264 | 63 | 113.05 | 1.75 | 1000 | 10 | 22.15 | PASS | 264V_63Hz_70%
97 | 164 | 30 | 1 | 0.1 | 1000 | 10 | 64.69 | PASS | 164VDC_LL
106 | 164 | 30 | 90.09 | 1.75 | 1000 | 10 | 26.46 | PASS | 164VDC_70%
115 | 200 | 30 | 101.57 | 1.75 | 1000 | 10 | 24 | PASS | 200VDC_70%
123 | 220 | 30 | 113.05 | 1.75 | 1000 | 10 | 21.76 | PASS | 220VDC_70%
132 | 300 | 30 | 1 | 0.1 | 1000 | 10 | 64.78 | PASS | 300VDC_LL
141 | 300 | 30 | 113.05 | 1.75 | 1000 | 10 | 21.96 | PASS | 300VDC_70%
---------------------------------------
Vsb Holdup CapLoad
SEQ | Vin | Fin | Main_Load(A) | Vsb_Load(A) | SPEC_Max | SPEC_Min | Value | Result | Ext
24 | 90 | 47 | 1 | 0.1 | 1000 | 70 | 91.77 | PASS | 90V_47Hz_LL
33 | 90 | 47 | 49.91 | 1.75 | 1000 | 70 | 78.9 | PASS | 90V_47Hz_70%
42 | 100 | 60 | 55.65 | 1.75 | 1000 | 70 | 78.98 | PASS | 100V_60Hz_70%
51 | 180 | 47 | 90.09 | 1.75 | 1000 | 70 | 79.08 | PASS | 180V_47Hz_70%
60 | 200 | 50 | 101.57 | 1.75 | 1000 | 70 | 78.45 | PASS | 200V_50Hz_70%
69 | 220 | 50 | 113.05 | 1.75 | 1000 | 70 | 78.34 | PASS | 220V_50Hz_70%
78 | 264 | 63 | 1 | 0.1 | 1000 | 70 | 92.45 | PASS | 264V_63Hz_LL
87 | 264 | 63 | 113.05 | 1.75 | 1000 | 70 | 79.07 | PASS | 264V_63Hz_70%
97 | 164 | 30 | 1 | 0.1 | 1000 | 70 | 92.57 | PASS | 164VDC_LL
106 | 164 | 30 | 90.09 | 1.75 | 1000 | 70 | 78.3 | PASS | 164VDC_70%
115 | 200 | 30 | 101.57 | 1.75 | 1000 | 70 | 78.99 | PASS | 200VDC_70%
123 | 220 | 30 | 113.05 | 1.75 | 1000 | 70 | 78.54 | PASS | 220VDC_70%
132 | 300 | 30 | 1 | 0.1 | 1000 | 70 | 92.94 | PASS | 300VDC_LL
141 | 300 | 30 | 113.05 | 1.75 | 1000 | 70 | 78.92 | PASS | 300VDC_70%
---------------------------------------
Pwok Holdup CapLoad
SEQ | Vin | Fin | Main_Load(A) | Vsb_Load(A) | SPEC_Max | SPEC_Min | Value | Result | Ext
24 | 90 | 47 | 1 | 0.1 | 300 | 9 | 42.87 | PASS | 90V_47Hz_LL
33 | 90 | 47 | 49.91 | 1.75 | 300 | 9 | 34.85 | PASS | 90V_47Hz_70%
42 | 100 | 60 | 55.65 | 1.75 | 300 | 9 | 31.53 | PASS | 100V_60Hz_70%
51 | 180 | 47 | 90.09 | 1.75 | 300 | 9 | 25.04 | PASS | 180V_47Hz_70%
60 | 200 | 50 | 101.57 | 1.75 | 300 | 9 | 22.43 | PASS | 200V_50Hz_70%
69 | 220 | 50 | 113.05 | 1.75 | 300 | 9 | 20.12 | PASS | 220V_50Hz_70%
78 | 264 | 63 | 1 | 0.1 | 300 | 9 | 42.94 | PASS | 264V_63Hz_LL
87 | 264 | 63 | 113.05 | 1.75 | 300 | 9 | 20.43 | PASS | 264V_63Hz_70%
97 | 164 | 30 | 1 | 0.1 | 300 | 9 | 43.27 | PASS | 164VDC_LL
106 | 164 | 30 | 90.09 | 1.75 | 300 | 9 | 24.67 | PASS | 164VDC_70%
115 | 200 | 30 | 101.57 | 1.75 | 300 | 9 | 22.35 | PASS | 200VDC_70%
123 | 220 | 30 | 113.05 | 1.75 | 300 | 9 | 20.1 | PASS | 220VDC_70%
132 | 300 | 30 | 1 | 0.1 | 300 | 9 | 43.28 | PASS | 300VDC_LL
141 | 300 | 30 | 113.05 | 1.75 | 300 | 9 | 20.3 | PASS | 300VDC_70%
---------------------------------------
Vin Good Delay Timing CapLoad
SEQ | Vin | Fin | Main_Load(A) | Vsb_Load(A) | SPEC_Max | SPEC_Min | Value | Result | Ext
24 | 90 | 47 | 1 | 0.1 | 4 | 0.01 | 2.57 | PASS | 90V_47Hz_LL
33 | 90 | 47 | 49.91 | 1.75 | 4 | 0.01 | 2.74 | PASS | 90V_47Hz_70%
42 | 100 | 60 | 55.65 | 1.75 | 4 | 0.01 | 2.6 | PASS | 100V_60Hz_70%
51 | 180 | 47 | 90.09 | 1.75 | 4 | 0.01 | 2.89 | PASS | 180V_47Hz_70%
60 | 200 | 50 | 101.57 | 1.75 | 4 | 0.01 | 2.68 | PASS | 200V_50Hz_70%
69 | 220 | 50 | 113.05 | 1.75 | 4 | 0.01 | 2.76 | PASS | 220V_50Hz_70%
78 | 264 | 63 | 1 | 0.1 | 4 | 0.01 | 2.83 | PASS | 264V_63Hz_LL
87 | 264 | 63 | 113.05 | 1.75 | 4 | 0.01 | 2.67 | PASS | 264V_63Hz_70%
97 | 164 | 30 | 1 | 0.1 | 4 | 0.01 | 2.58 | PASS | 164VDC_LL
106 | 164 | 30 | 90.09 | 1.75 | 4 | 0.01 | 2.53 | PASS | 164VDC_70%
115 | 200 | 30 | 101.57 | 1.75 | 4 | 0.01 | 2.8 | PASS | 200VDC_70%
123 | 220 | 30 | 113.05 | 1.75 | 4 | 0.01 | 2.75 | PASS | 220VDC_70%
132 | 300 | 30 | 1 | 0.1 | 4 | 0.01 | 2.79 | PASS | 300VDC_LL
141 | 300 | 30 | 113.05 | 1.75 | 4 | 0.01 | 2.75 | PASS | 300VDC_70%
---------------------------------------
Tpwok OffValue CapLoad
SEQ | Vin | Fin | Main_Load(A) | Vsb_Load(A) | SPEC_Max | SPEC_Min | Value | Result | Ext
24 | 90 | 47 | 1 | 0.1 | 100 | 1 | 21.13 | PASS | 90V_47Hz_LL
33 | 90 | 47 | 49.91 | 1.75 | 100 | 1 | 1.91 | PASS | 90V_47Hz_70%
42 | 100 | 60 | 55.65 | 1.75 | 100 | 1 | 1.9 | PASS | 100V_60Hz_70%
51 | 180 | 47 | 90.09 | 1.75 | 100 | 1 | 1.79 | PASS | 180V_47Hz_70%
60 | 200 | 50 | 101.57 | 1.75 | 100 | 1 | 1.72 | PASS | 200V_50Hz_70%
69 | 220 | 50 | 113.05 | 1.75 | 100 | 1 | 1.63 | PASS | 220V_50Hz_70%
78 | 264 | 63 | 1 | 0.1 | 100 | 1 | 21.35 | PASS | 264V_63Hz_LL
87 | 264 | 63 | 113.05 | 1.75 | 100 | 1 | 1.72 | PASS | 264V_63Hz_70%
97 | 164 | 30 | 1 | 0.1 | 100 | 1 | 21.42 | PASS | 164VDC_LL
106 | 164 | 30 | 90.09 | 1.75 | 100 | 1 | 1.79 | PASS | 164VDC_70%
115 | 200 | 30 | 101.57 | 1.75 | 100 | 1 | 1.65 | PASS | 200VDC_70%
123 | 220 | 30 | 113.05 | 1.75 | 100 | 1 | 1.65 | PASS | 220VDC_70%
132 | 300 | 30 | 1 | 0.1 | 100 | 1 | 21.5 | PASS | 300VDC_LL
141 | 300 | 30 | 113.05 | 1.75 | 100 | 1 | 1.66 | PASS | 300VDC_70%
---------------------------------------
Tvout Holdup
SEQ | Vin | Fin | Main_Load(A) | Vsb_Load(A) | SPEC_Max | SPEC_Min | Value | Result | Ext
13 | 264 | 63 | 113.05 | 1.75 | 1000 | 10 | 21.96 | PASS | 264V_63Hz_70%
172 | 90 | 47 | 1 | 0.1 | 1000 | 10 | 47.91 | PASS | 90V_47Hz_LL
200 | 90 | 47 | 49.91 | 1.75 | 1000 | 10 | 36.42 | PASS | 90V_47Hz_70%
230 | 100 | 60 | 55.65 | 1.75 | 1000 | 10 | 33.23 | PASS | 100V_60Hz_70%
260 | 180 | 47 | 90.09 | 1.75 | 1000 | 10 | 26.69 | PASS | 180V_47Hz_70%
290 | 200 | 50 | 101.57 | 1.75 | 1000 | 10 | 23.93 | PASS | 200V_50Hz_70%
324 | 220 | 50 | 113.05 | 1.75 | 1000 | 10 | 21.76 | PASS | 220V_50Hz_70%
355 | 264 | 63 | 1 | 0.1 | 1000 | 10 | 48.37 | PASS | 264V_63Hz_LL
389 | 264 | 63 | 113.05 | 1.75 | 1000 | 10 | 21.8 | PASS | 264V_63Hz_70%
423 | 164 | 30 | 1 | 0.1 | 1000 | 10 | 48.13 | PASS | 164VDC_LL
444 | 164 | 30 | 90.09 | 1.75 | 1000 | 10 | 26.81 | PASS | 164VDC_70%
463 | 200 | 30 | 101.57 | 1.75 | 1000 | 10 | 24.11 | PASS | 200Vdc_70%
483 | 220 | 30 | 113.05 | 1.75 | 1000 | 10 | 21.93 | PASS | 220VDC_70%
515 | 300 | 30 | 1 | 0.1 | 1000 | 10 | 47.56 | PASS | 300VDC_LL
537 | 300 | 30 | 113.05 | 1.75 | 1000 | 10 | 21.78 | PASS | 300VDC_70%
---------------------------------------
Vsb Holdup
SEQ | Vin | Fin | Main_Load(A) | Vsb_Load(A) | SPEC_Max | SPEC_Min | Value | Result | Ext
13 | 264 | 63 | 113.05 | 1.75 | 1000 | 70 | 78.99 | PASS | 264V_63Hz_70%
172 | 90 | 47 | 1 | 0.1 | 1000 | 70 | 91.89 | PASS | 90V_47Hz_LL
200 | 90 | 47 | 49.91 | 1.75 | 1000 | 70 | 78.58 | PASS | 90V_47Hz_70%
230 | 100 | 60 | 55.65 | 1.75 | 1000 | 70 | 78.2 | PASS | 100V_60Hz_70%
260 | 180 | 47 | 90.09 | 1.75 | 1000 | 70 | 79.04 | PASS | 180V_47Hz_70%
290 | 200 | 50 | 101.57 | 1.75 | 1000 | 70 | 78.29 | PASS | 200V_50Hz_70%
324 | 220 | 50 | 113.05 | 1.75 | 1000 | 70 | 78.5 | PASS | 220V_50Hz_70%
355 | 264 | 63 | 1 | 0.1 | 1000 | 70 | 92.45 | PASS | 264V_63Hz_LL
389 | 264 | 63 | 113.05 | 1.75 | 1000 | 70 | 79.01 | PASS | 264V_63Hz_70%
423 | 164 | 30 | 1 | 0.1 | 1000 | 70 | 92.03 | PASS | 164VDC_LL
444 | 164 | 30 | 90.09 | 1.75 | 1000 | 70 | 78.98 | PASS | 164VDC_70%
463 | 200 | 30 | 101.57 | 1.75 | 1000 | 70 | 78.66 | PASS | 200Vdc_70%
483 | 220 | 30 | 113.05 | 1.75 | 1000 | 70 | 78.94 | PASS | 220VDC_70%
515 | 300 | 30 | 1 | 0.1 | 1000 | 70 | 92.14 | PASS | 300VDC_LL
537 | 300 | 30 | 113.05 | 1.75 | 1000 | 70 | 78.93 | PASS | 300VDC_70%
---------------------------------------
Pwok Holdup
SEQ | Vin | Fin | Main_Load(A) | Vsb_Load(A) | SPEC_Max | SPEC_Min | Value | Result | Ext
13 | 264 | 63 | 113.05 | 1.75 | 300 | 9 | 20.35 | PASS | 264V_63Hz_70%
172 | 90 | 47 | 1 | 0.1 | 300 | 9 | 43.39 | PASS | 90V_47Hz_LL
200 | 90 | 47 | 49.91 | 1.75 | 300 | 9 | 34.7 | PASS | 90V_47Hz_70%
230 | 100 | 60 | 55.65 | 1.75 | 300 | 9 | 31.55 | PASS | 100V_60Hz_70%
260 | 180 | 47 | 90.09 | 1.75 | 300 | 9 | 25.02 | PASS | 180V_47Hz_70%
290 | 200 | 50 | 101.57 | 1.75 | 300 | 9 | 22.28 | PASS | 200V_50Hz_70%
324 | 220 | 50 | 113.05 | 1.75 | 300 | 9 | 20.09 | PASS | 220V_50Hz_70%
355 | 264 | 63 | 1 | 0.1 | 300 | 9 | 43.66 | PASS | 264V_63Hz_LL
389 | 264 | 63 | 113.05 | 1.75 | 300 | 9 | 20.22 | PASS | 264V_63Hz_70%
423 | 164 | 30 | 1 | 0.1 | 300 | 9 | 43.48 | PASS | 164VDC_LL
444 | 164 | 30 | 90.09 | 1.75 | 300 | 9 | 25.14 | PASS | 164VDC_70%
463 | 200 | 30 | 101.57 | 1.75 | 300 | 9 | 22.43 | PASS | 200Vdc_70%
483 | 220 | 30 | 113.05 | 1.75 | 300 | 9 | 20.35 | PASS | 220VDC_70%
515 | 300 | 30 | 1 | 0.1 | 300 | 9 | 42.84 | PASS | 300VDC_LL
537 | 300 | 30 | 113.05 | 1.75 | 300 | 9 | 20.12 | PASS | 300VDC_70%
---------------------------------------
Vin Good Delay Timing
SEQ | Vin | Fin | Main_Load(A) | Vsb_Load(A) | SPEC_Max | SPEC_Min | Value | Result | Ext
13 | 264 | 63 | 113.05 | 1.75 | 4 | 0.01 | 2.78 | PASS | 264V_63Hz_70%
172 | 90 | 47 | 1 | 0.1 | 4 | 0.01 | 2.7 | PASS | 90V_47Hz_LL
200 | 90 | 47 | 49.91 | 1.75 | 4 | 0.01 | 2.77 | PASS | 90V_47Hz_70%
230 | 100 | 60 | 55.65 | 1.75 | 4 | 0.01 | 2.62 | PASS | 100V_60Hz_70%
260 | 180 | 47 | 90.09 | 1.75 | 4 | 0.01 | 2.68 | PASS | 180V_47Hz_70%
290 | 200 | 50 | 101.57 | 1.75 | 4 | 0.01 | 2.75 | PASS | 200V_50Hz_70%
324 | 220 | 50 | 113.05 | 1.75 | 4 | 0.01 | 2.74 | PASS | 220V_50Hz_70%
355 | 264 | 63 | 1 | 0.1 | 4 | 0.01 | 2.77 | PASS | 264V_63Hz_LL
389 | 264 | 63 | 113.05 | 1.75 | 4 | 0.01 | 2.87 | PASS | 264V_63Hz_70%
423 | 164 | 30 | 1 | 0.1 | 4 | 0.01 | 2.6 | PASS | 164VDC_LL
444 | 164 | 30 | 90.09 | 1.75 | 4 | 0.01 | 2.6 | PASS | 164VDC_70%
463 | 200 | 30 | 101.57 | 1.75 | 4 | 0.01 | 2.69 | PASS | 200Vdc_70%
483 | 220 | 30 | 113.05 | 1.75 | 4 | 0.01 | 2.8 | PASS | 220VDC_70%
515 | 300 | 30 | 1 | 0.1 | 4 | 0.01 | 2.78 | PASS | 300VDC_LL
537 | 300 | 30 | 113.05 | 1.75 | 4 | 0.01 | 2.77 | PASS | 300VDC_70%
---------------------------------------
Tpwok OffValue
SEQ | Vin | Fin | Main_Load(A) | Vsb_Load(A) | SPEC_Max | SPEC_Min | Value | Result | Ext
13 | 264 | 63 | 113.05 | 1.75 | 100 | 1 | 1.62 | PASS | 264V_63Hz_70%
172 | 90 | 47 | 1 | 0.1 | 100 | 1 | 4.52 | PASS | 90V_47Hz_LL
200 | 90 | 47 | 49.91 | 1.75 | 100 | 1 | 1.73 | PASS | 90V_47Hz_70%
230 | 100 | 60 | 55.65 | 1.75 | 100 | 1 | 1.68 | PASS | 100V_60Hz_70%
260 | 180 | 47 | 90.09 | 1.75 | 100 | 1 | 1.68 | PASS | 180V_47Hz_70%
290 | 200 | 50 | 101.57 | 1.75 | 100 | 1 | 1.65 | PASS | 200V_50Hz_70%
324 | 220 | 50 | 113.05 | 1.75 | 100 | 1 | 1.67 | PASS | 220V_50Hz_70%
355 | 264 | 63 | 1 | 0.1 | 300 | 1 | 4.71 | PASS | 264V_63Hz_LL
389 | 264 | 63 | 113.05 | 1.75 | 100 | 1 | 1.58 | PASS | 264V_63Hz_70%
423 | 164 | 30 | 1 | 0.1 | 100 | 1 | 4.65 | PASS | 164VDC_LL
444 | 164 | 30 | 90.09 | 1.75 | 100 | 1 | 1.67 | PASS | 164VDC_70%
463 | 200 | 30 | 101.57 | 1.75 | 100 | 1 | 1.68 | PASS | 200Vdc_70%
483 | 220 | 30 | 113.05 | 1.75 | 100 | 1 | 1.58 | PASS | 220VDC_70%
515 | 300 | 30 | 1 | 0.1 | 300 | 1 | 4.72 | PASS | 300VDC_LL
537 | 300 | 30 | 113.05 | 1.75 | 100 | 1 | 1.66 | PASS | 300VDC_70%

## PS_OFF
---------------------------------------
Tpson_pwok_CAP
SEQ | SPEC_Max | SPEC_Min | Value | Result | Ext
19 | 50 | 0.01 | 0.72 | PASS | 90V_47Hz_LL
28 | 50 | 0.01 | 0.78 | PASS | 90V_47Hz_HH
37 | 50 | 0.01 | 0.66 | PASS | 100V_60Hz_HH
46 | 50 | 0.01 | 0.77 | PASS | 180V_47Hz_HH
55 | 50 | 0.01 | 0.67 | PASS | 200V_50Hz_HH
64 | 50 | 0.01 | 0.71 | PASS | 220V_50Hz_HH
73 | 50 | 0.01 | 0.69 | PASS | 264V_63Hz_LL
82 | 50 | 0.01 | 0.7 | PASS | 264V_63Hz_HH
92 | 50 | 0.01 | 0.64 | PASS | 164VDC_LL
101 | 50 | 0.01 | 0.61 | PASS | 164VDC_HH
110 | 50 | 0.01 | 0.67 | PASS | 200VDC_HH
118 | 50 | 0.01 | 0.61 | PASS | 220VDC_HH
127 | 50 | 0.01 | 0.72 | PASS | 300VDC_LL
136 | 50 | 0.01 | 0.65 | PASS | 300VDC_HH
---------------------------------------
Tpwok_off_CAP
SEQ | SPEC_Max | SPEC_Min | Value | Result | Ext
19 | 100 | 1 | 21.19 | PASS | 90V_47Hz_LL
28 | 100 | 1 | 1.85 | PASS | 90V_47Hz_HH
37 | 100 | 1 | 1.82 | PASS | 100V_60Hz_HH
46 | 100 | 1 | 1.73 | PASS | 180V_47Hz_HH
55 | 100 | 1 | 1.71 | PASS | 200V_50Hz_HH
64 | 100 | 1 | 1.7 | PASS | 220V_50Hz_HH
73 | 100 | 1 | 21.52 | PASS | 264V_63Hz_LL
82 | 100 | 1 | 1.7 | PASS | 264V_63Hz_HH
92 | 100 | 1 | 21.63 | PASS | 164VDC_LL
101 | 100 | 1 | 1.73 | PASS | 164VDC_HH
110 | 100 | 1 | 1.71 | PASS | 200VDC_HH
118 | 100 | 1 | 1.7 | PASS | 220VDC_HH
127 | 100 | 1 | 21.72 | PASS | 300VDC_LL
136 | 100 | 1 | 1.7 | PASS | 300VDC_HH
---------------------------------------
Tpson_pwok
SEQ | SPEC_Max | SPEC_Min | Value | Result | Ext
149 | 50 | 0.01 | 0.81 | PASS
182 | 50 | 0.01 | 0.71 | PASS | 90V_47Hz_HH
205 | 50 | 0.01 | 0.64 | PASS | 100V_60Hz_HH
235 | 50 | 0.01 | 0.65 | PASS | 180V_47Hz_HH
265 | 50 | 0.01 | 0.77 | PASS | 200V_50Hz_HH
295 | 50 | 0.01 | 0.74 | PASS | 220V_50Hz_HH
328 | 50 | 0.01 | 0.67 | PASS | 264V_63Hz_LL
360 | 50 | 0.01 | 0.74 | PASS | 264V_63Hz_HH
395 | 50 | 0.01 | 0.62 | PASS | 164VDC_LL
428 | 50 | 0.01 | 0.66 | PASS | 164VDC_HH
449 | 50 | 0.01 | 0.62 | PASS | 200Vdc_HH
468 | 50 | 0.01 | 0.74 | PASS | 220VDC_HH
488 | 50 | 0.01 | 0.71 | PASS | 300VDC_LL
521 | 50 | 0.01 | 0.73 | PASS | 300VDC_HH
---------------------------------------
Tpwok_off
SEQ | SPEC_Max | SPEC_Min | Value | Result | Ext
149 | 100 | 1 | 4.64 | PASS
182 | 100 | 1 | 1.7 | PASS | 90V_47Hz_HH
205 | 100 | 1 | 1.69 | PASS | 100V_60Hz_HH
235 | 100 | 1 | 1.66 | PASS | 180V_47Hz_HH
265 | 100 | 1 | 1.65 | PASS | 200V_50Hz_HH
295 | 100 | 1 | 1.65 | PASS | 220V_50Hz_HH
328 | 100 | 1 | 4.93 | PASS | 264V_63Hz_LL
360 | 100 | 1 | 1.65 | PASS | 264V_63Hz_HH
395 | 100 | 1 | 4.86 | PASS | 164VDC_LL
428 | 100 | 1 | 1.66 | PASS | 164VDC_HH
449 | 100 | 1 | 1.65 | PASS | 200Vdc_HH
468 | 100 | 1 | 1.65 | PASS | 220VDC_HH
488 | 100 | 1 | 4.96 | PASS | 300VDC_LL
521 | 100 | 1 | 1.65 | PASS | 300VDC_HH

## PS_ON
---------------------------------------
Tpson_on_delay_CAP
SEQ | SPEC_Max | SPEC_Min | Value | Result | Ext
20 | 400 | 5 | 62.14 | PASS | 90V_47Hz_LL
29 | 400 | 5 | 62.33 | PASS | 90V_47Hz_HH
38 | 400 | 5 | 62.41 | PASS | 100V_60Hz_HH
47 | 400 | 5 | 62.64 | PASS | 180V_47Hz_HH
56 | 400 | 5 | 62.58 | PASS | 200V_50Hz_HH
65 | 400 | 5 | 62.76 | PASS | 220V_50Hz_HH
74 | 400 | 5 | 62.15 | PASS | 264V_63Hz_LL
83 | 400 | 5 | 62.65 | PASS | 264V_63Hz_HH
93 | 400 | 5 | 62.11 | PASS | 164VDC_LL
102 | 400 | 5 | 62.51 | PASS | 164VDC_HH
111 | 400 | 5 | 62.71 | PASS | 200VDC_HH
119 | 400 | 5 | 62.7 | PASS | 220VDC_HH
128 | 400 | 5 | 62.1 | PASS | 300VDC_LL
137 | 400 | 5 | 62.63 | PASS | 300VDC_HH
---------------------------------------
Tpwok_on_CAP
SEQ | SPEC_Max | SPEC_Min | Value | Result | Ext
20 | 500 | 100 | 206.051 | PASS | 90V_47Hz_LL
29 | 500 | 100 | 205.676 | PASS | 90V_47Hz_HH
38 | 500 | 100 | 205.75 | PASS | 100V_60Hz_HH
47 | 500 | 100 | 205.695 | PASS | 180V_47Hz_HH
56 | 500 | 100 | 205.561 | PASS | 200V_50Hz_HH
65 | 500 | 100 | 205.439 | PASS | 220V_50Hz_HH
74 | 500 | 100 | 205.97 | PASS | 264V_63Hz_LL
83 | 500 | 100 | 205.544 | PASS | 264V_63Hz_HH
93 | 500 | 100 | 205.895 | PASS | 164VDC_LL
102 | 500 | 100 | 205.614 | PASS | 164VDC_HH
111 | 500 | 100 | 205.611 | PASS | 200VDC_HH
119 | 500 | 100 | 205.497 | PASS | 220VDC_HH
128 | 500 | 100 | 205.895 | PASS | 300VDC_LL
137 | 500 | 100 | 205.465 | PASS | 300VDC_HH
---------------------------------------
Tpson_on_delay
SEQ | SPEC_Max | SPEC_Min | Value | Result | Ext
157 | 400 | 5 | 62.31 | PASS | 90V_47Hz_LL
183 | 400 | 5 | 62.24 | PASS | 90V_47Hz_HH
206 | 400 | 5 | 62.41 | PASS | 100V_60Hz_HH
236 | 400 | 5 | 62.48 | PASS | 180V_47Hz_HH
266 | 400 | 5 | 62.56 | PASS | 200V_50Hz_HH
297 | 400 | 5 | 62.72 | PASS | 220V_50Hz_HH
322 | ******** | ******** | 無值 | PASS | 220V-Fast OCW_SMBAlert
336 | 400 | 5 | 62.22 | PASS
362 | 400 | 5 | 62.58 | PASS | 264V_63Hz_HH
387 | ******** | ******** | 無值 | PASS | 264V-Fast OCW_SMBAlert
404 | 400 | 5 | 62.19 | PASS | 164VDC_LL
430 | 400 | 5 | 62.59 | PASS | 164VDC_HH
450 | 400 | 5 | 62.7 | PASS | 200Vdc_HH
470 | 400 | 5 | 62.79 | PASS | 220VDC_HH
496 | 400 | 5 | 62.18 | PASS | 300VDC_LL
523 | 400 | 5 | 62.72 | PASS | 300VDC_HH
---------------------------------------
Tpwok_on
SEQ | SPEC_Max | SPEC_Min | Value | Result | Ext
157 | 500 | 100 | 205.828 | PASS | 90V_47Hz_LL
183 | 500 | 100 | 205.744 | PASS | 90V_47Hz_HH
206 | 500 | 100 | 205.774 | PASS | 100V_60Hz_HH
236 | 500 | 100 | 205.636 | PASS | 180V_47Hz_HH
266 | 500 | 100 | 205.577 | PASS | 200V_50Hz_HH
297 | 500 | 100 | 205.457 | PASS | 220V_50Hz_HH
322 | ********* | ********* | 無值 | PASS | 220V-Fast OCW_SMBAlert
336 | 500 | 100 | 205.846 | PASS
362 | 500 | 100 | 205.462 | PASS | 264V_63Hz_HH
387 | ********* | ********* | 無值 | PASS | 264V-Fast OCW_SMBAlert
404 | 500 | 100 | 205.863 | PASS | 164VDC_LL
430 | 500 | 100 | 205.484 | PASS | 164VDC_HH
450 | 500 | 100 | 205.43 | PASS | 200Vdc_HH
470 | 500 | 100 | 205.435 | PASS | 220VDC_HH
496 | 500 | 100 | 205.844 | PASS | 300VDC_LL
523 | 500 | 100 | 205.491 | PASS | 300VDC_HH
---------------------------------------
Tpson_on_delay_Rise_CAP
SEQ | SPEC_Max | SPEC_Min | Value | Result | Ext
23 | 70 | 5 | 51.3 | PASS | 90V_47Hz_LL_Tpson_12V_Rise
32 | 70 | 5 | 51.29 | PASS | 90V_47Hz_HH_Tpson_12V_Rise
41 | 70 | 5 | 51.25 | PASS | 100V_60Hz_HH_Tpson_12V_Rise
50 | 70 | 5 | 51.27 | PASS | 180V_47Hz_HH_Tpson_12V_Rise
59 | 70 | 5 | 51.32 | PASS | 200V_50Hz_HH_Tpson_12V_Rise
68 | 70 | 5 | 51.3 | PASS | 220V_50Hz_HH_Tpson_12V_Rise
77 | 70 | 5 | 51.28 | PASS | 264V_63Hz_LL_Tpson_12V_Rise
86 | 70 | 5 | 51.29 | PASS | 264V_63Hz_HH_Tpson_12V_Rise
96 | 70 | 5 | 51.26 | PASS | 164VDC_LL_Tpson_12V_Rise
105 | 70 | 5 | 51.26 | PASS | 164VDC_HH_Tpson_12V_Rise
114 | 70 | 5 | 51.27 | PASS | 200VDC_HH_Tpson_12V_Rise
122 | 70 | 5 | 51.3 | PASS | 220VDC_HH_Tpson_12V_Rise
131 | 70 | 5 | 51.29 | PASS | 300VDC_LL_Tpson_12V_Rise
140 | 70 | 5 | 51.27 | PASS | 300VDC_HH_Tpson_12V_Rise
---------------------------------------
Tpwok_on_Rise_CAP
SEQ | SPEC_Max | SPEC_Min | Value | Result | Ext
23 | ********* | ********* | 0.12 | PASS | 90V_47Hz_LL_Tpson_12V_Rise
32 | ********* | ********* | 0.109 | PASS | 90V_47Hz_HH_Tpson_12V_Rise
41 | ********* | ********* | 0.124 | PASS | 100V_60Hz_HH_Tpson_12V_Rise
50 | ********* | ********* | 0.128 | PASS | 180V_47Hz_HH_Tpson_12V_Rise
59 | ********* | ********* | 0.13 | PASS | 200V_50Hz_HH_Tpson_12V_Rise
68 | ********* | ********* | 0.131 | PASS | 220V_50Hz_HH_Tpson_12V_Rise
77 | ********* | ********* | 0.136 | PASS | 264V_63Hz_LL_Tpson_12V_Rise
86 | ********* | ********* | 0.138 | PASS | 264V_63Hz_HH_Tpson_12V_Rise
96 | ********* | ********* | 0.141 | PASS | 164VDC_LL_Tpson_12V_Rise
105 | ********* | ********* | 0.141 | PASS | 164VDC_HH_Tpson_12V_Rise
114 | ********* | ********* | 0.134 | PASS | 200VDC_HH_Tpson_12V_Rise
122 | ********* | ********* | 0.147 | PASS | 220VDC_HH_Tpson_12V_Rise
131 | ********* | ********* | 0.13 | PASS | 300VDC_LL_Tpson_12V_Rise
140 | ********* | ********* | 0.145 | PASS | 300VDC_HH_Tpson_12V_Rise
---------------------------------------
Tpson_on_delay_Rise
SEQ | SPEC_Max | SPEC_Min | Value | Result | Ext
160 | 70 | 5 | 51.28 | PASS | 90V_47Hz_LL_Tpson_12V_Rise
186 | 70 | 5 | 51.25 | PASS | 90V_47Hz_HH_Tpson_12V_Rise
209 | 70 | 5 | 51.25 | PASS | 100V_60Hz_HH_Tpson_12V_Rise
239 | 70 | 5 | 51.27 | PASS | 180V_47Hz_HH_Tpson_12V_Rise
269 | 70 | 5 | 51.27 | PASS | 200V_50Hz_HH_Tpson_12V_Rise
300 | 70 | 5 | 51.25 | PASS | 220V_50Hz_HH_Tpson_12V_Rise
339 | 70 | 5 | 51.3 | PASS | 264V_63Hz_LL_Tpson_12V_Rise
365 | 70 | 5 | 51.26 | PASS | 264V_63Hz_HH_Tpson_12V_Rise
407 | 70 | 5 | 51.28 | PASS | 164VDC_LL_Tpson_12V_Rise
433 | 70 | 5 | 51.21 | PASS | 164VDC_HH_Tpson_12V_Rise
453 | 70 | 5 | 51.24 | PASS | 200Vdc_HH_Tpson_12V_Rise
473 | 70 | 5 | 51.23 | PASS | 220VDC_HH_Tpson_12V_Rise
499 | 70 | 5 | 51.26 | PASS | 300VDC_LL_Tpson_12V_Rise
526 | 70 | 5 | 51.26 | PASS | 300VDC_HH_Tpson_12V_Rise
---------------------------------------
Tpwok_on_Rise
SEQ | SPEC_Max | SPEC_Min | Value | Result | Ext
160 | ********* | ********* | 0.145 | PASS | 90V_47Hz_LL_Tpson_12V_Rise
186 | ********* | ********* | 0.145 | PASS | 90V_47Hz_HH_Tpson_12V_Rise
209 | ********* | ********* | 0.097 | PASS | 100V_60Hz_HH_Tpson_12V_Rise
239 | ********* | ********* | 0.142 | PASS | 180V_47Hz_HH_Tpson_12V_Rise
269 | ********* | ********* | 0.169 | PASS | 200V_50Hz_HH_Tpson_12V_Rise
300 | ********* | ********* | 0.164 | PASS | 220V_50Hz_HH_Tpson_12V_Rise
339 | ********* | ********* | 0.168 | PASS | 264V_63Hz_LL_Tpson_12V_Rise
365 | ********* | ********* | 0.047 | PASS | 264V_63Hz_HH_Tpson_12V_Rise
407 | ********* | ********* | 0.173 | PASS | 164VDC_LL_Tpson_12V_Rise
433 | ********* | ********* | 0.168 | PASS | 164VDC_HH_Tpson_12V_Rise
453 | ********* | ********* | 0.047 | PASS | 200Vdc_HH_Tpson_12V_Rise
473 | ********* | ********* | 0.052 | PASS | 220VDC_HH_Tpson_12V_Rise
499 | ********* | ********* | 0.171 | PASS | 300VDC_LL_Tpson_12V_Rise
526 | ********* | ********* | 0.049 | PASS | 300VDC_HH_Tpson_12V_Rise

## Eff_Noise
Input Output Eff Noise Multi or Single
SEQ | SPEC_Max | SPEC_Min | CH1_Value | SPEC_Max | SPEC_Min | CH2_Value | SPEC_Max | SPEC_Min | CH3_Value | SPEC_Max | SPEC_Min | CH4_Value | SPEC_Max | SPEC_Min | CH5_Value | SPEC_Max | SPEC_Min | CH6_Value | SPEC_Max | SPEC_Min | CH7_Value | Vin | Fin | Main_Load(A) | Vsb_Load(A) | Result | Ext
150 | 0.4 | ******* | 0.203 | 12.6 | 11.4 | 12.185 | 0.4 | ******* | 0.039 | 3.46 | 2.5 | 3.242 | 3.46 | 2.5 | 3.216 | ******* | ******* | 0.13 | 0.4 | ******* | 0.003 | 90 | 47 | 0 | 0 | PASS | 90V_47Hz_No Load
152 | 0.4 | ******* | 0.001 | 12.6 | 11.4 | 12.009 | 0.4 | ******* | 0.037 | 3.46 | 2.5 | 3.245 | 3.46 | 2.5 | 3.211 | ******* | ******* | 0.337 | 0.4 | ******* | 0.001 | 90 | 47 | 1 | 2.5 | PASS | 90V_47Hz_LH_Standby_2.5A
156 | 0.4 | ******* | 0 | 12.6 | 11.4 | 12.144 | 0.4 | ******* | 0.039 | 3.46 | 2.5 | 3.24 | 3.46 | 2.5 | 3.219 | ******* | ******* | 0.308 | 0.4 | ******* | 0.003 | 90 | 47 | 1 | 0.1 | PASS | 90V_47Hz_LL_Standby_0.1A
161 | 12.81 | 11.59 | 12.258 | 12.6 | 11.4 | 12.186 | 3.46 | 2.5 | 3.248 | 3.46 | 2.5 | 3.244 | 3.46 | 2.5 | 3.217 | 0.3 | -0.3 | 0.017 | 0.4 | ******* | 0.003 | 90 | 47 | 0 | 0 | PASS | 90V_47Hz_No Load
166 | 12.81 | 11.59 | 12.259 | 12.6 | 11.4 | 12.142 | 3.46 | 2.5 | 3.245 | 3.46 | 2.5 | 3.249 | 3.46 | 2.5 | 3.215 | ******* | ******* | 0.06 | 0.4 | ******* | 0.003 | 90 | 47 | 1 | 0.1 | PASS | 90V_47Hz_LL
167 | 12.81 | 11.59 | 12.259 | 12.6 | 11.4 | 12.01 | 3.46 | 2.5 | 3.243 | 3.46 | 2.5 | 3.247 | 3.46 | 2.5 | 3.216 | ******* | ******* | 0.06 | 0.4 | ******* | 0.001 | 90 | 47 | 1 | 2.5 | PASS | 90V_47Hz_LH
187 | 12.81 | 11.59 | 12.22 | 12.6 | 11.4 | 12.133 | 3.46 | 2.5 | 3.241 | 3.46 | 2.5 | 3.241 | 3.46 | 2.5 | 3.218 | ******* | ******* | 3.53 | 0.4 | ******* | -0.007 | 90 | 47 | 71.3 | 0.1 | PASS | 90V_47Hz_HL
192 | 12.81 | 11.59 | 12.219 | 12.6 | 11.4 | 12.006 | 3.46 | 2.5 | 3.235 | 3.46 | 2.5 | 3.238 | 3.46 | 2.5 | 3.222 | ******* | ******* | 3.53 | 0.4 | ******* | -0.009 | 90 | 47 | 71.3 | 2.5 | PASS | 90V_47Hz_HH
210 | 12.81 | 11.59 | 12.21 | 12.6 | 11.4 | 12.132 | 3.46 | 2.5 | 3.24 | 3.46 | 2.5 | 3.234 | 3.46 | 2.5 | 3.22 | ******* | ******* | 3.933 | 0.4 | ******* | -0.009 | 100 | 60 | 79.5 | 0.1 | PASS | 100V_60Hz_HL
218 | 12.81 | 11.59 | 12.214 | 12.6 | 11.4 | 12.005 | 3.46 | 2.5 | 3.232 | 3.46 | 2.5 | 3.236 | 3.46 | 2.5 | 3.221 | ******* | ******* | 3.934 | 0.4 | ******* | -0.01 | 100 | 60 | 79.5 | 2.5 | PASS | HH
240 | 12.81 | 11.59 | 12.179 | 12.6 | 11.4 | 12.128 | 3.46 | 2.5 | 3.233 | 3.46 | 2.5 | 3.232 | 3.46 | 2.5 | 3.218 | ******* | ******* | 6.357 | 0.4 | ******* | -0.016 | 180 | 47 | 128.7 | 0.1 | PASS | 180V_47Hz_HL
248 | 12.81 | 11.59 | 12.182 | 12.6 | 11.4 | 12 | 3.46 | 2.5 | 3.229 | 3.46 | 2.5 | 3.225 | 3.46 | 2.5 | 3.226 | ******* | ******* | 6.359 | 0.4 | ******* | -0.017 | 180 | 47 | 128.7 | 2.5 | PASS | 180V_47Hz_HH
270 | 12.81 | 11.59 | 12.173 | 12.6 | 11.4 | 12.126 | 3.46 | 2.5 | 3.23 | 3.46 | 2.5 | 3.224 | 3.46 | 2.5 | 3.225 | ******* | ******* | 7.176 | 0.4 | ******* | -0.018 | 200 | 50 | 145.1 | 0.1 | PASS | 200V_50Hz_HL
278 | 12.81 | 11.59 | 12.176 | 12.6 | 11.4 | 11.996 | 3.46 | 2.5 | 3.223 | 3.46 | 2.5 | 3.228 | 3.46 | 2.5 | 3.219 | ******* | ******* | 7.176 | 0.4 | ******* | -0.02 | 200 | 50 | 145.1 | 2.5 | PASS | 200V_50Hz_HH
301 | 12.81 | 11.59 | 12.164 | 12.6 | 11.4 | 12.12 | 3.46 | 2.5 | 3.228 | 3.46 | 2.5 | 3.222 | 3.46 | 2.5 | 3.223 | ******* | ******* | 8.002 | 0.4 | ******* | -0.02 | 220 | 50 | 161.5 | 0.1 | PASS | 220V_50Hz_HL
309 | 12.81 | 11.59 | 12.163 | 12.6 | 11.4 | 11.995 | 3.46 | 2.5 | 3.222 | 3.46 | 2.5 | 3.226 | 3.46 | 2.5 | 3.224 | ******* | ******* | 8.002 | 0.4 | ******* | -0.022 | 220 | 50 | 161.5 | 2.5 | PASS | 220V_50Hz_HH
330 | 0.4 | ******* | 0.147 | 12.6 | 11.4 | 12.19 | 0.4 | ******* | 0.039 | 3.46 | 2.5 | 3.242 | 3.46 | 2.5 | 3.219 | ******* | ******* | 0.131 | 0.4 | ******* | 0.003 | 264 | 63 | 0 | 0 | PASS | 264V_63Hz_No Load
331 | 0.4 | ******* | 0.001 | 12.6 | 11.4 | 12.011 | 0.4 | ******* | 0.037 | 3.46 | 2.5 | 3.247 | 3.46 | 2.5 | 3.212 | ******* | ******* | 0.325 | 0.4 | ******* | 0.001 | 264 | 63 | 1 | 2.5 | PASS | 264V_63Hz_Standby_2.5A
335 | 0.4 | ******* | 0 | 12.6 | 11.4 | 12.148 | 0.4 | ******* | 0.039 | 3.46 | 2.5 | 3.245 | 3.46 | 2.5 | 3.214 | ******* | ******* | 0.343 | 0.4 | ******* | 0.003 | 264 | 63 | 1 | 0.1 | PASS | 264V_63Hz_LL_Standby_0.1A
340 | 12.81 | 11.59 | 12.259 | 12.6 | 11.4 | 12.191 | 3.46 | 2.5 | 3.244 | 3.46 | 2.5 | 3.245 | 3.46 | 2.5 | 3.218 | 0.3 | -0.3 | 0.017 | 0.4 | ******* | 0.003 | 264 | 63 | 0 | 0 | PASS | No Load
344 | 12.81 | 11.59 | 12.26 | 12.6 | 11.4 | 12.145 | 3.46 | 2.5 | 3.245 | 3.46 | 2.5 | 3.248 | 3.46 | 2.5 | 3.217 | ******* | ******* | 0.059 | 0.4 | ******* | 0.003 | 264 | 63 | 1 | 0.1 | PASS | 264V_63Hz_LL
345 | 12.81 | 11.59 | 12.26 | 12.6 | 11.4 | 12.013 | 3.46 | 2.5 | 3.243 | 3.46 | 2.5 | 3.25 | 3.46 | 2.5 | 3.213 | ******* | ******* | 0.058 | 0.4 | ******* | 0.001 | 264 | 63 | 1 | 2.5 | PASS | 264V_63Hz_LH
366 | 12.81 | 11.59 | 12.165 | 12.6 | 11.4 | 12.121 | 3.46 | 2.5 | 3.226 | 3.46 | 2.5 | 3.228 | 3.46 | 2.5 | 3.22 | ******* | ******* | 7.999 | 0.4 | ******* | -0.02 | 264 | 63 | 161.5 | 0.1 | PASS | 264V_63Hz_HL
374 | 12.81 | 11.59 | 12.166 | 12.6 | 11.4 | 11.994 | 3.46 | 2.5 | 3.227 | 3.46 | 2.5 | 3.221 | 3.46 | 2.5 | 3.226 | ******* | ******* | 8.004 | 0.4 | ******* | -0.022 | 264 | 63 | 161.5 | 2.5 | PASS | HH
398 | 0.4 | ******* | 0.143 | 12.6 | 11.4 | 12.19 | 0.4 | ******* | 0.039 | 3.46 | 2.5 | 3.242 | 3.46 | 2.5 | 3.219 | ******* | ******* | 0.137 | 0.4 | ******* | 0.003 | 164 | 30 | 0 | 0 | PASS | 164VDC_No Load
399 | 0.4 | ******* | 0.001 | 12.6 | 11.4 | 12.011 | 0.4 | ******* | 0.037 | 3.46 | 2.5 | 3.244 | 3.46 | 2.5 | 3.214 | ******* | ******* | 0.337 | 0.4 | ******* | 0.001 | 164 | 30 | 1 | 2.5 | PASS | 164Vdc_Standby_2.5A
403 | 0.4 | ******* | 0 | 12.6 | 11.4 | 12.148 | 0.4 | ******* | 0.039 | 3.46 | 2.5 | 3.241 | 3.46 | 2.5 | 3.219 | ******* | ******* | 0.293 | 0.4 | ******* | 0.003 | 164 | 30 | 1 | 0.1 | PASS | 164VDC_LL_Standby_0.1A
413 | 12.81 | 11.59 | 12.246 | 12.6 | 11.4 | 12.192 | 3.46 | 2.5 | 3.25 | 3.46 | 2.5 | 3.25 | 3.46 | 2.5 | 3.211 | 0.3 | -0.3 | 0.017 | 0.4 | ******* | 0.003 | 164 | 30 | 0 | 0 | PASS | No Load
417 | 12.81 | 11.59 | 12.259 | 12.6 | 11.4 | 12.145 | 3.46 | 2.5 | 3.25 | 3.46 | 2.5 | 3.244 | 3.46 | 2.5 | 3.219 | ******* | ******* | 0.062 | 0.4 | ******* | 0.003 | 164 | 30 | 1 | 0.1 | PASS | 164VDC_LL
418 | 12.81 | 11.59 | 12.259 | 12.6 | 11.4 | 12.013 | 3.46 | 2.5 | 3.248 | 3.46 | 2.5 | 3.243 | 3.46 | 2.5 | 3.22 | ******* | ******* | 0.06 | 0.4 | ******* | 0.002 | 164 | 30 | 1 | 2.5 | PASS | 164VDC_LH
434 | 12.81 | 11.59 | 12.225 | 12.6 | 11.4 | 12.045 | 3.46 | 2.5 | 3.239 | 3.46 | 2.5 | 3.24 | 3.46 | 2.5 | 3.216 | ******* | ******* | 3.191 | 0.4 | ******* | -0.007 | 164 | 30 | 64.35 | 1.25 | PASS | 164VDC_50%_L
435 | 12.81 | 11.59 | 12.186 | 12.6 | 11.4 | 11.996 | 3.46 | 2.5 | 3.225 | 3.46 | 2.5 | 3.231 | 3.46 | 2.5 | 3.22 | ******* | ******* | 6.355 | 0.4 | ******* | -0.017 | 164 | 30 | 128.7 | 2.5 | PASS | 164VDC_HH
443 | 12.81 | 11.59 | 12.187 | 12.6 | 11.4 | 12.128 | 3.46 | 2.5 | 3.23 | 3.46 | 2.5 | 3.228 | 3.46 | 2.5 | 3.226 | ******* | ******* | 6.36 | 0.4 | ******* | -0.015 | 164 | 30 | 128.7 | 0.1 | PASS | 164VDC_HL
454 | 12.81 | 11.59 | 12.174 | 12.6 | 11.4 | 12.127 | 3.46 | 2.5 | 3.225 | 3.46 | 2.5 | 3.231 | 3.46 | 2.5 | 3.22 | ******* | ******* | 7.175 | 0.4 | ******* | -0.018 | 200 | 30 | 145.1 | 0.1 | PASS | 200Vdc_HL
462 | 12.81 | 11.59 | 12.177 | 12.6 | 11.4 | 11.996 | 3.46 | 2.5 | 3.227 | 3.46 | 2.5 | 3.223 | 3.46 | 2.5 | 3.228 | ******* | ******* | 7.177 | 0.4 | ******* | -0.019 | 200 | 30 | 145.1 | 2.5 | PASS | 200Vdc_HH
474 | 12.81 | 11.59 | 12.167 | 12.6 | 11.4 | 12.125 | 3.46 | 2.5 | 3.228 | 3.46 | 2.5 | 3.223 | 3.46 | 2.5 | 3.224 | ******* | ******* | 8.001 | 0.4 | ******* | -0.02 | 220 | 30 | 161.5 | 0.1 | PASS | 220VDC_HL
482 | 12.81 | 11.59 | 12.167 | 12.6 | 11.4 | 11.994 | 3.46 | 2.5 | 3.225 | 3.46 | 2.5 | 3.222 | 3.46 | 2.5 | 3.224 | ******* | ******* | 8.003 | 0.4 | ******* | -0.022 | 220 | 30 | 161.5 | 2.5 | PASS | 220VDC_HH
490 | 0.4 | ******* | 0.152 | 12.6 | 11.4 | 12.189 | 0.4 | ******* | 0.038 | 3.46 | 2.5 | 3.247 | 3.46 | 2.5 | 3.212 | ******* | ******* | 0.164 | 0.4 | ******* | 0.003 | 300 | 30 | 0 | 0 | PASS | No Load
491 | 0.4 | ******* | 0.001 | 12.6 | 11.4 | 12.013 | 0.4 | ******* | 0.037 | 3.46 | 2.5 | 3.24 | 3.46 | 2.5 | 3.219 | ******* | ******* | 0.299 | 0.4 | ******* | 0.001 | 300 | 30 | 1 | 2.5 | PASS | 300Vdc_Standby_2.5A
495 | 0.4 | ******* | 0 | 12.6 | 11.4 | 12.145 | 0.4 | ******* | 0.039 | 3.46 | 2.5 | 3.242 | 3.46 | 2.5 | 3.218 | ******* | ******* | 0.313 | 0.4 | ******* | 0.003 | 300 | 30 | 1 | 0.1 | PASS | 300Vdc_Standby_0.1A
505 | 12.81 | 11.59 | 12.259 | 12.6 | 11.4 | 12.191 | 3.46 | 2.5 | 3.248 | 3.46 | 2.5 | 3.244 | 3.46 | 2.5 | 3.218 | 0.3 | -0.3 | 0.017 | 0.4 | ******* | 0.003 | 300 | 30 | 0 | 0 | PASS | No Load
509 | 12.81 | 11.59 | 12.26 | 12.6 | 11.4 | 12.142 | 3.46 | 2.5 | 3.247 | 3.46 | 2.5 | 3.246 | 3.46 | 2.5 | 3.218 | ******* | ******* | 0.062 | 0.4 | ******* | 0.003 | 300 | 30 | 1 | 0.1 | PASS | 300VDC_LL
510 | 12.81 | 11.59 | 12.261 | 12.6 | 11.4 | 12.014 | 3.46 | 2.5 | 3.248 | 3.46 | 2.5 | 3.244 | 3.46 | 2.5 | 3.219 | ******* | ******* | 0.061 | 0.4 | ******* | 0.002 | 300 | 30 | 1 | 2.5 | PASS | 300VDC_LH
527 | 12.81 | 11.59 | 12.216 | 12.6 | 11.4 | 12.044 | 3.46 | 2.5 | 3.233 | 3.46 | 2.5 | 3.238 | 3.46 | 2.5 | 3.219 | ******* | ******* | 3.996 | 0.4 | ******* | -0.009 | 300 | 30 | 80.75 | 1.25 | PASS | 300VDC_50%_L
528 | 12.81 | 11.59 | 12.167 | 12.6 | 11.4 | 12.121 | 3.46 | 2.5 | 3.228 | 3.46 | 2.5 | 3.224 | 3.46 | 2.5 | 3.223 | ******* | ******* | 8.002 | 0.4 | ******* | -0.02 | 300 | 30 | 161.5 | 0.1 | PASS | 300VDC_HL
533 | 12.81 | 11.59 | 12.166 | 12.6 | 11.4 | 11.994 | 3.46 | 2.5 | 3.22 | 3.46 | 2.5 | 3.225 | 3.46 | 2.5 | 3.225 | ******* | ******* | 8.003 | 0.4 | ******* | -0.022 | 300 | 30 | 161.5 | 2.5 | PASS | 300VDC_HH
---------------------------------------
Eff_Noise_Ripple_Main
SEQ | Vin | Fin | Main_Load(A) | Vsb_Load(A) | SPEC_Max | SPEC_Min | Value | Result | Ext
150 | 90 | 47 | 0 | 0 | 120 | 0 | 0.18 | PASS | 90V_47Hz_No Load
152 | 90 | 47 | 1 | 2.5 | 120 | 0 | 0 | PASS | 90V_47Hz_LH_Standby_2.5A
156 | 90 | 47 | 1 | 0.1 | 120 | 0 | 0 | PASS | 90V_47Hz_LL_Standby_0.1A
161 | 90 | 47 | 0 | 0 | 120 | 0 | 8.33 | PASS | 90V_47Hz_No Load
166 | 90 | 47 | 1 | 0.1 | 120 | 0 | 10.61 | PASS | 90V_47Hz_LL
167 | 90 | 47 | 1 | 2.5 | 120 | 0 | 7.15 | PASS | 90V_47Hz_LH
187 | 90 | 47 | 71.3 | 0.1 | 120 | 0 | 12.69 | PASS | 90V_47Hz_HL
192 | 90 | 47 | 71.3 | 2.5 | 120 | 0 | 11.11 | PASS | 90V_47Hz_HH
210 | 100 | 60 | 79.5 | 0.1 | 120 | 0 | 12.39 | PASS | 100V_60Hz_HL
218 | 100 | 60 | 79.5 | 2.5 | 120 | 0 | 12.53 | PASS | HH
240 | 180 | 47 | 128.7 | 0.1 | 120 | 0 | 15 | PASS | 180V_47Hz_HL
248 | 180 | 47 | 128.7 | 2.5 | 120 | 0 | 13.43 | PASS | 180V_47Hz_HH
270 | 200 | 50 | 145.1 | 0.1 | 120 | 0 | 14.86 | PASS | 200V_50Hz_HL
278 | 200 | 50 | 145.1 | 2.5 | 120 | 0 | 13.69 | PASS | 200V_50Hz_HH
301 | 220 | 50 | 161.5 | 0.1 | 120 | 0 | 15.6 | PASS | 220V_50Hz_HL
309 | 220 | 50 | 161.5 | 2.5 | 120 | 0 | 14.91 | PASS | 220V_50Hz_HH
330 | 264 | 63 | 0 | 0 | 120 | 0 | 1.15 | PASS | 264V_63Hz_No Load
331 | 264 | 63 | 1 | 2.5 | 120 | 0 | 0.23 | PASS | 264V_63Hz_Standby_2.5A
335 | 264 | 63 | 1 | 0.1 | 120 | 0 | 0.21 | PASS | 264V_63Hz_LL_Standby_0.1A
340 | 264 | 63 | 0 | 0 | 120 | 0 | 8.33 | PASS | No Load
344 | 264 | 63 | 1 | 0.1 | 120 | 0 | 9.86 | PASS | 264V_63Hz_LL
345 | 264 | 63 | 1 | 2.5 | 120 | 0 | 7.87 | PASS | 264V_63Hz_LH
366 | 264 | 63 | 161.5 | 0.1 | 120 | 0 | 16.05 | PASS | 264V_63Hz_HL
374 | 264 | 63 | 161.5 | 2.5 | 120 | 0 | 15.35 | PASS | HH
398 | 164 | 30 | 0 | 0 | 120 | 0 | 1.1 | PASS | 164VDC_No Load
399 | 164 | 30 | 1 | 2.5 | 120 | 0 | 0.23 | PASS | 164Vdc_Standby_2.5A
403 | 164 | 30 | 1 | 0.1 | 120 | 0 | 0.1 | PASS | 164VDC_LL_Standby_0.1A
413 | 164 | 30 | 0 | 0 | 120 | 0 | 8.83 | PASS | No Load
417 | 164 | 30 | 1 | 0.1 | 120 | 0 | 7.95 | PASS | 164VDC_LL
418 | 164 | 30 | 1 | 2.5 | 120 | 0 | 6.99 | PASS | 164VDC_LH
434 | 164 | 30 | 64.35 | 1.25 | 120 | 0 | 12.03 | PASS | 164VDC_50%_L
435 | 164 | 30 | 128.7 | 2.5 | 120 | 0 | 12.62 | PASS | 164VDC_HH
443 | 164 | 30 | 128.7 | 0.1 | 120 | 0 | 13.95 | PASS | 164VDC_HL
454 | 200 | 30 | 145.1 | 0.1 | 120 | 0 | 15.54 | PASS | 200Vdc_HL
462 | 200 | 30 | 145.1 | 2.5 | 120 | 0 | 14.02 | PASS | 200Vdc_HH
474 | 220 | 30 | 161.5 | 0.1 | 120 | 0 | 15.7 | PASS | 220VDC_HL
482 | 220 | 30 | 161.5 | 2.5 | 120 | 0 | 14.4 | PASS | 220VDC_HH
490 | 300 | 30 | 0 | 0 | 120 | 0 | 0.89 | PASS | No Load
491 | 300 | 30 | 1 | 2.5 | 120 | 0 | 0.04 | PASS | 300Vdc_Standby_2.5A
495 | 300 | 30 | 1 | 0.1 | 120 | 0 | 0.03 | PASS | 300Vdc_Standby_0.1A
505 | 300 | 30 | 0 | 0 | 120 | 0 | 9.27 | PASS | No Load
509 | 300 | 30 | 1 | 0.1 | 120 | 0 | 8.7 | PASS | 300VDC_LL
510 | 300 | 30 | 1 | 2.5 | 120 | 0 | 5.69 | PASS | 300VDC_LH
527 | 300 | 30 | 80.75 | 1.25 | 120 | 0 | 12.22 | PASS | 300VDC_50%_L
528 | 300 | 30 | 161.5 | 0.1 | 120 | 0 | 14.72 | PASS | 300VDC_HL
533 | 300 | 30 | 161.5 | 2.5 | 120 | 0 | 14.04 | PASS | 300VDC_HH
---------------------------------------
Eff_Noise_Ripple_CH2
SEQ | Vin | Fin | Main_Load(A) | Vsb_Load(A) | SPEC_Max | SPEC_Min | Value | Result | Ext
150 | 90 | 47 | 0 | 0 | 120 | 0 | 4.69 | PASS | 90V_47Hz_No Load
152 | 90 | 47 | 1 | 2.5 | 120 | 0 | 1.92 | PASS | 90V_47Hz_LH_Standby_2.5A
156 | 90 | 47 | 1 | 0.1 | 120 | 0 | 7.82 | PASS | 90V_47Hz_LL_Standby_0.1A
161 | 90 | 47 | 0 | 0 | 120 | 0 | 4.38 | PASS | 90V_47Hz_No Load
166 | 90 | 47 | 1 | 0.1 | 120 | 0 | 7.3 | PASS | 90V_47Hz_LL
167 | 90 | 47 | 1 | 2.5 | 120 | 0 | 2.16 | PASS | 90V_47Hz_LH
187 | 90 | 47 | 71.3 | 0.1 | 120 | 0 | 6.45 | PASS | 90V_47Hz_HL
192 | 90 | 47 | 71.3 | 2.5 | 120 | 0 | 13.9 | PASS | 90V_47Hz_HH
210 | 100 | 60 | 79.5 | 0.1 | 120 | 0 | 6.69 | PASS | 100V_60Hz_HL
218 | 100 | 60 | 79.5 | 2.5 | 120 | 0 | 14.02 | PASS | HH
240 | 180 | 47 | 128.7 | 0.1 | 120 | 0 | 7.22 | PASS | 180V_47Hz_HL
248 | 180 | 47 | 128.7 | 2.5 | 120 | 0 | 14.9 | PASS | 180V_47Hz_HH
270 | 200 | 50 | 145.1 | 0.1 | 120 | 0 | 7.26 | PASS | 200V_50Hz_HL
278 | 200 | 50 | 145.1 | 2.5 | 120 | 0 | 15.12 | PASS | 200V_50Hz_HH
301 | 220 | 50 | 161.5 | 0.1 | 120 | 0 | 7.75 | PASS | 220V_50Hz_HL
309 | 220 | 50 | 161.5 | 2.5 | 120 | 0 | 15.18 | PASS | 220V_50Hz_HH
330 | 264 | 63 | 0 | 0 | 120 | 0 | 5.82 | PASS | 264V_63Hz_No Load
331 | 264 | 63 | 1 | 2.5 | 120 | 0 | 2.53 | PASS | 264V_63Hz_Standby_2.5A
335 | 264 | 63 | 1 | 0.1 | 120 | 0 | 8.47 | PASS | 264V_63Hz_LL_Standby_0.1A
340 | 264 | 63 | 0 | 0 | 120 | 0 | 6.13 | PASS | No Load
344 | 264 | 63 | 1 | 0.1 | 120 | 0 | 7.99 | PASS | 264V_63Hz_LL
345 | 264 | 63 | 1 | 2.5 | 120 | 0 | 3.19 | PASS | 264V_63Hz_LH
366 | 264 | 63 | 161.5 | 0.1 | 120 | 0 | 7.28 | PASS | 264V_63Hz_HL
374 | 264 | 63 | 161.5 | 2.5 | 120 | 0 | 15.03 | PASS | HH
398 | 164 | 30 | 0 | 0 | 120 | 0 | 5.45 | PASS | 164VDC_No Load
399 | 164 | 30 | 1 | 2.5 | 120 | 0 | 2.43 | PASS | 164Vdc_Standby_2.5A
403 | 164 | 30 | 1 | 0.1 | 120 | 0 | 8.29 | PASS | 164VDC_LL_Standby_0.1A
413 | 164 | 30 | 0 | 0 | 120 | 0 | 5.47 | PASS | No Load
417 | 164 | 30 | 1 | 0.1 | 120 | 0 | 7.54 | PASS | 164VDC_LL
418 | 164 | 30 | 1 | 2.5 | 120 | 0 | 2.97 | PASS | 164VDC_LH
434 | 164 | 30 | 64.35 | 1.25 | 120 | 0 | 11.41 | PASS | 164VDC_50%_L
435 | 164 | 30 | 128.7 | 2.5 | 120 | 0 | 14.78 | PASS | 164VDC_HH
443 | 164 | 30 | 128.7 | 0.1 | 120 | 0 | 6.21 | PASS | 164VDC_HL
454 | 200 | 30 | 145.1 | 0.1 | 120 | 0 | 7.11 | PASS | 200Vdc_HL
462 | 200 | 30 | 145.1 | 2.5 | 120 | 0 | 14.59 | PASS | 200Vdc_HH
474 | 220 | 30 | 161.5 | 0.1 | 120 | 0 | 7.39 | PASS | 220VDC_HL
482 | 220 | 30 | 161.5 | 2.5 | 120 | 0 | 14.99 | PASS | 220VDC_HH
490 | 300 | 30 | 0 | 0 | 120 | 0 | 5.14 | PASS | No Load
491 | 300 | 30 | 1 | 2.5 | 120 | 0 | 2.25 | PASS | 300Vdc_Standby_2.5A
495 | 300 | 30 | 1 | 0.1 | 120 | 0 | 8.23 | PASS | 300Vdc_Standby_0.1A
505 | 300 | 30 | 0 | 0 | 120 | 0 | 5.74 | PASS | No Load
509 | 300 | 30 | 1 | 0.1 | 120 | 0 | 7.79 | PASS | 300VDC_LL
510 | 300 | 30 | 1 | 2.5 | 120 | 0 | 2.93 | PASS | 300VDC_LH
527 | 300 | 30 | 80.75 | 1.25 | 120 | 0 | 9.06 | PASS | 300VDC_50%_L
528 | 300 | 30 | 161.5 | 0.1 | 120 | 0 | 6.18 | PASS | 300VDC_HL
533 | 300 | 30 | 161.5 | 2.5 | 120 | 0 | 15.35 | PASS | 300VDC_HH
---------------------------------------
Vrms
SEQ | Vin | Fin | Main_Load(A) | Vsb_Load(A) | SPEC_Max | SPEC_Min | Value | Result | Ext
150 | 90 | 47 | 0 | 0 | ******** | ******** | 90.124 | PASS | 90V_47Hz_No Load
152 | 90 | 47 | 1 | 2.5 | ******** | ******** | 90.085 | PASS | 90V_47Hz_LH_Standby_2.5A
156 | 90 | 47 | 1 | 0.1 | ******** | ******** | 90.122 | PASS | 90V_47Hz_LL_Standby_0.1A
161 | 90 | 47 | 0 | 0 | ******** | ******** | 90.124 | PASS | 90V_47Hz_No Load
166 | 90 | 47 | 1 | 0.1 | ******** | ******** | 90.107 | PASS | 90V_47Hz_LL
167 | 90 | 47 | 1 | 2.5 | ******** | ******** | 90.069 | PASS | 90V_47Hz_LH
187 | 90 | 47 | 71.3 | 0.1 | ******** | ******** | 89.232 | PASS | 90V_47Hz_HL
192 | 90 | 47 | 71.3 | 2.5 | ******** | ******** | 89.195 | PASS | 90V_47Hz_HH
210 | 100 | 60 | 79.5 | 0.1 | ******** | ******** | 99.176 | PASS | 100V_60Hz_HL
218 | 100 | 60 | 79.5 | 2.5 | ******** | ******** | 99.152 | PASS | HH
240 | 180 | 47 | 128.7 | 0.1 | ******** | ******** | 179.39 | PASS | 180V_47Hz_HL
248 | 180 | 47 | 128.7 | 2.5 | ******** | ******** | 179.366 | PASS | 180V_47Hz_HH
270 | 200 | 50 | 145.1 | 0.1 | ******** | ******** | 199.365 | PASS | 200V_50Hz_HL
278 | 200 | 50 | 145.1 | 2.5 | ******** | ******** | 199.385 | PASS | 200V_50Hz_HH
301 | 220 | 50 | 161.5 | 0.1 | ******** | ******** | 219.402 | PASS | 220V_50Hz_HL
309 | 220 | 50 | 161.5 | 2.5 | ******** | ******** | 219.393 | PASS | 220V_50Hz_HH
330 | 264 | 63 | 0 | 0 | ******** | ******** | 264.256 | PASS | 264V_63Hz_No Load
331 | 264 | 63 | 1 | 2.5 | ******** | ******** | 264.242 | PASS | 264V_63Hz_Standby_2.5A
335 | 264 | 63 | 1 | 0.1 | ******** | ******** | 264.255 | PASS | 264V_63Hz_LL_Standby_0.1A
340 | 264 | 63 | 0 | 0 | ******** | ******** | 264.256 | PASS | No Load
344 | 264 | 63 | 1 | 0.1 | ******** | ******** | 264.276 | PASS | 264V_63Hz_LL
345 | 264 | 63 | 1 | 2.5 | ******** | ******** | 264.262 | PASS | 264V_63Hz_LH
366 | 264 | 63 | 161.5 | 0.1 | ******** | ******** | 263.524 | PASS | 264V_63Hz_HL
374 | 264 | 63 | 161.5 | 2.5 | ******** | ******** | 263.515 | PASS | HH
398 | 164 | 30 | 0 | 0 | ******** | ******** | 164.197 | PASS | 164VDC_No Load
399 | 164 | 30 | 1 | 2.5 | ******** | ******** | 164.171 | PASS | 164Vdc_Standby_2.5A
403 | 164 | 30 | 1 | 0.1 | ******** | ******** | 164.195 | PASS | 164VDC_LL_Standby_0.1A
413 | 164 | 30 | 0 | 0 | ******** | ******** | 164.193 | PASS | No Load
417 | 164 | 30 | 1 | 0.1 | ******** | ******** | 164.187 | PASS | 164VDC_LL
418 | 164 | 30 | 1 | 2.5 | ******** | ******** | 164.163 | PASS | 164VDC_LH
434 | 164 | 30 | 64.35 | 1.25 | ******** | ******** | 163.765 | PASS | 164VDC_50%_L
435 | 164 | 30 | 128.7 | 2.5 | ******** | ******** | 163.276 | PASS | 164VDC_HH
443 | 164 | 30 | 128.7 | 0.1 | ******** | ******** | 163.334 | PASS | 164VDC_HL
454 | 200 | 30 | 145.1 | 0.1 | ******** | ******** | 199.378 | PASS | 200Vdc_HL
462 | 200 | 30 | 145.1 | 2.5 | ******** | ******** | 199.425 | PASS | 200Vdc_HH
474 | 220 | 30 | 161.5 | 0.1 | ******** | ******** | 219.419 | PASS | 220VDC_HL
482 | 220 | 30 | 161.5 | 2.5 | ******** | ******** | 219.421 | PASS | 220VDC_HH
490 | 300 | 30 | 0 | 0 | ******** | ******** | 300.321 | PASS | No Load
491 | 300 | 30 | 1 | 2.5 | ******** | ******** | 300.31 | PASS | 300Vdc_Standby_2.5A
495 | 300 | 30 | 1 | 0.1 | ******** | ******** | 300.318 | PASS | 300Vdc_Standby_0.1A
505 | 300 | 30 | 0 | 0 | ******** | ******** | 300.336 | PASS | No Load
509 | 300 | 30 | 1 | 0.1 | ******** | ******** | 300.328 | PASS | 300VDC_LL
510 | 300 | 30 | 1 | 2.5 | ******** | ******** | 300.316 | PASS | 300VDC_LH
527 | 300 | 30 | 80.75 | 1.25 | ******** | ******** | 300.047 | PASS | 300VDC_50%_L
528 | 300 | 30 | 161.5 | 0.1 | ******** | ******** | 299.718 | PASS | 300VDC_HL
533 | 300 | 30 | 161.5 | 2.5 | ******** | ******** | 299.72 | PASS | 300VDC_HH
---------------------------------------
PF
SEQ | Vin | Fin | Main_Load(A) | Vsb_Load(A) | SPEC_Max | SPEC_Min | Value | Result | Ext
150 | 90 | 47 | 0 | 0 | 1 | ******** | 0 | PASS | 90V_47Hz_No Load
152 | 90 | 47 | 1 | 2.5 | 1 | ******** | 0.9857 | PASS | 90V_47Hz_LH_Standby_2.5A
156 | 90 | 47 | 1 | 0.1 | 1 | ******** | 0.793 | PASS | 90V_47Hz_LL_Standby_0.1A
161 | 90 | 47 | 0 | 0 | 1 | ******** | 0 | PASS | 90V_47Hz_No Load
166 | 90 | 47 | 1 | 0.1 | 1 | ******** | 0.9617 | PASS | 90V_47Hz_LL
167 | 90 | 47 | 1 | 2.5 | 1 | ******** | 0.992 | PASS | 90V_47Hz_LH
187 | 90 | 47 | 71.3 | 0.1 | 1 | ******** | 0.9993 | PASS | 90V_47Hz_HL
192 | 90 | 47 | 71.3 | 2.5 | 1 | ******** | 0.9992 | PASS | 90V_47Hz_HH
210 | 100 | 60 | 79.5 | 0.1 | 1 | ******** | 0.9994 | PASS | 100V_60Hz_HL
218 | 100 | 60 | 79.5 | 2.5 | 1 | ******** | 0.9994 | PASS | HH
240 | 180 | 47 | 128.7 | 0.1 | 1 | ******** | 0.9992 | PASS | 180V_47Hz_HL
248 | 180 | 47 | 128.7 | 2.5 | 1 | ******** | 0.9992 | PASS | 180V_47Hz_HH
270 | 200 | 50 | 145.1 | 0.1 | 1 | ******** | 0.999 | PASS | 200V_50Hz_HL
278 | 200 | 50 | 145.1 | 2.5 | 1 | ******** | 0.999 | PASS | 200V_50Hz_HH
301 | 220 | 50 | 161.5 | 0.1 | 1 | ******** | 0.9987 | PASS | 220V_50Hz_HL
309 | 220 | 50 | 161.5 | 2.5 | 1 | ******** | 0.9987 | PASS | 220V_50Hz_HH
330 | 264 | 63 | 0 | 0 | 1 | ******** | 0.123 | PASS | 264V_63Hz_No Load
331 | 264 | 63 | 1 | 2.5 | 1 | ******** | 0.6416 | PASS | 264V_63Hz_Standby_2.5A
335 | 264 | 63 | 1 | 0.1 | 1 | ******** | 0.1654 | PASS | 264V_63Hz_LL_Standby_0.1A
340 | 264 | 63 | 0 | 0 | 1 | ******** | 0.1011 | PASS | No Load
344 | 264 | 63 | 1 | 0.1 | 1 | ******** | 0.403 | PASS | 264V_63Hz_LL
345 | 264 | 63 | 1 | 2.5 | 1 | ******** | 0.7261 | PASS | 264V_63Hz_LH
366 | 264 | 63 | 161.5 | 0.1 | 1 | ******** | 0.9975 | PASS | 264V_63Hz_HL
374 | 264 | 63 | 161.5 | 2.5 | 1 | ******** | 0.9974 | PASS | HH
398 | 164 | 30 | 0 | 0 | 1 | ******** | 0 | PASS | 164VDC_No Load
399 | 164 | 30 | 1 | 2.5 | 1 | ******** | 0.9997 | PASS | 164Vdc_Standby_2.5A
403 | 164 | 30 | 1 | 0.1 | 1 | ******** | 0 | PASS | 164VDC_LL_Standby_0.1A
413 | 164 | 30 | 0 | 0 | 1 | ******** | 0 | PASS | No Load
417 | 164 | 30 | 1 | 0.1 | 1 | ******** | 0.9984 | PASS | 164VDC_LL
418 | 164 | 30 | 1 | 2.5 | 1 | ******** | 0.9992 | PASS | 164VDC_LH
434 | 164 | 30 | 64.35 | 1.25 | 1 | ******** | 1 | PASS | 164VDC_50%_L
435 | 164 | 30 | 128.7 | 2.5 | 1 | ******** | 0.9999 | PASS | 164VDC_HH
443 | 164 | 30 | 128.7 | 0.1 | 1 | ******** | 1 | PASS | 164VDC_HL
454 | 200 | 30 | 145.1 | 0.1 | 1 | ******** | 1 | PASS | 200Vdc_HL
462 | 200 | 30 | 145.1 | 2.5 | 1 | ******** | 1 | PASS | 200Vdc_HH
474 | 220 | 30 | 161.5 | 0.1 | 1 | ******** | 1 | PASS | 220VDC_HL
482 | 220 | 30 | 161.5 | 2.5 | 1 | ******** | 1 | PASS | 220VDC_HH
490 | 300 | 30 | 0 | 0 | 1 | ******** | 0 | PASS | No Load
491 | 300 | 30 | 1 | 2.5 | 1 | ******** | 0.9992 | PASS | 300Vdc_Standby_2.5A
495 | 300 | 30 | 1 | 0.1 | 1 | ******** | 0 | PASS | 300Vdc_Standby_0.1A
505 | 300 | 30 | 0 | 0 | 1 | ******** | 0 | PASS | No Load
509 | 300 | 30 | 1 | 0.1 | 1 | ******** | 0 | PASS | 300VDC_LL
510 | 300 | 30 | 1 | 2.5 | 1 | ******** | 0.9994 | PASS | 300VDC_LH
527 | 300 | 30 | 80.75 | 1.25 | 1 | ******** | 1 | PASS | 300VDC_50%_L
528 | 300 | 30 | 161.5 | 0.1 | 1 | ******** | 1 | PASS | 300VDC_HL
533 | 300 | 30 | 161.5 | 2.5 | 1 | ******** | 1 | PASS | 300VDC_HH
---------------------------------------
THDi
SEQ | Vin | Fin | Main_Load(A) | Vsb_Load(A) | SPEC_Max | SPEC_Min | Value | Result | Ext
150 | 90 | 47 | 0 | 0 | ******** | * | 19.473 | PASS | 90V_47Hz_No Load
152 | 90 | 47 | 1 | 2.5 | ******** | * | 13.328 | PASS | 90V_47Hz_LH_Standby_2.5A
156 | 90 | 47 | 1 | 0.1 | ******** | * | 18.204 | PASS | 90V_47Hz_LL_Standby_0.1A
161 | 90 | 47 | 0 | 0 | ******** | * | 19.158 | PASS | 90V_47Hz_No Load
166 | 90 | 47 | 1 | 0.1 | ******** | * | 15.398 | PASS | 90V_47Hz_LL
167 | 90 | 47 | 1 | 2.5 | ******** | * | 11.236 | PASS | 90V_47Hz_LH
187 | 90 | 47 | 71.3 | 0.1 | ******** | * | 3.13 | PASS | 90V_47Hz_HL
192 | 90 | 47 | 71.3 | 2.5 | ******** | * | 3.322 | PASS | 90V_47Hz_HH
210 | 100 | 60 | 79.5 | 0.1 | ******** | * | 2.703 | PASS | 100V_60Hz_HL
218 | 100 | 60 | 79.5 | 2.5 | ******** | * | 2.727 | PASS | HH
240 | 180 | 47 | 128.7 | 0.1 | ******** | * | 2.525 | PASS | 180V_47Hz_HL
248 | 180 | 47 | 128.7 | 2.5 | ******** | * | 2.461 | PASS | 180V_47Hz_HH
270 | 200 | 50 | 145.1 | 0.1 | ******** | * | 2.448 | PASS | 200V_50Hz_HL
278 | 200 | 50 | 145.1 | 2.5 | ******** | * | 2.388 | PASS | 200V_50Hz_HH
301 | 220 | 50 | 161.5 | 0.1 | ******** | * | 2.405 | PASS | 220V_50Hz_HL
309 | 220 | 50 | 161.5 | 2.5 | ******** | * | 2.425 | PASS | 220V_50Hz_HH
330 | 264 | 63 | 0 | 0 | ******** | * | 18.694 | PASS | 264V_63Hz_No Load
331 | 264 | 63 | 1 | 2.5 | ******** | * | 22.878 | PASS | 264V_63Hz_Standby_2.5A
335 | 264 | 63 | 1 | 0.1 | ******** | * | 21.906 | PASS | 264V_63Hz_LL_Standby_0.1A
340 | 264 | 63 | 0 | 0 | ******** | * | 8.387 | PASS | No Load
344 | 264 | 63 | 1 | 0.1 | ******** | * | 28.515 | PASS | 264V_63Hz_LL
345 | 264 | 63 | 1 | 2.5 | ******** | * | 21.009 | PASS | 264V_63Hz_LH
366 | 264 | 63 | 161.5 | 0.1 | ******** | * | 2.294 | PASS | 264V_63Hz_HL
374 | 264 | 63 | 161.5 | 2.5 | ******** | * | 2.277 | PASS | HH
398 | 164 | 30 | 0 | 0 | ******** | * | XXXXXXXX | PASS | 164VDC_No Load
399 | 164 | 30 | 1 | 2.5 | ******** | * | 956.148 | PASS | 164Vdc_Standby_2.5A
403 | 164 | 30 | 1 | 0.1 | ******** | * | XXXXXXXX | PASS | 164VDC_LL_Standby_0.1A
413 | 164 | 30 | 0 | 0 | ******** | * | 71.345 | PASS | No Load
417 | 164 | 30 | 1 | 0.1 | ******** | * | 276.841 | PASS | 164VDC_LL
418 | 164 | 30 | 1 | 2.5 | ******** | * | 58.341 | PASS | 164VDC_LH
434 | 164 | 30 | 64.35 | 1.25 | ******** | * | 204.911 | PASS | 164VDC_50%_L
435 | 164 | 30 | 128.7 | 2.5 | ******** | * | 117.79 | PASS | 164VDC_HH
443 | 164 | 30 | 128.7 | 0.1 | ******** | * | 433.077 | PASS | 164VDC_HL
454 | 200 | 30 | 145.1 | 0.1 | ******** | * | 310.014 | PASS | 200Vdc_HL
462 | 200 | 30 | 145.1 | 2.5 | ******** | * | XXXXXXXX | PASS | 200Vdc_HH
474 | 220 | 30 | 161.5 | 0.1 | ******** | * | 236.608 | PASS | 220VDC_HL
482 | 220 | 30 | 161.5 | 2.5 | ******** | * | XXXXXXXX | PASS | 220VDC_HH
490 | 300 | 30 | 0 | 0 | ******** | * | XXXXXXXX | PASS | No Load
491 | 300 | 30 | 1 | 2.5 | ******** | * | 264.822 | PASS | 300Vdc_Standby_2.5A
495 | 300 | 30 | 1 | 0.1 | ******** | * | XXXXXXXX | PASS | 300Vdc_Standby_0.1A
505 | 300 | 30 | 0 | 0 | ******** | * | XXXXXXXX | PASS | No Load
509 | 300 | 30 | 1 | 0.1 | ******** | * | 299.626 | PASS | 300VDC_LL
510 | 300 | 30 | 1 | 2.5 | ******** | * | 407.544 | PASS | 300VDC_LH
527 | 300 | 30 | 80.75 | 1.25 | ******** | * | 133.165 | PASS | 300VDC_50%_L
528 | 300 | 30 | 161.5 | 0.1 | ******** | * | 128.478 | PASS | 300VDC_HL
533 | 300 | 30 | 161.5 | 2.5 | ******** | * | XXXXXXXX | PASS | 300VDC_HH
---------------------------------------
Irms
SEQ | Vin | Fin | Main_Load(A) | Vsb_Load(A) | SPEC_Max | SPEC_Min | Value | Result | Ext
150 | 90 | 47 | 0 | 0 | ******** | ******** | 0 | PASS | 90V_47Hz_No Load
152 | 90 | 47 | 1 | 2.5 | ******** | ******** | 0.471 | PASS | 90V_47Hz_LH_Standby_2.5A
156 | 90 | 47 | 1 | 0.1 | ******** | ******** | 0.088 | PASS | 90V_47Hz_LL_Standby_0.1A
161 | 90 | 47 | 0 | 0 | ******** | ******** | 0 | PASS | 90V_47Hz_No Load
166 | 90 | 47 | 1 | 0.1 | ******** | ******** | 0.249 | PASS | 90V_47Hz_LL
167 | 90 | 47 | 1 | 2.5 | ******** | ******** | 0.64 | PASS | 90V_47Hz_LH
187 | 90 | 47 | 71.3 | 0.1 | ******** | ******** | 11.232 | PASS | 90V_47Hz_HL
192 | 90 | 47 | 71.3 | 2.5 | ******** | ******** | 11.682 | PASS | 90V_47Hz_HH
210 | 100 | 60 | 79.5 | 0.1 | ******** | ******** | 11.166 | PASS | 100V_60Hz_HL
218 | 100 | 60 | 79.5 | 2.5 | 13 | ******** | 11.562 | PASS | HH
240 | 180 | 47 | 128.7 | 0.1 | ******** | ******** | 9.675 | PASS | 180V_47Hz_HL
248 | 180 | 47 | 128.7 | 2.5 | ******** | ******** | 9.881 | PASS | 180V_47Hz_HH
270 | 200 | 50 | 145.1 | 0.1 | ******** | ******** | 9.808 | PASS | 200V_50Hz_HL
278 | 200 | 50 | 145.1 | 2.5 | ******** | ******** | 9.993 | PASS | 200V_50Hz_HH
301 | 220 | 50 | 161.5 | 0.1 | ******** | ******** | 9.922 | PASS | 220V_50Hz_HL
309 | 220 | 50 | 161.5 | 2.5 | ******** | ******** | 10.099 | PASS | 220V_50Hz_HH
330 | 264 | 63 | 0 | 0 | ******** | ******** | 0.114 | PASS | 264V_63Hz_No Load
331 | 264 | 63 | 1 | 2.5 | ******** | ******** | 0.243 | PASS | 264V_63Hz_Standby_2.5A
335 | 264 | 63 | 1 | 0.1 | ******** | ******** | 0.118 | PASS | 264V_63Hz_LL_Standby_0.1A
340 | 264 | 63 | 0 | 0 | ******** | ******** | 0.112 | PASS | No Load
344 | 264 | 63 | 1 | 0.1 | ******** | ******** | 0.164 | PASS | 264V_63Hz_LL
345 | 264 | 63 | 1 | 2.5 | ******** | ******** | 0.298 | PASS | 264V_63Hz_LH
366 | 264 | 63 | 161.5 | 0.1 | ******** | ******** | 8.203 | PASS | 264V_63Hz_HL
374 | 264 | 63 | 161.5 | 2.5 | ******** | ******** | 8.35 | PASS | HH
398 | 164 | 30 | 0 | 0 | ******** | ******** | 0 | PASS | 164VDC_No Load
399 | 164 | 30 | 1 | 2.5 | ******** | ******** | 0.253 | PASS | 164Vdc_Standby_2.5A
403 | 164 | 30 | 1 | 0.1 | ******** | ******** | 0 | PASS | 164VDC_LL_Standby_0.1A
413 | 164 | 30 | 0 | 0 | ******** | ******** | 0 | PASS | No Load
417 | 164 | 30 | 1 | 0.1 | ******** | ******** | 0.108 | PASS | 164VDC_LL
418 | 164 | 30 | 1 | 2.5 | ******** | ******** | 0.341 | PASS | 164VDC_LH
434 | 164 | 30 | 64.35 | 1.25 | ******** | ******** | 5.426 | PASS | 164VDC_50%_L
435 | 164 | 30 | 128.7 | 2.5 | ******** | ******** | 10.906 | PASS | 164VDC_HH
443 | 164 | 30 | 128.7 | 0.1 | ******** | ******** | 10.686 | PASS | 164VDC_HL
454 | 200 | 30 | 145.1 | 0.1 | ******** | ******** | 9.808 | PASS | 200Vdc_HL
462 | 200 | 30 | 145.1 | 2.5 | ******** | ******** | 9.989 | PASS | 200Vdc_HH
474 | 220 | 30 | 161.5 | 0.1 | ******** | ******** | 9.919 | PASS | 220VDC_HL
482 | 220 | 30 | 161.5 | 2.5 | ******** | ******** | 10.092 | PASS | 220VDC_HH
490 | 300 | 30 | 0 | 0 | ******** | ******** | 0 | PASS | No Load
491 | 300 | 30 | 1 | 2.5 | ******** | ******** | 0.136 | PASS | 300Vdc_Standby_2.5A
495 | 300 | 30 | 1 | 0.1 | ******** | ******** | 0 | PASS | 300Vdc_Standby_0.1A
505 | 300 | 30 | 0 | 0 | ******** | ******** | 0 | PASS | No Load
509 | 300 | 30 | 1 | 0.1 | ******** | ******** | 0 | PASS | 300VDC_LL
510 | 300 | 30 | 1 | 2.5 | ******** | ******** | 0.187 | PASS | 300VDC_LH
527 | 300 | 30 | 80.75 | 1.25 | ******** | ******** | 3.607 | PASS | 300VDC_50%_L
528 | 300 | 30 | 161.5 | 0.1 | ******** | ******** | 7.172 | PASS | 300VDC_HL
533 | 300 | 30 | 161.5 | 2.5 | ******** | ******** | 7.295 | PASS | 300VDC_HH
---------------------------------------
Pin
SEQ | Vin | Fin | Main_Load(A) | Vsb_Load(A) | SPEC_Max | SPEC_Min | Value | Result | Ext
150 | 90 | 47 | 0 | 0 | ******** | ******** | 0 | PASS | 90V_47Hz_No Load
152 | 90 | 47 | 1 | 2.5 | ******** | ******** | 41.804 | PASS | 90V_47Hz_LH_Standby_2.5A
156 | 90 | 47 | 1 | 0.1 | ******** | ******** | 6.324 | PASS | 90V_47Hz_LL_Standby_0.1A
161 | 90 | 47 | 0 | 0 | ******** | ******** | 0 | PASS | 90V_47Hz_No Load
166 | 90 | 47 | 1 | 0.1 | ******** | ******** | 21.587 | PASS | 90V_47Hz_LL
167 | 90 | 47 | 1 | 2.5 | ******** | ******** | 57.181 | PASS | 90V_47Hz_LH
187 | 90 | 47 | 71.3 | 0.1 | ******** | ******** | XXXXXXXX | PASS | 90V_47Hz_HL
192 | 90 | 47 | 71.3 | 2.5 | ******** | ******** | XXXXXXXX | PASS | 90V_47Hz_HH
210 | 100 | 60 | 79.5 | 0.1 | ******** | ******** | XXXXXXXX | PASS | 100V_60Hz_HL
218 | 100 | 60 | 79.5 | 2.5 | ******** | ******** | XXXXXXXX | PASS | HH
240 | 180 | 47 | 128.7 | 0.1 | ******** | ******** | XXXXXXXX | PASS | 180V_47Hz_HL
248 | 180 | 47 | 128.7 | 2.5 | ******** | ******** | XXXXXXXX | PASS | 180V_47Hz_HH
270 | 200 | 50 | 145.1 | 0.1 | ******** | ******** | XXXXXXXX | PASS | 200V_50Hz_HL
278 | 200 | 50 | 145.1 | 2.5 | ******** | ******** | XXXXXXXX | PASS | 200V_50Hz_HH
301 | 220 | 50 | 161.5 | 0.1 | ******** | ******** | XXXXXXXX | PASS | 220V_50Hz_HL
309 | 220 | 50 | 161.5 | 2.5 | ******** | ******** | XXXXXXXX | PASS | 220V_50Hz_HH
330 | 264 | 63 | 0 | 0 | ******** | ******** | 3.691 | PASS | 264V_63Hz_No Load
331 | 264 | 63 | 1 | 2.5 | ******** | ******** | 41.225 | PASS | 264V_63Hz_Standby_2.5A
335 | 264 | 63 | 1 | 0.1 | ******** | ******** | 5.168 | PASS | 264V_63Hz_LL_Standby_0.1A
340 | 264 | 63 | 0 | 0 | ******** | ******** | 3.005 | PASS | No Load
344 | 264 | 63 | 1 | 0.1 | ******** | ******** | 17.494 | PASS | 264V_63Hz_LL
345 | 264 | 63 | 1 | 2.5 | ******** | ******** | 57.182 | PASS | 264V_63Hz_LH
366 | 264 | 63 | 161.5 | 0.1 | ******** | ******** | XXXXXXXX | PASS | 264V_63Hz_HL
374 | 264 | 63 | 161.5 | 2.5 | ******** | ******** | XXXXXXXX | PASS | HH
398 | 164 | 30 | 0 | 0 | ******** | ******** | 0 | PASS | 164VDC_No Load
399 | 164 | 30 | 1 | 2.5 | ******** | ******** | 41.589 | PASS | 164Vdc_Standby_2.5A
403 | 164 | 30 | 1 | 0.1 | ******** | ******** | 0 | PASS | 164VDC_LL_Standby_0.1A
413 | 164 | 30 | 0 | 0 | ******** | ******** | 0 | PASS | No Load
417 | 164 | 30 | 1 | 0.1 | ******** | ******** | 17.728 | PASS | 164VDC_LL
418 | 164 | 30 | 1 | 2.5 | ******** | ******** | 55.878 | PASS | 164VDC_LH
434 | 164 | 30 | 64.35 | 1.25 | ******** | ******** | 888.47 | PASS | 164VDC_50%_L
435 | 164 | 30 | 128.7 | 2.5 | ******** | ******** | XXXXXXXX | PASS | 164VDC_HH
443 | 164 | 30 | 128.7 | 0.1 | ******** | ******** | XXXXXXXX | PASS | 164VDC_HL
454 | 200 | 30 | 145.1 | 0.1 | ******** | ******** | XXXXXXXX | PASS | 200Vdc_HL
462 | 200 | 30 | 145.1 | 2.5 | ******** | ******** | XXXXXXXX | PASS | 200Vdc_HH
474 | 220 | 30 | 161.5 | 0.1 | ******** | ******** | XXXXXXXX | PASS | 220VDC_HL
482 | 220 | 30 | 161.5 | 2.5 | ******** | ******** | XXXXXXXX | PASS | 220VDC_HH
490 | 300 | 30 | 0 | 0 | ******** | ******** | 0 | PASS | No Load
491 | 300 | 30 | 1 | 2.5 | ******** | ******** | 40.932 | PASS | 300Vdc_Standby_2.5A
495 | 300 | 30 | 1 | 0.1 | ******** | ******** | 0 | PASS | 300Vdc_Standby_0.1A
505 | 300 | 30 | 0 | 0 | ******** | ******** | 0 | PASS | No Load
509 | 300 | 30 | 1 | 0.1 | ******** | ******** | 0 | PASS | 300VDC_LL
510 | 300 | 30 | 1 | 2.5 | ******** | ******** | 56.239 | PASS | 300VDC_LH
527 | 300 | 30 | 80.75 | 1.25 | ******** | ******** | XXXXXXXX | PASS | 300VDC_50%_L
528 | 300 | 30 | 161.5 | 0.1 | ******** | ******** | XXXXXXXX | PASS | 300VDC_HL
533 | 300 | 30 | 161.5 | 2.5 | ******** | ******** | XXXXXXXX | PASS | 300VDC_HH
---------------------------------------
Pout
SEQ | Vin | Fin | Main_Load(A) | Vsb_Load(A) | SPEC_Max | SPEC_Min | Value | Result | Ext
150 | 90 | 47 | 0 | 0 | ******** | ******** | 0 | PASS | 90V_47Hz_No Load
152 | 90 | 47 | 1 | 2.5 | ******** | ******** | 30.019 | PASS | 90V_47Hz_LH_Standby_2.5A
156 | 90 | 47 | 1 | 0.1 | ******** | ******** | 1.217 | PASS | 90V_47Hz_LL_Standby_0.1A
161 | 90 | 47 | 0 | 0 | ******** | ******** | 0 | PASS | 90V_47Hz_No Load
166 | 90 | 47 | 1 | 0.1 | ******** | ******** | 13.446 | PASS | 90V_47Hz_LL
167 | 90 | 47 | 1 | 2.5 | ******** | ******** | 42.253 | PASS | 90V_47Hz_LH
187 | 90 | 47 | 71.3 | 0.1 | ******** | ******** | 872.48 | PASS | 90V_47Hz_HL
192 | 90 | 47 | 71.3 | 2.5 | ******** | ******** | 901.223 | PASS | 90V_47Hz_HH
210 | 100 | 60 | 79.5 | 0.1 | ******** | ******** | 971.92 | PASS | 100V_60Hz_HL
218 | 100 | 60 | 79.5 | 2.5 | ******** | ******** | XXXXXXXX | PASS | HH
240 | 180 | 47 | 128.7 | 0.1 | ******** | ******** | XXXXXXXX | PASS | 180V_47Hz_HL
248 | 180 | 47 | 128.7 | 2.5 | ******** | ******** | XXXXXXXX | PASS | 180V_47Hz_HH
270 | 200 | 50 | 145.1 | 0.1 | ******** | ******** | XXXXXXXX | PASS | 200V_50Hz_HL
278 | 200 | 50 | 145.1 | 2.5 | ******** | ******** | XXXXXXXX | PASS | 200V_50Hz_HH
301 | 220 | 50 | 161.5 | 0.1 | ******** | ******** | XXXXXXXX | PASS | 220V_50Hz_HL
309 | 220 | 50 | 161.5 | 2.5 | ******** | ******** | XXXXXXXX | PASS | 220V_50Hz_HH
330 | 264 | 63 | 0 | 0 | ******** | ******** | 0 | PASS | 264V_63Hz_No Load
331 | 264 | 63 | 1 | 2.5 | ******** | ******** | 30.024 | PASS | 264V_63Hz_Standby_2.5A
335 | 264 | 63 | 1 | 0.1 | ******** | ******** | 1.217 | PASS | 264V_63Hz_LL_Standby_0.1A
340 | 264 | 63 | 0 | 0 | ******** | ******** | 0 | PASS | No Load
344 | 264 | 63 | 1 | 0.1 | ******** | ******** | 13.45 | PASS | 264V_63Hz_LL
345 | 264 | 63 | 1 | 2.5 | ******** | ******** | 42.261 | PASS | 264V_63Hz_LH
366 | 264 | 63 | 161.5 | 0.1 | ******** | ******** | XXXXXXXX | PASS | 264V_63Hz_HL
374 | 264 | 63 | 161.5 | 2.5 | ******** | ******** | XXXXXXXX | PASS | HH
398 | 164 | 30 | 0 | 0 | ******** | ******** | 0 | PASS | 164VDC_No Load
399 | 164 | 30 | 1 | 2.5 | ******** | ******** | 30.026 | PASS | 164Vdc_Standby_2.5A
403 | 164 | 30 | 1 | 0.1 | ******** | ******** | 1.217 | PASS | 164VDC_LL_Standby_0.1A
413 | 164 | 30 | 0 | 0 | ******** | ******** | 0 | PASS | No Load
417 | 164 | 30 | 1 | 0.1 | ******** | ******** | 13.446 | PASS | 164VDC_LL
418 | 164 | 30 | 1 | 2.5 | ******** | ******** | 42.26 | PASS | 164VDC_LH
434 | 164 | 30 | 64.35 | 1.25 | ******** | ******** | 801.675 | PASS | 164VDC_50%_L
435 | 164 | 30 | 128.7 | 2.5 | ******** | ******** | XXXXXXXX | PASS | 164VDC_HH
443 | 164 | 30 | 128.7 | 0.1 | ******** | ******** | XXXXXXXX | PASS | 164VDC_HL
454 | 200 | 30 | 145.1 | 0.1 | ******** | ******** | XXXXXXXX | PASS | 200Vdc_HL
462 | 200 | 30 | 145.1 | 2.5 | ******** | ******** | XXXXXXXX | PASS | 200Vdc_HH
474 | 220 | 30 | 161.5 | 0.1 | ******** | ******** | XXXXXXXX | PASS | 220VDC_HL
482 | 220 | 30 | 161.5 | 2.5 | ******** | ******** | XXXXXXXX | PASS | 220VDC_HH
490 | 300 | 30 | 0 | 0 | ******** | ******** | 0 | PASS | No Load
491 | 300 | 30 | 1 | 2.5 | ******** | ******** | 30.03 | PASS | 300Vdc_Standby_2.5A
495 | 300 | 30 | 1 | 0.1 | ******** | ******** | 1.217 | PASS | 300Vdc_Standby_0.1A
505 | 300 | 30 | 0 | 0 | ******** | ******** | 0 | PASS | No Load
509 | 300 | 30 | 1 | 0.1 | ******** | ******** | 13.45 | PASS | 300VDC_LL
510 | 300 | 30 | 1 | 2.5 | ******** | ******** | 42.264 | PASS | 300VDC_LH
527 | 300 | 30 | 80.75 | 1.25 | ******** | ******** | XXXXXXXX | PASS | 300VDC_50%_L
528 | 300 | 30 | 161.5 | 0.1 | ******** | ******** | XXXXXXXX | PASS | 300VDC_HL
533 | 300 | 30 | 161.5 | 2.5 | ******** | ******** | XXXXXXXX | PASS | 300VDC_HH
---------------------------------------
EFF
SEQ | Vin | Fin | Main_Load(A) | Vsb_Load(A) | SPEC_Max | SPEC_Min | Value | Result | Ext
150 | 90 | 47 | 0 | 0 | ******** | ******** | 0 | PASS | 90V_47Hz_No Load
152 | 90 | 47 | 1 | 2.5 | ******** | ******** | 71.809 | PASS | 90V_47Hz_LH_Standby_2.5A
156 | 90 | 47 | 1 | 0.1 | ******** | ******** | 19.241 | PASS | 90V_47Hz_LL_Standby_0.1A
161 | 90 | 47 | 0 | 0 | ******** | ******** | 0 | PASS | 90V_47Hz_No Load
166 | 90 | 47 | 1 | 0.1 | ******** | ******** | 62.287 | PASS | 90V_47Hz_LL
167 | 90 | 47 | 1 | 2.5 | ******** | ******** | 73.893 | PASS | 90V_47Hz_LH
187 | 90 | 47 | 71.3 | 0.1 | ******** | ******** | 87.118 | PASS | 90V_47Hz_HL
192 | 90 | 47 | 71.3 | 2.5 | ******** | ******** | 86.558 | PASS | 90V_47Hz_HH
210 | 100 | 60 | 79.5 | 0.1 | ******** | ******** | 87.813 | PASS | 100V_60Hz_HL
218 | 100 | 60 | 79.5 | 2.5 | ******** | ******** | 87.368 | PASS | HH
240 | 180 | 47 | 128.7 | 0.1 | ******** | ******** | 90.459 | PASS | 180V_47Hz_HL
248 | 180 | 47 | 128.7 | 2.5 | ******** | ******** | 90.23 | PASS | 180V_47Hz_HH
270 | 200 | 50 | 145.1 | 0.1 | ******** | ******** | 90.478 | PASS | 200V_50Hz_HL
278 | 200 | 50 | 145.1 | 2.5 | ******** | ******** | 90.26 | PASS | 200V_50Hz_HH
301 | 220 | 50 | 161.5 | 0.1 | ******** | ******** | 90.417 | PASS | 220V_50Hz_HL
309 | 220 | 50 | 161.5 | 2.5 | ******** | ******** | 90.124 | PASS | 220V_50Hz_HH
330 | 264 | 63 | 0 | 0 | ******** | ******** | 0 | PASS | 264V_63Hz_No Load
331 | 264 | 63 | 1 | 2.5 | ******** | ******** | 72.83 | PASS | 264V_63Hz_Standby_2.5A
335 | 264 | 63 | 1 | 0.1 | ******** | ******** | 23.55 | PASS | 264V_63Hz_LL_Standby_0.1A
340 | 264 | 63 | 0 | 0 | ******** | ******** | 0 | PASS | No Load
344 | 264 | 63 | 1 | 0.1 | ******** | ******** | 76.881 | PASS | 264V_63Hz_LL
345 | 264 | 63 | 1 | 2.5 | ******** | ******** | 73.906 | PASS | 264V_63Hz_LH
366 | 264 | 63 | 161.5 | 0.1 | ******** | ******** | 91.162 | PASS | 264V_63Hz_HL
374 | 264 | 63 | 161.5 | 2.5 | ******** | ******** | 90.886 | PASS | HH
398 | 164 | 30 | 0 | 0 | ******** | ******** | 0 | PASS | 164VDC_No Load
399 | 164 | 30 | 1 | 2.5 | ******** | ******** | 72.197 | PASS | 164Vdc_Standby_2.5A
403 | 164 | 30 | 1 | 0.1 | ******** | ******** | 0 | PASS | 164VDC_LL_Standby_0.1A
413 | 164 | 30 | 0 | 0 | ******** | ******** | 0 | PASS | No Load
417 | 164 | 30 | 1 | 0.1 | ******** | ******** | 75.847 | PASS | 164VDC_LL
418 | 164 | 30 | 1 | 2.5 | ******** | ******** | 75.629 | PASS | 164VDC_LH
434 | 164 | 30 | 64.35 | 1.25 | ******** | ******** | 90.231 | PASS | 164VDC_50%_L
435 | 164 | 30 | 128.7 | 2.5 | ******** | ******** | 89.763 | PASS | 164VDC_HH
443 | 164 | 30 | 128.7 | 0.1 | ******** | ******** | 89.934 | PASS | 164VDC_HL
454 | 200 | 30 | 145.1 | 0.1 | ******** | ******** | 90.398 | PASS | 200Vdc_HL
462 | 200 | 30 | 145.1 | 2.5 | ******** | ******** | 90.201 | PASS | 200Vdc_HH
474 | 220 | 30 | 161.5 | 0.1 | ******** | ******** | 90.34 | PASS | 220VDC_HL
482 | 220 | 30 | 161.5 | 2.5 | ******** | ******** | 90.086 | PASS | 220VDC_HH
490 | 300 | 30 | 0 | 0 | ******** | ******** | 0 | PASS | No Load
491 | 300 | 30 | 1 | 2.5 | ******** | ******** | 73.364 | PASS | 300Vdc_Standby_2.5A
495 | 300 | 30 | 1 | 0.1 | ******** | ******** | 0 | PASS | 300Vdc_Standby_0.1A
505 | 300 | 30 | 0 | 0 | ******** | ******** | 0 | PASS | No Load
509 | 300 | 30 | 1 | 0.1 | ******** | ******** | 0 | PASS | 300VDC_LL
510 | 300 | 30 | 1 | 2.5 | ******** | ******** | 75.152 | PASS | 300VDC_LH
527 | 300 | 30 | 80.75 | 1.25 | ******** | ******** | 92.544 | PASS | 300VDC_50%_L
528 | 300 | 30 | 161.5 | 0.1 | ******** | ******** | 91.472 | PASS | 300VDC_HL
533 | 300 | 30 | 161.5 | 2.5 | ******** | ******** | 91.234 | PASS | 300VDC_HH

## ACDC
Static ACDC 34970_or_Load_Multi or Single
SEQ | SPEC_Max | SPEC_Min | CH1_Value | SPEC_Max | SPEC_Min | CH2_Value | SPEC_Max | SPEC_Min | CH3_Value | SPEC_Max | SPEC_Min | CH4_Value | SPEC_Max | SPEC_Min | CH5_Value | SPEC_Max | SPEC_Min | CH6_Value | SPEC_Max | SPEC_Min | CH7_Value | Vin | Fin | Main_Load(A) | Vsb_Load(A) | Result | Ext
153 | 0.4 | ******* | 0.001 | 12.6 | 11.4 | 12.008 | 0.4 | ******* | 0.037 | 3.46 | 2.5 | 3.239 | 3.46 | 2.5 | 3.22 | ******* | ******* | 0.305 | 0.4 | ******* | 0.001 | 90 | 47 | 0 | 2.75 | PASS | 12Vsb_2.75A
154 | 0.4 | ******* | 0 | 12.6 | ******* | 11.973 | 0.4 | ******* | 0.036 | 3.46 | 2.4 | 3.241 | 3.46 | ******* | 3.211 | ******* | ******* | 0.312 | 0.4 | ******* | 0.004 | 90 | 47 | 0 | 3.65 | PASS | 12Vsb_OCP
155 | 0.4 | ******* | 0.001 | 12.6 | 11.4 | 12.006 | 0.4 | ******* | 0.037 | 3.46 | 2.5 | 3.245 | 3.46 | 2.5 | 3.211 | ******* | ******* | 0.342 | 0.4 | ******* | 0.001 | 90 | 47 | 0 | 2.75 | PASS | 12Vsb_2.75A
163 | 12.81 | 11.59 | 12.259 | 12.6 | 11.4 | 12.003 | 3.46 | 2.5 | 3.243 | 3.46 | 2.5 | 3.243 | 3.46 | 2.5 | 3.219 | ******* | ******* | 0.06 | 0.4 | ******* | 0.001 | 90 | 47 | 1 | 2.75 | PASS | 12Vsb_2.75A
164 | 0.4 | ******* | 0.001 | 12.6 | ******* | 11.976 | 0.4 | ******* | 0.039 | 3.46 | 2.4 | 3.242 | 3.46 | ******* | 3.211 | ******* | ******* | 0.121 | 0.4 | ******* | 0.004 | 90 | 47 | 1 | 3.65 | PASS | 12Vsb_OCP
165 | 12.81 | 11.59 | 12.251 | 12.6 | 11.4 | 12.007 | 3.46 | 2.5 | 3.243 | 3.46 | 2.5 | 3.243 | 3.46 | 2.5 | 3.219 | ******* | ******* | 0.061 | 0.4 | ******* | 0.001 | 90 | 47 | 1 | 2.75 | PASS | 12Vsb_2.75A
169 | 12.81 | 11.59 | 12.258 | 12.6 | 11.4 | 12.141 | 3.46 | 2.5 | 3.247 | 3.46 | 2.5 | 3.243 | 3.46 | 2.5 | 3.214 | ******* | ******* | 0.061 | 3.46 | 2.5 | 3.19 | 90 | 47 | 1 | 0.1 | PASS | 90V_47Hz_LL_Cheak CR
171 | 12.81 | 11.59 | 12.259 | 12.6 | 11.4 | 12.136 | 3.46 | 2.5 | 3.251 | 3.46 | 2.5 | 3.245 | 3.46 | 2.5 | 3.216 | ******* | ******* | 0.061 | 0.4 | ******* | 0.003 | 90 | 47 | 1 | 0.1 | PASS | 90V_47Hz_LL_Clear CR
178 | 0.4 | ******* | 0.001 | 12.6 | 11.4 | 12.014 | 0.4 | ******* | 0.037 | 3.46 | 2.5 | 3.239 | 3.46 | 2.5 | 3.217 | ******* | ******* | 0.134 | 0.4 | ******* | 0.003 | 90 | 47 | 71.3 | 2.5 | PASS | 90V_47Hz_HH_I2C_OVP
189 | 12.81 | 11.59 | 12.219 | 12.6 | 11.4 | 12.002 | 3.46 | 2.5 | 3.229 | 3.46 | 2.5 | 3.236 | 3.46 | 2.5 | 3.216 | ******* | ******* | 3.53 | 3.46 | 2.5 | 3.179 | 90 | 47 | 71.3 | 2.5 | PASS | 90V_47Hz_HH_Cheak CR
191 | 12.81 | 11.59 | 12.219 | 12.6 | 11.4 | 12.005 | 3.46 | 2.5 | 3.238 | 3.46 | 2.5 | 3.235 | 3.46 | 2.5 | 3.218 | ******* | ******* | 3.53 | 0.4 | ******* | -0.009 | 90 | 47 | 71.3 | 2.5 | PASS | 90V_47Hz_HH_Clear CR
196 | 0.4 | ******* | 0.001 | 12.6 | 11.4 | 12.016 | 0.4 | ******* | 0.037 | 3.46 | 2.5 | 3.239 | 0.4 | ******* | 0.069 | ******* | ******* | -0.006 | 0.4 | ******* | 0.003 | 90 | 47 | 71.3 | 2.5 | PASS | 90V-OCP2 Recover Set
198 | 12.81 | 11.59 | 12.218 | 12.6 | 11.4 | 12.006 | 3.46 | 2.5 | 3.236 | 3.46 | 2.5 | 3.24 | 3.46 | 2.5 | 3.216 | ******* | ******* | 3.531 | 0.4 | ******* | -0.009 | 90 | 47 | 71.3 | 2.5 | PASS | 90V-OCP2_Recover Check
211 | 12.81 | 11.59 | 12.214 | 12.6 | 11.4 | 11.994 | 3.46 | 2.5 | 3.235 | 3.46 | 2.5 | 3.237 | 3.46 | 2.5 | 3.216 | ******* | ******* | 3.933 | 0.4 | ******* | -0.01 | 100 | 60 | 79.5 | 2.75 | PASS | 100V_60Hz_H_12Vsb_2.75A
212 | 0.4 | ******* | 0.001 | 12.6 | ******* | 11.976 | 0.4 | ******* | 0.038 | 3.46 | 2.4 | 3.244 | 3.46 | ******* | 3.218 | ******* | ******* | 0.161 | 0.4 | ******* | 0.004 | 100 | 60 | 79.5 | 3.65 | PASS | 100V_60Hz_H_12Vsb_OCP
213 | 12.81 | 11.59 | 12.199 | 12.6 | 11.4 | 11.994 | 3.46 | 2.5 | 3.238 | 3.46 | 2.5 | 3.237 | 3.46 | 2.5 | 3.218 | ******* | ******* | 3.933 | 0.4 | ******* | -0.01 | 100 | 60 | 79.5 | 2.75 | PASS | 100V_60Hz_H_12Vsb_2.75A
215 | 12.81 | 11.59 | 12.216 | 12.6 | 11.4 | 12.005 | 3.46 | 2.5 | 3.228 | 3.46 | 2.5 | 3.235 | 3.46 | 2.5 | 3.217 | ******* | ******* | 3.934 | 3.46 | 2.5 | 3.178 | 100 | 60 | 79.5 | 2.5 | PASS | 100V_60Hz_HH_Cheak CR
217 | 12.81 | 11.59 | 12.214 | 12.6 | 11.4 | 12.005 | 3.46 | 2.5 | 3.236 | 3.46 | 2.5 | 3.233 | 3.46 | 2.5 | 3.222 | ******* | ******* | 3.934 | 0.4 | ******* | -0.01 | 100 | 60 | 79.5 | 2.5 | PASS | 100V_60Hz_HH_Clear CR
219 | 12.81 | 11.59 | 12.209 | 12.6 | 11.4 | 12.002 | 3.46 | 2.5 | 3.236 | 3.46 | 2.5 | 3.23 | 3.46 | ******* | 0.056 | ******* | ******* | 4.51 | 0.4 | ******* | -0.012 | 110 | 60 | 91.425 | 2.5 | PASS | 110V-OCW
241 | 12.81 | 11.59 | 12.183 | 12.6 | 11.4 | 11.989 | 3.46 | 2.5 | 3.23 | 3.46 | 2.5 | 3.224 | 3.46 | 2.5 | 3.226 | ******* | ******* | 6.357 | 0.4 | ******* | -0.017 | 180 | 47 | 128.7 | 2.75 | PASS | 180V_47Hz_H_12Vsb_2.75A
242 | 0.4 | ******* | 0.001 | 12.6 | ******* | 11.976 | 0.4 | ******* | 0.039 | 3.46 | 2.4 | 3.244 | 3.46 | ******* | 3.214 | ******* | ******* | 0.192 | 0.4 | ******* | 0.004 | 180 | 47 | 128.7 | 3.65 | PASS | 180V_47Hz_H_12Vsb_OCP
243 | 12.81 | 11.59 | 12.177 | 12.6 | 11.4 | 11.991 | 3.46 | 2.5 | 3.226 | 3.46 | 2.5 | 3.231 | 3.46 | 2.5 | 3.221 | ******* | ******* | 6.359 | 0.4 | ******* | -0.017 | 180 | 47 | 128.7 | 2.75 | PASS | 180V_47Hz_H_12Vsb_2.75A
245 | 12.81 | 11.59 | 12.184 | 12.6 | 11.4 | 12 | 3.46 | 2.5 | 3.228 | 3.46 | 2.5 | 3.222 | 3.46 | 2.5 | 3.222 | ******* | ******* | 6.358 | 3.46 | 2.5 | 3.171 | 180 | 47 | 128.7 | 2.5 | PASS | 180V_47Hz_HH_Cheak CR
247 | 12.81 | 11.59 | 12.183 | 12.6 | 11.4 | 11.999 | 3.46 | 2.5 | 3.227 | 3.46 | 2.5 | 3.228 | 3.46 | 2.5 | 3.224 | ******* | ******* | 6.357 | 0.4 | ******* | -0.017 | 180 | 47 | 128.7 | 2.5 | PASS | 180V_47Hz_HH_Clear CR
249 | 12.81 | 11.59 | 12.172 | 12.6 | 11.4 | 11.996 | 3.46 | 2.5 | 3.222 | 3.46 | 2.5 | 3.228 | 3.46 | ******* | 0.048 | ******* | ******* | 7.323 | 0.4 | ******* | -0.02 | 180 | 47 | 148.005 | 2.5 | PASS | 180V-OCW
271 | 12.81 | 11.59 | 12.174 | 12.6 | 11.4 | 11.986 | 3.46 | 2.5 | 3.225 | 3.46 | 2.5 | 3.228 | 3.46 | 2.5 | 3.219 | ******* | ******* | 7.175 | 0.4 | ******* | -0.02 | 200 | 50 | 145.1 | 2.75 | PASS | 200V_50Hz_H_12Vsb_2.75A
272 | 0.4 | ******* | 0.001 | 12.6 | ******* | 11.977 | 0.4 | ******* | 0.039 | 3.46 | 2.4 | 3.241 | 3.46 | ******* | 3.219 | ******* | ******* | 0.161 | 0.4 | ******* | 0.004 | 200 | 50 | 145.1 | 3.65 | PASS | 200V_50Hz_H_12Vsb_OCP
273 | 12.81 | 11.59 | 12.171 | 12.6 | 11.4 | 11.988 | 3.46 | 2.5 | 3.222 | 3.46 | 2.5 | 3.223 | 3.46 | 2.5 | 3.226 | ******* | ******* | 7.173 | 0.4 | ******* | -0.02 | 200 | 50 | 145.1 | 2.75 | PASS | 200V_50Hz_H_12Vsb_2.75A
275 | 12.81 | 11.59 | 12.176 | 12.6 | 11.4 | 11.997 | 3.46 | 2.5 | 3.223 | 3.46 | 2.5 | 3.219 | 3.46 | 2.5 | 3.227 | ******* | ******* | 7.176 | 3.46 | 2.5 | 3.168 | 200 | 50 | 145.1 | 2.5 | PASS | 200V_50Hz_HH_Cheak CR
277 | 12.81 | 11.59 | 12.176 | 12.6 | 11.4 | 11.997 | 3.46 | 2.5 | 3.227 | 3.46 | 2.5 | 3.222 | 3.46 | 2.5 | 3.224 | ******* | ******* | 7.176 | 0.4 | ******* | -0.02 | 200 | 50 | 145.1 | 2.5 | PASS | 200V_50Hz_HH_Clear CR
279 | 12.81 | 11.59 | 12.163 | 12.6 | 11.4 | 11.994 | 3.46 | 2.5 | 3.226 | 3.46 | 2.5 | 3.22 | 3.46 | ******* | 0.045 | ******* | ******* | 8.274 | 0.4 | ******* | -0.023 | 200 | 50 | 166.865 | 2.5 | PASS | 200V-OCW
302 | 12.81 | 11.59 | 12.164 | 12.6 | 11.4 | 11.984 | 3.46 | 2.5 | 3.221 | 3.46 | 2.5 | 3.227 | 3.46 | 2.5 | 3.22 | ******* | ******* | 8.002 | 0.4 | ******* | -0.022 | 220 | 50 | 161.5 | 2.75 | PASS | 220V_50Hz_H_12Vsb_2.75A
303 | 0.4 | ******* | 0.001 | 12.6 | ******* | 11.977 | 0.4 | ******* | 0.039 | 3.46 | 2.4 | 3.242 | 3.46 | ******* | 3.216 | ******* | ******* | 0.159 | 0.4 | ******* | 0.004 | 220 | 50 | 161.5 | 3.65 | PASS | 220V_50Hz_H_12Vsb_OCP
304 | 12.81 | 11.59 | 12.157 | 12.6 | 11.4 | 11.988 | 3.46 | 2.5 | 3.219 | 3.46 | 2.5 | 3.222 | 3.46 | 2.5 | 3.226 | ******* | ******* | 7.998 | 0.4 | ******* | -0.022 | 220 | 50 | 161.5 | 2.75 | PASS | 220V_50Hz_H_12Vsb_2.75A
306 | 12.81 | 11.59 | 12.163 | 12.6 | 11.4 | 11.995 | 3.46 | 2.5 | 3.218 | 3.46 | 2.5 | 3.223 | 3.46 | 2.5 | 3.22 | ******* | ******* | 8.003 | 3.46 | 2.5 | 3.166 | 220 | 50 | 161.5 | 2.5 | PASS | 220V_50Hz_HH_Cheak CR
308 | 12.81 | 11.59 | 12.165 | 12.6 | 11.4 | 11.995 | 3.46 | 2.5 | 3.221 | 3.46 | 2.5 | 3.224 | 3.46 | 2.5 | 3.226 | ******* | ******* | 8.004 | 0.4 | ******* | -0.022 | 220 | 50 | 161.5 | 2.5 | PASS | 220V_50Hz_HH_Clear CR
310 | 12.81 | 11.59 | 12.153 | 12.6 | 11.4 | 11.992 | 3.46 | 2.5 | 3.22 | 3.46 | 2.5 | 3.22 | 3.46 | ******* | 3.224 | ******* | ******* | 9.016 | 0.4 | ******* | -0.026 | 220 | 50 | 185.38 | 2.5 | PASS | 220V-OCW
332 | 0.4 | ******* | 0.001 | 12.6 | 11.4 | 12.01 | 0.4 | ******* | 0.037 | 3.46 | 2.5 | 3.24 | 3.46 | 2.5 | 3.219 | ******* | ******* | 0.308 | 0.4 | ******* | 0.001 | 264 | 63 | 0 | 2.75 | PASS | 12Vsb_2.75A
333 | 0.4 | ******* | 0 | 12.6 | ******* | 11.974 | 0.4 | ******* | 0.036 | 3.46 | 2.4 | 3.243 | 3.46 | ******* | 3.213 | ******* | ******* | 0.307 | 0.4 | ******* | 0.005 | 264 | 63 | 0 | 3.65 | PASS | 12Vsb_OCP
334 | 0.4 | ******* | 0.001 | 12.6 | 11.4 | 12.008 | 0.4 | ******* | 0.037 | 3.46 | 2.5 | 3.241 | 3.46 | 2.5 | 3.218 | ******* | ******* | 0.349 | 0.4 | ******* | 0.001 | 264 | 63 | 0 | 2.75 | PASS | 12Vsb_2.75A
341 | 12.81 | 11.59 | 12.262 | 12.6 | 11.4 | 12.005 | 3.46 | 2.5 | 3.249 | 3.46 | 2.5 | 3.246 | 3.46 | 2.5 | 3.214 | ******* | ******* | 0.059 | 0.4 | ******* | 0.001 | 264 | 63 | 1 | 2.75 | PASS | 12Vsb_2.75A
342 | 0.4 | ******* | 0.001 | 12.6 | ******* | 11.978 | 0.4 | ******* | 0.038 | 3.46 | 2.4 | 3.246 | 3.46 | ******* | 3.216 | ******* | ******* | 0.167 | 0.4 | ******* | 0.005 | 264 | 63 | 1 | 3.65 | PASS | 12Vsb_OCP
343 | 12.81 | 11.59 | 12.259 | 12.6 | 11.4 | 12.009 | 3.46 | 2.5 | 3.248 | 3.46 | 2.5 | 3.249 | 3.46 | 2.5 | 3.212 | ******* | ******* | 0.061 | 0.4 | ******* | 0.001 | 264 | 63 | 1 | 2.75 | PASS | 12Vsb_2.75A
347 | 12.81 | 11.59 | 12.261 | 12.6 | 11.4 | 12.145 | 3.46 | 2.5 | 3.241 | 3.46 | 2.5 | 3.245 | 3.46 | 2.5 | 3.216 | ******* | ******* | 0.061 | 3.46 | 2.5 | 3.19 | 264 | 63 | 1 | 0.1 | PASS | 264V_63Hz_LL_Cheak CR
349 | 12.81 | 11.59 | 12.261 | 12.6 | 11.4 | 12.14 | 3.46 | 2.5 | 3.246 | 3.46 | 2.5 | 3.247 | 3.46 | 2.5 | 3.217 | ******* | ******* | 0.06 | 0.4 | ******* | 0.003 | 264 | 63 | 1 | 0.1 | PASS | 264V_63Hz_LL_Clear CR
351 | 0.4 | ******* | 0 | 12.6 | 11.4 | 12.139 | 0.4 | ******* | 0.039 | 3.46 | 2.5 | 3.242 | 3.46 | 2.5 | 3.215 | ******* | ******* | 0.131 | 0.4 | ******* | 0.004 | 264 | 63 | 1 | 0.1 | PASS | 264V_63Hz_LL
367 | 12.81 | 11.59 | 12.166 | 12.6 | 11.4 | 11.983 | 3.46 | 2.5 | 3.226 | 3.46 | 2.5 | 3.22 | 3.46 | 2.5 | 3.226 | ******* | ******* | 7.998 | 0.4 | ******* | -0.022 | 264 | 63 | 161.5 | 2.75 | PASS | 264V_63Hz_H_12Vsb_2.75A
368 | 0.4 | ******* | 0.001 | 12.6 | ******* | 11.976 | 0.4 | ******* | 0.039 | 3.46 | 2.4 | 3.24 | 3.46 | ******* | 3.218 | ******* | ******* | 0.154 | 0.4 | ******* | 0.005 | 264 | 63 | 161.5 | 3.65 | PASS | 264V_63Hz_H_12Vsb_OCP
369 | 12.81 | 11.59 | 12.161 | 12.6 | 11.4 | 11.988 | 3.46 | 2.5 | 3.222 | 3.46 | 2.5 | 3.22 | 3.46 | 2.5 | 3.228 | ******* | ******* | 7.999 | 0.4 | ******* | -0.022 | 264 | 63 | 161.5 | 2.75 | PASS | 264V_63Hz_H_12Vsb_2.75A
371 | 12.81 | 11.59 | 12.168 | 12.6 | 11.4 | 11.996 | 3.46 | 2.5 | 3.216 | 3.46 | 2.5 | 3.223 | 3.46 | 2.5 | 3.223 | ******* | ******* | 8.002 | 3.46 | 2.5 | 3.166 | 264 | 63 | 161.5 | 2.5 | PASS | 264V_63Hz_HH_Cheak CR
373 | 12.81 | 11.59 | 12.165 | 12.6 | 11.4 | 11.995 | 3.46 | 2.5 | 3.22 | 3.46 | 2.5 | 3.226 | 3.46 | 2.5 | 3.225 | ******* | ******* | 8.002 | 0.4 | ******* | -0.022 | 264 | 63 | 161.5 | 2.5 | PASS | 264V_63Hz_HH_Clear CR
375 | 12.81 | 11.59 | 12.154 | 12.6 | 11.4 | 11.992 | 3.46 | 2.5 | 3.217 | 3.46 | 2.5 | 3.22 | 3.46 | ******* | 3.227 | ******* | ******* | 9.017 | 0.4 | ******* | -0.026 | 264 | 63 | 185.38 | 2.5 | PASS | 264V-OCW
400 | 0.4 | ******* | 0.001 | 12.6 | 11.4 | 12.011 | 0.4 | ******* | 0.037 | 3.46 | 2.5 | 3.242 | 3.46 | 2.5 | 3.217 | ******* | ******* | 0.318 | 0.4 | ******* | 0.001 | 164 | 30 | 0 | 2.75 | PASS | 12Vsb_2.75A
401 | 0.4 | ******* | 0 | 12.6 | ******* | 11.665 | 0.4 | ******* | 0.036 | 3.46 | 2.4 | 3.245 | 3.46 | ******* | 3.212 | ******* | ******* | 0.312 | 0.4 | ******* | 0.005 | 164 | 30 | 0 | 3.65 | PASS | 12Vsb_OCP
402 | 0.4 | ******* | 0.001 | 12.6 | 11.4 | 12.008 | 0.4 | ******* | 0.037 | 3.46 | 2.5 | 3.242 | 3.46 | 2.5 | 3.214 | ******* | ******* | 0.311 | 0.4 | ******* | 0.001 | 164 | 30 | 0 | 2.75 | PASS | 12Vsb_2.75A
409 | 0.4 | ******* | 0 | 12.6 | 11.4 | 12.14 | 0.4 | ******* | 0.038 | 3.46 | 2.5 | 3.245 | 3.46 | 2.5 | 3.212 | ******* | ******* | 0.314 | 0.4 | ******* | 0.004 | 164 | 30 | 1 | 0.1 | PASS | 164VDC_LL
414 | 12.81 | 11.59 | 12.259 | 12.6 | 11.4 | 12.005 | 3.46 | 2.5 | 3.243 | 3.46 | 2.5 | 3.249 | 3.46 | 2.5 | 3.213 | ******* | ******* | 0.059 | 0.4 | ******* | 0.001 | 164 | 30 | 1 | 2.75 | PASS | 12Vsb_2.75A
415 | 0.4 | ******* | 0.001 | 12.6 | ******* | 11.977 | 0.4 | ******* | 0.039 | 3.46 | 2.4 | 3.245 | 3.46 | ******* | 3.214 | ******* | ******* | 0.124 | 0.4 | ******* | 0.005 | 164 | 30 | 1 | 3.65 | PASS | 12Vsb_OCP
416 | 12.81 | 11.59 | 12.257 | 12.6 | 11.4 | 12.008 | 3.46 | 2.5 | 3.243 | 3.46 | 2.5 | 3.245 | 3.46 | 2.5 | 3.218 | ******* | ******* | 0.063 | 0.4 | ******* | 0.002 | 164 | 30 | 1 | 2.75 | PASS | 12Vsb_2.75A
420 | 12.81 | 11.59 | 12.258 | 12.6 | 11.4 | 12.144 | 3.46 | 2.5 | 3.245 | 3.46 | 2.5 | 3.241 | 3.46 | 2.5 | 3.219 | ******* | ******* | 0.063 | 3.46 | 2.5 | 3.19 | 164 | 30 | 1 | 0.1 | PASS | 164VDC_LL_Cheak CR
422 | 12.81 | 11.59 | 12.259 | 12.6 | 11.4 | 12.141 | 3.46 | 2.5 | 3.246 | 3.46 | 2.5 | 3.246 | 3.46 | 2.5 | 3.218 | ******* | ******* | 0.061 | 0.4 | ******* | 0.003 | 164 | 30 | 1 | 0.1 | PASS | 164VDC_LL_Clear CR
436 | 12.81 | 11.59 | 12.188 | 12.6 | 11.4 | 11.993 | 3.46 | 2.5 | 3.228 | 3.46 | 2.5 | 3.225 | 3.46 | 2.5 | 3.227 | ******* | ******* | 6.357 | 0.4 | ******* | -0.017 | 164 | 30 | 128.7 | 2.75 | PASS | 164VDC_H_12Vsb_2.75A
437 | 0.4 | ******* | 0.001 | 12.6 | ******* | 11.977 | 0.4 | ******* | 0.039 | 3.46 | 2.4 | 3.245 | 3.46 | ******* | 3.213 | ******* | ******* | 0.151 | 0.4 | ******* | 0.005 | 164 | 30 | 128.7 | 3.65 | PASS | 164VDC_H_12Vsb_OCP
438 | 12.81 | 11.59 | 12.182 | 12.6 | 11.4 | 11.991 | 3.46 | 2.5 | 3.23 | 3.46 | 2.5 | 3.231 | 3.46 | 2.5 | 3.218 | ******* | ******* | 6.358 | 0.4 | ******* | -0.017 | 164 | 30 | 128.7 | 2.75 | PASS | 164VDC_H_12Vsb_2.75A
440 | 12.81 | 11.59 | 12.188 | 12.6 | 11.4 | 12 | 3.46 | 2.5 | 3.228 | 3.46 | 2.5 | 3.222 | 3.46 | 2.5 | 3.222 | ******* | ******* | 6.358 | 3.46 | 2.5 | 3.171 | 164 | 30 | 128.7 | 2.5 | PASS | 164VDC_HH_Cheak CR
442 | 12.81 | 11.59 | 12.187 | 12.6 | 11.4 | 11.998 | 3.46 | 2.5 | 3.227 | 3.46 | 2.5 | 3.231 | 3.46 | 2.5 | 3.218 | ******* | ******* | 6.357 | 0.4 | ******* | -0.017 | 164 | 30 | 128.7 | 2.5 | PASS | 164VDC_HH_Clear CR
455 | 12.81 | 11.59 | 12.176 | 12.6 | 11.4 | 11.986 | 3.46 | 2.5 | 3.228 | 3.46 | 2.5 | 3.226 | 3.46 | 2.5 | 3.221 | ******* | ******* | 7.175 | 0.4 | ******* | -0.019 | 200 | 30 | 145.1 | 2.75 | PASS | 200Vdc_H_12Vsb_2.75A
456 | 0.4 | ******* | 0.001 | 12.6 | ******* | 11.977 | 0.4 | ******* | 0.039 | 3.46 | 2.4 | 3.24 | 3.46 | ******* | 3.219 | ******* | ******* | 0.154 | 0.4 | ******* | 0.004 | 200 | 30 | 145.1 | 3.65 | PASS | 200Vdc_H_12Vsb_OCP
457 | 12.81 | 11.59 | 12.172 | 12.6 | 11.4 | 11.989 | 3.46 | 2.5 | 3.228 | 3.46 | 2.5 | 3.225 | 3.46 | 2.5 | 3.223 | ******* | ******* | 7.176 | 0.4 | ******* | -0.019 | 200 | 30 | 145.1 | 2.75 | PASS | 200Vdc_H_12Vsb_2.75A
459 | 12.81 | 11.59 | 12.176 | 12.6 | 11.4 | 11.997 | 3.46 | 2.5 | 3.223 | 3.46 | 2.5 | 3.219 | 3.46 | 2.5 | 3.226 | ******* | ******* | 7.174 | 3.46 | 2.5 | 3.168 | 200 | 30 | 145.1 | 2.5 | PASS | 200Vdc_HH_Cheak CR
461 | 12.81 | 11.59 | 12.176 | 12.6 | 11.4 | 11.997 | 3.46 | 2.5 | 3.229 | 3.46 | 2.5 | 3.223 | 3.46 | 2.5 | 3.224 | ******* | ******* | 7.176 | 0.4 | ******* | -0.019 | 200 | 30 | 145.1 | 2.5 | PASS | 200Vdc_HH_Clear CR
475 | 12.81 | 11.59 | 12.166 | 12.6 | 11.4 | 11.983 | 3.46 | 2.5 | 3.22 | 3.46 | 2.5 | 3.225 | 3.46 | 2.5 | 3.225 | ******* | ******* | 8.001 | 0.4 | ******* | -0.022 | 220 | 30 | 161.5 | 2.75 | PASS | 220Vdc_H_12Vsb_2.75A
476 | 0.4 | ******* | 0.001 | 12.6 | ******* | 11.978 | 0.4 | ******* | 0.038 | 3.46 | 2.4 | 3.247 | 3.46 | ******* | 3.211 | ******* | ******* | 0.17 | 0.4 | ******* | 0.005 | 220 | 30 | 161.5 | 3.65 | PASS | 220Vdc_H_12Vsb_OCP
477 | 12.81 | 11.59 | 12.16 | 12.6 | 11.4 | 11.988 | 3.46 | 2.5 | 3.224 | 3.46 | 2.5 | 3.227 | 3.46 | 2.5 | 3.22 | ******* | ******* | 8.001 | 0.4 | ******* | -0.022 | 220 | 30 | 161.5 | 2.75 | PASS | 220Vdc_H_12Vsb_2.75A
479 | 12.81 | 11.59 | 12.168 | 12.6 | 11.4 | 11.995 | 3.46 | 2.5 | 3.222 | 3.46 | 2.5 | 3.219 | 3.46 | 2.5 | 3.223 | ******* | ******* | 8.001 | 3.46 | 2.5 | 3.166 | 220 | 30 | 161.5 | 2.5 | PASS | 220VDC_HH_Cheak CR
481 | 12.81 | 11.59 | 12.168 | 12.6 | 11.4 | 11.995 | 3.46 | 2.5 | 3.223 | 3.46 | 2.5 | 3.221 | 3.46 | 2.5 | 3.228 | ******* | ******* | 8.002 | 0.4 | ******* | -0.022 | 220 | 30 | 161.5 | 2.5 | PASS | 220VDC_HH_Clear CR
492 | 0.4 | ******* | 0.001 | 12.6 | 11.4 | 12.009 | 0.4 | ******* | 0.037 | 3.46 | 2.5 | 3.239 | 3.46 | 2.5 | 3.22 | ******* | ******* | 0.302 | 0.4 | ******* | 0.001 | 300 | 30 | 0 | 2.75 | PASS | 12Vsb_2.75A
493 | 0.4 | ******* | 0 | 12.6 | ******* | 11.97 | 0.4 | ******* | 0.036 | 3.46 | 2.4 | 3.24 | 3.46 | ******* | 3.219 | ******* | ******* | 0.299 | 0.4 | ******* | 0.005 | 300 | 30 | 0 | 3.65 | PASS | 12Vsb_OCP
494 | 0.4 | ******* | 0.001 | 12.6 | 11.4 | 12.009 | 0.4 | ******* | 0.037 | 3.46 | 2.5 | 3.242 | 3.46 | 2.5 | 3.217 | ******* | ******* | 0.325 | 0.4 | ******* | 0.001 | 300 | 30 | 0 | 2.75 | PASS | 12Vsb_2.75A
501 | 0.4 | ******* | 0 | 12.6 | 11.4 | 12.139 | 0.4 | ******* | 0.039 | 3.46 | 2.5 | 3.24 | 3.46 | 2.5 | 3.219 | ******* | ******* | 0.295 | 0.4 | ******* | 0.004 | 300 | 30 | 1 | 0.1 | PASS | 300VDC_LL
506 | 12.81 | 11.59 | 12.261 | 12.6 | 11.4 | 12.004 | 3.46 | 2.5 | 3.244 | 3.46 | 2.5 | 3.246 | 3.46 | 2.5 | 3.217 | ******* | ******* | 0.059 | 0.4 | ******* | 0.001 | 300 | 30 | 1 | 2.75 | PASS | 12Vsb_2.75A
507 | 0.4 | ******* | 0.001 | 12.6 | ******* | 11.978 | 0.4 | ******* | 0.039 | 3.46 | 2.4 | 3.245 | 3.46 | ******* | 3.213 | ******* | ******* | 0.112 | 0.4 | ******* | 0.005 | 300 | 30 | 1 | 3.65 | PASS | 12Vsb_OCP
508 | 12.81 | 11.59 | 12.259 | 12.6 | 11.4 | 12.008 | 3.46 | 2.5 | 3.247 | 3.46 | 2.5 | 3.25 | 3.46 | 2.5 | 3.211 | ******* | ******* | 0.062 | 0.4 | ******* | 0.002 | 300 | 30 | 1 | 2.75 | PASS | 12Vsb_2.75A
512 | 12.81 | 11.59 | 12.262 | 12.6 | 11.4 | 12.145 | 3.46 | 2.5 | 3.243 | 3.46 | 2.5 | 3.246 | 3.46 | 2.5 | 3.212 | ******* | ******* | 0.061 | 3.46 | 2.5 | 3.19 | 300 | 30 | 1 | 0.1 | PASS | 300VDC_LL_Cheak CR
514 | 12.81 | 11.59 | 12.261 | 12.6 | 11.4 | 12.139 | 3.46 | 2.5 | 3.245 | 3.46 | 2.5 | 3.249 | 3.46 | 2.5 | 3.216 | ******* | ******* | 0.061 | 0.4 | ******* | 0.003 | 300 | 30 | 1 | 0.1 | PASS | 300VDC_LL_Clear CR
530 | 12.81 | 11.59 | 12.167 | 12.6 | 11.4 | 11.991 | 3.46 | 2.5 | 3.216 | 3.46 | 2.5 | 3.223 | 3.46 | 2.5 | 3.223 | ******* | ******* | 8.002 | 3.46 | 2.5 | 3.166 | 300 | 30 | 161.5 | 2.5 | PASS | 300VDC_HH_Cheak CR
532 | 12.81 | 11.59 | 12.165 | 12.6 | 11.4 | 11.994 | 3.46 | 2.5 | 3.226 | 3.46 | 2.5 | 3.22 | 3.46 | 2.5 | 3.226 | ******* | ******* | 7.999 | 0.4 | ******* | -0.022 | 300 | 30 | 161.5 | 2.5 | PASS | 300VDC_HH_Clear CR
534 | 12.81 | 11.59 | 12.165 | 12.6 | 11.4 | 11.988 | 3.46 | 2.5 | 3.226 | 3.46 | 2.5 | 3.224 | 3.46 | 2.5 | 3.222 | ******* | ******* | 8.003 | 0.4 | ******* | -0.022 | 300 | 30 | 161.5 | 2.75 | PASS | 300Vdc_H_12Vsb_2.75A
535 | 0.4 | ******* | 0.001 | 12.6 | ******* | 11.978 | 0.4 | ******* | 0.039 | 3.46 | 2.4 | 3.24 | 3.46 | ******* | 3.215 | ******* | ******* | 0.148 | 0.4 | ******* | 0.005 | 300 | 30 | 161.5 | 3.65 | PASS | 300Vdc_H_12Vsb_OCP
536 | 12.81 | 11.59 | 12.159 | 12.6 | 11.4 | 11.987 | 3.46 | 2.5 | 3.222 | 3.46 | 2.5 | 3.22 | 3.46 | 2.5 | 3.228 | ******* | ******* | 8.001 | 0.4 | ******* | -0.022 | 300 | 30 | 161.5 | 2.75 | PASS | 300Vdc_H_12Vsb_2.75A
542 | 12.81 | 11.59 | 12.219 | 12.6 | 11.4 | 12.005 | 3.46 | 2.5 | 3.235 | 3.46 | 2.5 | 3.24 | 3.46 | 2.5 | 3.215 | ******* | ******* | 3.531 | 0.4 | ******* | -0.009 | 100 | 60 | 71.3 | 2.5 | PASS | --------100Vac Distortion_H
544 | 12.81 | 11.59 | 12.259 | 12.6 | 11.4 | 12.138 | 3.46 | 2.5 | 3.246 | 3.46 | 2.5 | 3.251 | 3.46 | 2.5 | 3.212 | ******* | ******* | 0.06 | 0.4 | ******* | 0.003 | 100 | 60 | 1 | 0.1 | PASS | --------100Vac Distortion_L
546 | 12.81 | 11.59 | 12.259 | 12.6 | 11.4 | 12.135 | 3.46 | 2.5 | 3.244 | 3.46 | 2.5 | 3.249 | 3.46 | 2.5 | 3.214 | ******* | ******* | 0.06 | 0.4 | ******* | 0.003 | 200 | 50 | 1 | 0.1 | PASS | --------200Vac Distortion_L
548 | 12.81 | 11.59 | 12.185 | 12.6 | 11.4 | 11.995 | 3.46 | 2.5 | 3.227 | 3.46 | 2.5 | 3.232 | 3.46 | 2.5 | 3.218 | ******* | ******* | 6.359 | 0.4 | ******* | -0.017 | 200 | 50 | 128.7 | 2.5 | PASS | --------200Vac Distortion_H
550 | 12.81 | 11.59 | 12.259 | 12.6 | 11.4 | 12.135 | 3.46 | 2.5 | 3.244 | 3.46 | 2.5 | 3.251 | 3.46 | 2.5 | 3.214 | ******* | ******* | 0.06 | 0.4 | ******* | 0.003 | 89.5 | 47 | 1 | 0.1 | PASS | 89.5Vac_ON
551 | 12.81 | 11.59 | 12.259 | 12.6 | 11.4 | 12.133 | 3.46 | 2.5 | 3.251 | 3.46 | 2.5 | 3.244 | 3.46 | 2.5 | 3.219 | ******* | ******* | 0.061 | 0.4 | ******* | 0.003 | 80 | 47 | 1 | 0.1 | PASS | 80Vac_ON
552 | 0.4 | ******* | 0 | 0.4 | ******* | 0.11 | 0.4 | ******* | 0.038 | 0.4 | ******* | 0.039 | 0.4 | ******* | 0.071 | ******* | ******* | -0.012 | 0.4 | ******* | 0.004 | 70.5 | 47 | 1 | 0.1 | PASS | 70.5Vac_OFF
553 | 0.4 | ******* | 0 | 0.4 | ******* | 0.11 | 0.4 | ******* | 0.038 | 0.4 | ******* | 0.039 | 0.4 | ******* | 0.07 | ******* | ******* | -0.018 | 0.4 | ******* | 0.004 | 79.8 | 47 | 1 | 0.1 | PASS | 79.8Vac_OFF
555 | 12.81 | 11.59 | 12.216 | 12.6 | 11.4 | 12.003 | 3.46 | 2.5 | 3.234 | 3.46 | 2.5 | 3.233 | 3.46 | 2.5 | 3.215 | ******* | ******* | 3.532 | 0.4 | ******* | -0.009 | 89.5 | 47 | 71.3 | 2.5 | PASS | 89.5Vac_ON
556 | 12.81 | 11.59 | 12.214 | 12.6 | 11.4 | 12.005 | 3.46 | 2.5 | 3.233 | 3.46 | 2.5 | 3.238 | 3.46 | 2.5 | 3.219 | ******* | ******* | 3.532 | 0.4 | ******* | -0.009 | 80 | 47 | 71.3 | 2.5 | PASS | 80Vac_ON
557 | 0.4 | ******* | 0 | 0.4 | ******* | 0.099 | 0.4 | ******* | 0.038 | 0.4 | ******* | 0.039 | 0.4 | ******* | 0.071 | ******* | ******* | 0.005 | 0.4 | ******* | 0.004 | 70.5 | 47 | 71.3 | 2.5 | PASS | 70.5Vac_OFF
558 | 0.4 | ******* | 0 | 0.4 | ******* | 0.099 | 0.4 | ******* | 0.039 | 0.4 | ******* | 0.039 | 0.4 | ******* | 0.071 | ******* | ******* | -0.045 | 0.4 | ******* | 0.004 | 79.8 | 47 | 71.3 | 2.5 | PASS | 79.8Vac_OFF
560 | 12.81 | 11.59 | 12.216 | 12.6 | 11.4 | 12.005 | 3.46 | 2.5 | 3.237 | 3.46 | 2.5 | 3.238 | 3.46 | 2.5 | 3.218 | ******* | ******* | 3.533 | 0.4 | ******* | -0.009 | 90 | 47 | 71.3 | 2.5 | PASS
563 | 12.81 | 11.59 | 12.159 | 12.6 | 11.4 | 11.994 | 3.46 | 2.5 | 3.225 | 3.46 | 2.5 | 3.221 | 3.46 | 2.5 | 3.228 | ******* | ******* | 8.004 | 0.4 | ******* | -0.021 | 264 | 63 | 161.5 | 2.5 | PASS
---------------------------------------
Pout (W)
SEQ | Vin | Fin | Main_Load(A) | Vsb_Load(A) | SPEC_Max | SPEC_Min | Value | Result | Ext
153 | 90 | 47 | 0 | 2.75 | ******* | ******* | 33.018 | PASS | 12Vsb_2.75A
154 | 90 | 47 | 0 | 3.65 | ******* | ******* | 43.698 | PASS | 12Vsb_OCP
155 | 90 | 47 | 0 | 2.75 | ******* | ******* | 33.013 | PASS | 12Vsb_2.75A
163 | 90 | 47 | 1 | 2.75 | ******* | ******* | 45.234 | PASS | 12Vsb_2.75A
164 | 90 | 47 | 1 | 3.65 | ******* | ******* | 0.124 | PASS | 12Vsb_OCP
165 | 90 | 47 | 1 | 2.75 | ******* | ******* | 45.237 | PASS | 12Vsb_2.75A
169 | 90 | 47 | 1 | 0.1 | ******* | ******* | 13.445 | PASS | 90V_47Hz_LL_Cheak CR
171 | 90 | 47 | 1 | 0.1 | ******* | ******* | 13.447 | PASS | 90V_47Hz_LL_Clear CR
178 | 90 | 47 | 71.3 | 2.5 | ******* | ******* | 30.033 | PASS | 90V_47Hz_HH_I2C_OVP
189 | 90 | 47 | 71.3 | 2.5 | ******* | ******* | 901.215 | PASS | 90V_47Hz_HH_Cheak CR
191 | 90 | 47 | 71.3 | 2.5 | ******* | ******* | 901.169 | PASS | 90V_47Hz_HH_Clear CR
196 | 90 | 47 | 71.3 | 2.5 | ******* | ******* | 30.037 | PASS | 90V-OCP2 Recover Set
198 | 90 | 47 | 71.3 | 2.5 | ******* | ******* | 901.117 | PASS | 90V-OCP2_Recover Check
211 | 100 | 60 | 79.5 | 2.75 | ******* | ******* | XXXXXXX | PASS | 100V_60Hz_H_12Vsb_2.75A
212 | 100 | 60 | 79.5 | 3.65 | ******* | ******* | 0.123 | PASS | 100V_60Hz_H_12Vsb_OCP
213 | 100 | 60 | 79.5 | 2.75 | ******* | ******* | XXXXXXX | PASS | 100V_60Hz_H_12Vsb_2.75A
215 | 100 | 60 | 79.5 | 2.5 | ******* | ******* | XXXXXXX | PASS | 100V_60Hz_HH_Cheak CR
217 | 100 | 60 | 79.5 | 2.5 | ******* | ******* | XXXXXXX | PASS | 100V_60Hz_HH_Clear CR
219 | 110 | 60 | 91.425 | 2.5 | ******* | ******* | XXXXXXX | PASS | 110V-OCW
241 | 180 | 47 | 128.7 | 2.75 | ******* | ******* | XXXXXXX | PASS | 180V_47Hz_H_12Vsb_2.75A
242 | 180 | 47 | 128.7 | 3.65 | ******* | ******* | 0.113 | PASS | 180V_47Hz_H_12Vsb_OCP
243 | 180 | 47 | 128.7 | 2.75 | ******* | ******* | XXXXXXX | PASS | 180V_47Hz_H_12Vsb_2.75A
245 | 180 | 47 | 128.7 | 2.5 | ******* | ******* | XXXXXXX | PASS | 180V_47Hz_HH_Cheak CR
247 | 180 | 47 | 128.7 | 2.5 | ******* | ******* | XXXXXXX | PASS | 180V_47Hz_HH_Clear CR
249 | 180 | 47 | 148.005 | 2.5 | ******* | ******* | XXXXXXX | PASS | 180V-OCW
271 | 200 | 50 | 145.1 | 2.75 | ******* | ******* | XXXXXXX | PASS | 200V_50Hz_H_12Vsb_2.75A
272 | 200 | 50 | 145.1 | 3.65 | ******* | ******* | 0.095 | PASS | 200V_50Hz_H_12Vsb_OCP
273 | 200 | 50 | 145.1 | 2.75 | ******* | ******* | XXXXXXX | PASS | 200V_50Hz_H_12Vsb_2.75A
275 | 200 | 50 | 145.1 | 2.5 | ******* | ******* | XXXXXXX | PASS | 200V_50Hz_HH_Cheak CR
277 | 200 | 50 | 145.1 | 2.5 | ******* | ******* | XXXXXXX | PASS | 200V_50Hz_HH_Clear CR
279 | 200 | 50 | 166.865 | 2.5 | ******* | ******* | XXXXXXX | PASS | 200V-OCW
302 | 220 | 50 | 161.5 | 2.75 | ******* | ******* | XXXXXXX | PASS | 220V_50Hz_H_12Vsb_2.75A
303 | 220 | 50 | 161.5 | 3.65 | ******* | ******* | 0.113 | PASS | 220V_50Hz_H_12Vsb_OCP
304 | 220 | 50 | 161.5 | 2.75 | ******* | ******* | XXXXXXX | PASS | 220V_50Hz_H_12Vsb_2.75A
306 | 220 | 50 | 161.5 | 2.5 | ******* | ******* | XXXXXXX | PASS | 220V_50Hz_HH_Cheak CR
308 | 220 | 50 | 161.5 | 2.5 | ******* | ******* | XXXXXXX | PASS | 220V_50Hz_HH_Clear CR
310 | 220 | 50 | 185.38 | 2.5 | ******* | ******* | XXXXXXX | PASS | 220V-OCW
332 | 264 | 63 | 0 | 2.75 | ******* | ******* | 33.025 | PASS | 12Vsb_2.75A
333 | 264 | 63 | 0 | 3.65 | ******* | ******* | 43.704 | PASS | 12Vsb_OCP
334 | 264 | 63 | 0 | 2.75 | ******* | ******* | 33.019 | PASS | 12Vsb_2.75A
341 | 264 | 63 | 1 | 2.75 | ******* | ******* | 45.244 | PASS | 12Vsb_2.75A
342 | 264 | 63 | 1 | 3.65 | ******* | ******* | 0.13 | PASS | 12Vsb_OCP
343 | 264 | 63 | 1 | 2.75 | ******* | ******* | 45.255 | PASS | 12Vsb_2.75A
347 | 264 | 63 | 1 | 0.1 | ******* | ******* | 13.449 | PASS | 264V_63Hz_LL_Cheak CR
349 | 264 | 63 | 1 | 0.1 | ******* | ******* | 13.45 | PASS | 264V_63Hz_LL_Clear CR
351 | 264 | 63 | 1 | 0.1 | ******* | ******* | 1.216 | PASS | 264V_63Hz_LL
367 | 264 | 63 | 161.5 | 2.75 | ******* | ******* | XXXXXXX | PASS | 264V_63Hz_H_12Vsb_2.75A
368 | 264 | 63 | 161.5 | 3.65 | ******* | ******* | 0.134 | PASS | 264V_63Hz_H_12Vsb_OCP
369 | 264 | 63 | 161.5 | 2.75 | ******* | ******* | XXXXXXX | PASS | 264V_63Hz_H_12Vsb_2.75A
371 | 264 | 63 | 161.5 | 2.5 | ******* | ******* | XXXXXXX | PASS | 264V_63Hz_HH_Cheak CR
373 | 264 | 63 | 161.5 | 2.5 | ******* | ******* | XXXXXXX | PASS | 264V_63Hz_HH_Clear CR
375 | 264 | 63 | 185.38 | 2.5 | ******* | ******* | XXXXXXX | PASS | 264V-OCW
400 | 164 | 30 | 0 | 2.75 | ******* | ******* | 33.027 | PASS | 12Vsb_2.75A
401 | 164 | 30 | 0 | 3.65 | ******* | ******* | 42.574 | PASS | 12Vsb_OCP
402 | 164 | 30 | 0 | 2.75 | ******* | ******* | 33.021 | PASS | 12Vsb_2.75A
409 | 164 | 30 | 1 | 0.1 | ******* | ******* | 1.216 | PASS | 164VDC_LL
414 | 164 | 30 | 1 | 2.75 | ******* | ******* | 45.243 | PASS | 12Vsb_2.75A
415 | 164 | 30 | 1 | 3.65 | ******* | ******* | 0.132 | PASS | 12Vsb_OCP
416 | 164 | 30 | 1 | 2.75 | ******* | ******* | 45.249 | PASS | 12Vsb_2.75A
420 | 164 | 30 | 1 | 0.1 | ******* | ******* | 13.447 | PASS | 164VDC_LL_Cheak CR
422 | 164 | 30 | 1 | 0.1 | ******* | ******* | 13.448 | PASS | 164VDC_LL_Clear CR
436 | 164 | 30 | 128.7 | 2.75 | ******* | ******* | XXXXXXX | PASS | 164VDC_H_12Vsb_2.75A
437 | 164 | 30 | 128.7 | 3.65 | ******* | ******* | 0.126 | PASS | 164VDC_H_12Vsb_OCP
438 | 164 | 30 | 128.7 | 2.75 | ******* | ******* | XXXXXXX | PASS | 164VDC_H_12Vsb_2.75A
440 | 164 | 30 | 128.7 | 2.5 | ******* | ******* | XXXXXXX | PASS | 164VDC_HH_Cheak CR
442 | 164 | 30 | 128.7 | 2.5 | ******* | ******* | XXXXXXX | PASS | 164VDC_HH_Clear CR
455 | 200 | 30 | 145.1 | 2.75 | ******* | ******* | XXXXXXX | PASS | 200Vdc_H_12Vsb_2.75A
456 | 200 | 30 | 145.1 | 3.65 | ******* | ******* | 0.118 | PASS | 200Vdc_H_12Vsb_OCP
457 | 200 | 30 | 145.1 | 2.75 | ******* | ******* | XXXXXXX | PASS | 200Vdc_H_12Vsb_2.75A
459 | 200 | 30 | 145.1 | 2.5 | ******* | ******* | XXXXXXX | PASS | 200Vdc_HH_Cheak CR
461 | 200 | 30 | 145.1 | 2.5 | ******* | ******* | XXXXXXX | PASS | 200Vdc_HH_Clear CR
475 | 220 | 30 | 161.5 | 2.75 | ******* | ******* | XXXXXXX | PASS | 220Vdc_H_12Vsb_2.75A
476 | 220 | 30 | 161.5 | 3.65 | ******* | ******* | 0.157 | PASS | 220Vdc_H_12Vsb_OCP
477 | 220 | 30 | 161.5 | 2.75 | ******* | ******* | XXXXXXX | PASS | 220Vdc_H_12Vsb_2.75A
479 | 220 | 30 | 161.5 | 2.5 | ******* | ******* | XXXXXXX | PASS | 220VDC_HH_Cheak CR
481 | 220 | 30 | 161.5 | 2.5 | ******* | ******* | XXXXXXX | PASS | 220VDC_HH_Clear CR
492 | 300 | 30 | 0 | 2.75 | ******* | ******* | 33.023 | PASS | 12Vsb_2.75A
493 | 300 | 30 | 0 | 3.65 | ******* | ******* | 0.49 | PASS | 12Vsb_OCP
494 | 300 | 30 | 0 | 2.75 | ******* | ******* | 33.023 | PASS | 12Vsb_2.75A
501 | 300 | 30 | 1 | 0.1 | ******* | ******* | 1.216 | PASS | 300VDC_LL
506 | 300 | 30 | 1 | 2.75 | ******* | ******* | 45.241 | PASS | 12Vsb_2.75A
507 | 300 | 30 | 1 | 3.65 | ******* | ******* | 0.151 | PASS | 12Vsb_OCP
508 | 300 | 30 | 1 | 2.75 | ******* | ******* | 45.251 | PASS | 12Vsb_2.75A
512 | 300 | 30 | 1 | 0.1 | ******* | ******* | 13.45 | PASS | 300VDC_LL_Cheak CR
514 | 300 | 30 | 1 | 0.1 | ******* | ******* | 13.449 | PASS | 300VDC_LL_Clear CR
530 | 300 | 30 | 161.5 | 2.5 | ******* | ******* | XXXXXXX | PASS | 300VDC_HH_Cheak CR
532 | 300 | 30 | 161.5 | 2.5 | ******* | ******* | XXXXXXX | PASS | 300VDC_HH_Clear CR
534 | 300 | 30 | 161.5 | 2.75 | ******* | ******* | XXXXXXX | PASS | 300Vdc_H_12Vsb_2.75A
535 | 300 | 30 | 161.5 | 3.65 | ******* | ******* | 0.148 | PASS | 300Vdc_H_12Vsb_OCP
536 | 300 | 30 | 161.5 | 2.75 | ******* | ******* | XXXXXXX | PASS | 300Vdc_H_12Vsb_2.75A
542 | 100 | 60 | 71.3 | 2.5 | ******* | ******* | 901.222 | PASS | --------100Vac Distortion_H
544 | 100 | 60 | 1 | 0.1 | ******* | ******* | 13.446 | PASS | --------100Vac Distortion_L
546 | 200 | 50 | 1 | 0.1 | ******* | ******* | 13.447 | PASS | --------200Vac Distortion_L
548 | 200 | 50 | 128.7 | 2.5 | ******* | ******* | XXXXXXX | PASS | --------200Vac Distortion_H
550 | 89.5 | 47 | 1 | 0.1 | ******* | ******* | 13.446 | PASS | 89.5Vac_ON
551 | 80 | 47 | 1 | 0.1 | ******* | ******* | 13.447 | PASS | 80Vac_ON
552 | 70.5 | 47 | 1 | 0.1 | ******* | ******* | 0.001 | PASS | 70.5Vac_OFF
553 | 79.8 | 47 | 1 | 0.1 | ******* | ******* | 0.001 | PASS | 79.8Vac_OFF
555 | 89.5 | 47 | 71.3 | 2.5 | ******* | ******* | 900.953 | PASS | 89.5Vac_ON
556 | 80 | 47 | 71.3 | 2.5 | ******* | ******* | 900.85 | PASS | 80Vac_ON
557 | 70.5 | 47 | 71.3 | 2.5 | ******* | ******* | 0.001 | PASS | 70.5Vac_OFF
558 | 79.8 | 47 | 71.3 | 2.5 | ******* | ******* | 0.001 | PASS | 79.8Vac_OFF
560 | 90 | 47 | 71.3 | 2.5 | ******* | ******* | 901.011 | PASS
563 | 264 | 63 | 161.5 | 2.5 | ******* | ******* | XXXXXXX | PASS

## Drop
AC_DC Line Sag Surge 80611N-2_Multi_S2
SEQ | SPEC_Max | SPEC_Min | Value1_H | Value1_L | SPEC_Max | SPEC_Min | Value2_H | Value2_L | SPEC_Max | SPEC_Min | Value3_H | Value3_L | SPEC_Max | SPEC_Min | Value4_H | Value4_L | SPEC_Max | SPEC_Min | Value5_H | Value5_L | Vin | Fin | DelayTime(ms) | DropTime(ms) | DropRecoveryTime(ms) | DropVoltage | DropFrequency | Degree | DutyCycle | Main_Load(A) | Vsb_Load(A) | Result | Ext
572 | 12.81 | 11.59 | 12.251 | 12.232 | 12.6 | 11.4 | 12.057 | 12.046 | 3.46 | 2.5 | 3.27 | 3.277 | 3.46 | ********* | 3.263 | 0.061 | 3.46 | ********* | 3.258 | 3.257 | 90 | 47 | 3000 | 10 | 500 | 0 | 47 | 0 | 100 | 49.91 | 1.75 | PASS | 90Vac -->0Vac -10ms-0
574 | 12.81 | 11.59 | 12.251 | 12.231 | 12.6 | 11.4 | 12.058 | 12.047 | 3.46 | 2.5 | 3.27 | 3.277 | 3.46 | ********* | 3.263 | 0.065 | 3.46 | ********* | 3.259 | 3.257 | 90 | 47 | 500 | 10 | 500 | 0 | 47 | 45 | 100 | 49.91 | 1.75 | PASS | 90Vac -->0Vac - 10ms-45
576 | 12.81 | 11.59 | 12.251 | 12.231 | 12.6 | 11.4 | 12.056 | 12.046 | 3.46 | 2.5 | 3.27 | 3.277 | 3.46 | ********* | 3.265 | 0.065 | 3.46 | ********* | 3.258 | 3.255 | 90 | 47 | 500 | 10 | 500 | 0 | 47 | 90 | 100 | 49.91 | 1.75 | PASS | 90Vac -->0Vac - 10ms-90
578 | 12.81 | 11.59 | 12.251 | 12.233 | 12.6 | 11.4 | 12.056 | 12.047 | 3.46 | 2.5 | 3.27 | 3.278 | 3.46 | ********* | 3.263 | 0.063 | 3.46 | ********* | 3.258 | 3.257 | 90 | 47 | 500 | 10 | 500 | 0 | 47 | 135 | 100 | 49.91 | 1.75 | PASS | 90Vac -->0Vac - 10ms-135
580 | 12.81 | 11.59 | 12.251 | 12.231 | 12.6 | 11.4 | 12.057 | 12.047 | 3.46 | 2.5 | 3.27 | 3.277 | 3.46 | ********* | 3.263 | 0.064 | 3.46 | ********* | 3.258 | 3.257 | 90 | 47 | 500 | 10 | 500 | 0 | 47 | 225 | 100 | 49.91 | 1.75 | PASS | 90Vac -->0Vac - 10ms-225
582 | 12.81 | 11.59 | 12.249 | 12.231 | 12.6 | 11.4 | 12.057 | 12.047 | 3.46 | 2.5 | 3.27 | 3.278 | 3.46 | ********* | 3.263 | 0.065 | 3.46 | ********* | 3.258 | 3.255 | 90 | 47 | 500 | 10 | 500 | 0 | 47 | 270 | 100 | 49.91 | 1.75 | PASS | 90Vac -->0Vac - 10ms-270
584 | 12.81 | 11.59 | 12.249 | 12.231 | 12.6 | 11.4 | 12.057 | 12.047 | 3.46 | 2.5 | 3.27 | 3.277 | 3.46 | ********* | 3.264 | 0.063 | 3.46 | ********* | 3.257 | 3.255 | 90 | 47 | 500 | 10 | 500 | 0 | 47 | 315 | 100 | 49.91 | 1.75 | PASS | 90Vac -->0Vac - 10ms-315
589 | 12.81 | 11.59 | 12.245 | 12.224 | 12.6 | 11.4 | 12.055 | 12.046 | 3.46 | 2.5 | 3.269 | 3.275 | 3.46 | ********* | 3.263 | 0.064 | 3.46 | ********* | 3.258 | 3.257 | 100 | 60 | 3000 | 10 | 500 | 0 | 60 | 0 | 100 | 55.65 | 1.75 | PASS | 100Vac -->0Vac -10ms-0
591 | 12.81 | 11.59 | 12.247 | 12.226 | 12.6 | 11.4 | 12.055 | 12.046 | 3.46 | 2.5 | 3.27 | 3.274 | 3.46 | ********* | 3.262 | 0.064 | 3.46 | ********* | 3.258 | 3.257 | 100 | 60 | 500 | 10 | 500 | 0 | 60 | 45 | 100 | 55.65 | 1.75 | PASS | 100Vac -->0Vac - 10ms-45
593 | 12.81 | 11.59 | 12.245 | 12.227 | 12.6 | 11.4 | 12.055 | 12.046 | 3.46 | 2.5 | 3.269 | 3.277 | 3.46 | ********* | 3.262 | 0.061 | 3.46 | ********* | 3.257 | 3.257 | 100 | 60 | 500 | 10 | 500 | 0 | 60 | 90 | 100 | 55.65 | 1.75 | PASS | 100Vac -->0Vac - 10ms-90
595 | 12.81 | 11.59 | 12.245 | 12.226 | 12.6 | 11.4 | 12.057 | 12.047 | 3.46 | 2.5 | 3.268 | 3.277 | 3.46 | ********* | 3.263 | 0.062 | 3.46 | ********* | 3.259 | 3.257 | 100 | 60 | 500 | 10 | 500 | 0 | 60 | 135 | 100 | 55.65 | 1.75 | PASS | 100Vac -->0Vac - 10ms-135
597 | 12.81 | 11.59 | 12.247 | 12.227 | 12.6 | 11.4 | 12.057 | 12.046 | 3.46 | 2.5 | 3.269 | 3.275 | 3.46 | ********* | 3.263 | 0.065 | 3.46 | ********* | 3.258 | 3.257 | 100 | 60 | 500 | 10 | 500 | 0 | 60 | 225 | 100 | 55.65 | 1.75 | PASS | 100Vac -->0Vac - 10ms-225
599 | 12.81 | 11.59 | 12.247 | 12.227 | 12.6 | 11.4 | 12.057 | 12.047 | 3.46 | 2.5 | 3.27 | 3.275 | 3.46 | ********* | 3.263 | 0.062 | 3.46 | ********* | 3.257 | 3.257 | 100 | 60 | 500 | 10 | 500 | 0 | 60 | 270 | 100 | 55.65 | 1.75 | PASS | 100Vac -->0Vac - 10ms-270
601 | 12.81 | 11.59 | 12.247 | 12.226 | 12.6 | 11.4 | 12.057 | 12.047 | 3.46 | 2.5 | 3.269 | 3.275 | 3.46 | ********* | 3.263 | 0.065 | 3.46 | ********* | 3.258 | 3.258 | 100 | 60 | 500 | 10 | 500 | 0 | 60 | 315 | 100 | 55.65 | 1.75 | PASS | 100Vac -->0Vac - 10ms-315
606 | 12.81 | 11.59 | 12.225 | 12.204 | 12.6 | 11.4 | 12.052 | 12.042 | 3.46 | 2.5 | 3.264 | 3.272 | 3.46 | ********* | 3.257 | 0.057 | 3.46 | ********* | 3.26 | 3.259 | 180 | 47 | 3000 | 10 | 500 | 0 | 47 | 0 | 100 | 90.09 | 1.75 | PASS | 180Vac -->0Vac -10ms-0
608 | 12.81 | 11.59 | 12.225 | 12.205 | 12.6 | 11.4 | 12.051 | 12.043 | 3.46 | 2.5 | 3.264 | 3.271 | 3.46 | ********* | 3.26 | 0.06 | 3.46 | ********* | 3.26 | 3.258 | 180 | 47 | 500 | 10 | 500 | 0 | 47 | 45 | 100 | 90.09 | 1.75 | PASS | 180Vac -->0Vac - 10ms-45
610 | 12.81 | 11.59 | 12.224 | 12.204 | 12.6 | 11.4 | 12.052 | 12.044 | 3.46 | 2.5 | 3.264 | 3.271 | 3.46 | ********* | 3.26 | 0.06 | 3.46 | ********* | 3.26 | 3.258 | 180 | 47 | 500 | 10 | 500 | 0 | 47 | 90 | 100 | 90.09 | 1.75 | PASS | 180Vac -->0Vac - 10ms-90
612 | 12.81 | 11.59 | 12.225 | 12.205 | 12.6 | 11.4 | 12.052 | 12.043 | 3.46 | 2.5 | 3.265 | 3.271 | 3.46 | ********* | 3.259 | 0.061 | 3.46 | ********* | 3.26 | 3.259 | 180 | 47 | 500 | 10 | 500 | 0 | 47 | 135 | 100 | 90.09 | 1.75 | PASS | 180Vac -->0Vac - 10ms-135
614 | 12.81 | 11.59 | 12.225 | 12.205 | 12.6 | 11.4 | 12.051 | 12.042 | 3.46 | 2.5 | 3.266 | 3.272 | 3.46 | ********* | 3.259 | 0.059 | 3.46 | ********* | 3.26 | 3.26 | 180 | 47 | 500 | 10 | 500 | 0 | 47 | 225 | 100 | 90.09 | 1.75 | PASS | 180Vac -->0Vac - 10ms-225
616 | 12.81 | 11.59 | 12.225 | 12.205 | 12.6 | 11.4 | 12.051 | 12.044 | 3.46 | 2.5 | 3.264 | 3.271 | 3.46 | ********* | 3.259 | 0.058 | 3.46 | ********* | 3.26 | 3.258 | 180 | 47 | 500 | 10 | 500 | 0 | 47 | 270 | 100 | 90.09 | 1.75 | PASS | 180Vac -->0Vac - 10ms-270
618 | 12.81 | 11.59 | 12.224 | 12.205 | 12.6 | 11.4 | 12.05 | 12.043 | 3.46 | 2.5 | 3.265 | 3.272 | 3.46 | ********* | 3.259 | 0.061 | 3.46 | ********* | 3.26 | 3.258 | 180 | 47 | 500 | 10 | 500 | 0 | 47 | 315 | 100 | 90.09 | 1.75 | PASS | 180Vac -->0Vac - 10ms-315
623 | 12.81 | 11.59 | 12.217 | 12.197 | 12.6 | 11.4 | 12.049 | 12.041 | 3.46 | 2.5 | 3.263 | 3.269 | 3.46 | ********* | 3.256 | 0.058 | 3.46 | ********* | 3.26 | 3.259 | 200 | 50 | 3000 | 10 | 500 | 0 | 50 | 0 | 100 | 101.57 | 1.75 | PASS | 200Vac -->0Vac -10ms-0
625 | 12.81 | 11.59 | 12.217 | 12.197 | 12.6 | 11.4 | 12.051 | 12.043 | 3.46 | 2.5 | 3.263 | 3.269 | 3.46 | ********* | 3.256 | 0.056 | 3.46 | ********* | 3.26 | 3.258 | 200 | 50 | 500 | 10 | 500 | 0 | 50 | 45 | 100 | 101.57 | 1.75 | PASS | 200Vac -->0Vac - 10ms-45
627 | 12.81 | 11.59 | 12.217 | 12.198 | 12.6 | 11.4 | 12.05 | 12.042 | 3.46 | 2.5 | 3.263 | 3.27 | 3.46 | ********* | 3.257 | 0.06 | 3.46 | ********* | 3.26 | 3.26 | 200 | 50 | 500 | 10 | 500 | 0 | 50 | 90 | 100 | 101.57 | 1.75 | PASS | 200Vac -->0Vac - 10ms-90
629 | 12.81 | 11.59 | 12.218 | 12.198 | 12.6 | 11.4 | 12.05 | 12.043 | 3.46 | 2.5 | 3.263 | 3.271 | 3.46 | ********* | 3.257 | 0.058 | 3.46 | ********* | 3.26 | 3.26 | 200 | 50 | 500 | 10 | 500 | 0 | 50 | 135 | 100 | 101.57 | 1.75 | PASS | 200Vac -->0Vac - 10ms-135
631 | 12.81 | 11.59 | 12.217 | 12.198 | 12.6 | 11.4 | 12.05 | 12.042 | 3.46 | 2.5 | 3.263 | 3.271 | 3.46 | ********* | 3.256 | 0.056 | 3.46 | ********* | 3.26 | 3.259 | 200 | 50 | 500 | 10 | 500 | 0 | 50 | 225 | 100 | 101.57 | 1.75 | PASS | 200Vac -->0Vac - 10ms-225
633 | 12.81 | 11.59 | 12.217 | 12.2 | 12.6 | 11.4 | 12.05 | 12.042 | 3.46 | 2.5 | 3.263 | 3.27 | 3.46 | ********* | 3.257 | 0.056 | 3.46 | ********* | 3.26 | 3.258 | 200 | 50 | 500 | 10 | 500 | 0 | 50 | 270 | 100 | 101.57 | 1.75 | PASS | 200Vac -->0Vac - 10ms-270
635 | 12.81 | 11.59 | 12.218 | 12.197 | 12.6 | 11.4 | 12.049 | 12.043 | 3.46 | 2.5 | 3.263 | 3.27 | 3.46 | ********* | 3.257 | 0.055 | 3.46 | ********* | 3.26 | 3.259 | 200 | 50 | 500 | 10 | 500 | 0 | 50 | 315 | 100 | 101.57 | 1.75 | PASS | 200Vac -->0Vac - 10ms-315
640 | 12.81 | 11.59 | 12.209 | 12.19 | 12.6 | 11.4 | 12.049 | 12.04 | 3.46 | 2.5 | 3.262 | 3.269 | 3.46 | ********* | 3.255 | 0.056 | 3.46 | ********* | 3.26 | 3.257 | 220 | 50 | 3000 | 10 | 500 | 0 | 50 | 0 | 100 | 113.05 | 1.75 | PASS | 220Vac -->0Vac -10ms-0
642 | 12.81 | 11.59 | 12.21 | 12.19 | 12.6 | 11.4 | 12.047 | 12.04 | 3.46 | 2.5 | 3.261 | 3.27 | 3.46 | ********* | 3.253 | 0.055 | 3.46 | ********* | 3.262 | 3.259 | 220 | 50 | 500 | 10 | 500 | 0 | 50 | 45 | 100 | 113.05 | 1.75 | PASS | 220Vac -->0Vac - 10ms-45
644 | 12.81 | 11.59 | 12.209 | 12.191 | 12.6 | 11.4 | 12.049 | 12.041 | 3.46 | 2.5 | 3.262 | 3.268 | 3.46 | ********* | 3.255 | 0.052 | 3.46 | ********* | 3.262 | 3.26 | 220 | 50 | 500 | 10 | 500 | 0 | 50 | 90 | 100 | 113.05 | 1.75 | PASS | 220Vac -->0Vac - 10ms-90
646 | 12.81 | 11.59 | 12.21 | 12.19 | 12.6 | 11.4 | 12.05 | 12.041 | 3.46 | 2.5 | 3.261 | 3.269 | 3.46 | ********* | 3.254 | 0.056 | 3.46 | ********* | 3.262 | 3.26 | 220 | 50 | 500 | 10 | 500 | 0 | 50 | 135 | 100 | 113.05 | 1.75 | PASS | 220Vac -->0Vac - 10ms-135
648 | 12.81 | 11.59 | 12.21 | 12.191 | 12.6 | 11.4 | 12.049 | 12.042 | 3.46 | 2.5 | 3.261 | 3.268 | 3.46 | ********* | 3.254 | 0.054 | 3.46 | ********* | 3.263 | 3.261 | 220 | 50 | 500 | 10 | 500 | 0 | 50 | 225 | 100 | 113.05 | 1.75 | PASS | 220Vac -->0Vac - 10ms-225
650 | 12.81 | 11.59 | 12.21 | 12.19 | 12.6 | 11.4 | 12.049 | 12.041 | 3.46 | 2.5 | 3.261 | 3.269 | 3.46 | ********* | 3.254 | 0.056 | 3.46 | ********* | 3.262 | 3.26 | 220 | 50 | 500 | 10 | 500 | 0 | 50 | 270 | 100 | 113.05 | 1.75 | PASS | 220Vac -->0Vac - 10ms-270
652 | 12.81 | 11.59 | 12.211 | 12.19 | 12.6 | 11.4 | 12.049 | 12.04 | 3.46 | 2.5 | 3.261 | 3.268 | 3.46 | ********* | 3.255 | 0.056 | 3.46 | ********* | 3.26 | 3.26 | 220 | 50 | 500 | 10 | 500 | 0 | 50 | 315 | 100 | 113.05 | 1.75 | PASS | 220Vac -->0Vac - 10ms-315
657 | 12.81 | 11.59 | 12.21 | 12.189 | 12.6 | 11.4 | 12.049 | 12.038 | 3.46 | 2.5 | 3.26 | 3.268 | 3.46 | ********* | 3.254 | 0.056 | 3.46 | ********* | 3.26 | 3.26 | 264 | 63 | 3000 | 10 | 500 | 0 | 63 | 0 | 100 | 113.05 | 1.75 | PASS | 264Vac -->0Vac -10ms-0
659 | 12.81 | 11.59 | 12.209 | 12.19 | 12.6 | 11.4 | 12.049 | 12.041 | 3.46 | 2.5 | 3.261 | 3.268 | 3.46 | ********* | 3.255 | 0.055 | 3.46 | ********* | 3.26 | 3.26 | 264 | 63 | 500 | 10 | 500 | 0 | 63 | 45 | 100 | 113.05 | 1.75 | PASS | 264Vac -->0Vac - 10ms-45
661 | 12.81 | 11.59 | 12.209 | 12.19 | 12.6 | 11.4 | 12.049 | 12.041 | 3.46 | 2.5 | 3.26 | 3.268 | 3.46 | ********* | 3.253 | 0.055 | 3.46 | ********* | 3.262 | 3.26 | 264 | 63 | 500 | 10 | 500 | 0 | 63 | 90 | 100 | 113.05 | 1.75 | PASS | 264Vac -->0Vac - 10ms-90
663 | 12.81 | 11.59 | 12.209 | 12.191 | 12.6 | 11.4 | 12.049 | 12.041 | 3.46 | 2.5 | 3.26 | 3.268 | 3.46 | ********* | 3.254 | 0.056 | 3.46 | ********* | 3.26 | 3.26 | 264 | 63 | 500 | 10 | 500 | 0 | 63 | 135 | 100 | 113.05 | 1.75 | PASS | 264Vac -->0Vac - 10ms-135
665 | 12.81 | 11.59 | 12.21 | 12.19 | 12.6 | 11.4 | 12.049 | 12.04 | 3.46 | 2.5 | 3.261 | 3.269 | 3.46 | ********* | 3.255 | 0.052 | 3.46 | ********* | 3.26 | 3.26 | 264 | 63 | 500 | 10 | 500 | 0 | 63 | 225 | 100 | 113.05 | 1.75 | PASS | 264Vac -->0Vac - 10ms-225
667 | 12.81 | 11.59 | 12.209 | 12.191 | 12.6 | 11.4 | 12.049 | 12.041 | 3.46 | 2.5 | 3.261 | 3.27 | 3.46 | ********* | 3.254 | 0.054 | 3.46 | ********* | 3.262 | 3.26 | 264 | 63 | 500 | 10 | 500 | 0 | 63 | 270 | 100 | 113.05 | 1.75 | PASS | 264Vac -->0Vac - 10ms-270
669 | 12.81 | 11.59 | 12.209 | 12.19 | 12.6 | 11.4 | 12.047 | 12.04 | 3.46 | 2.5 | 3.261 | 3.268 | 3.46 | ********* | 3.254 | 0.054 | 3.46 | ********* | 3.26 | 3.26 | 264 | 63 | 500 | 10 | 500 | 0 | 63 | 315 | 100 | 113.05 | 1.75 | PASS | 264Vac -->0Vac - 10ms-315
754 | 12.81 | 11.59 | 12.229 | 12.207 | 12.6 | 11.4 | 12.053 | 12.042 | 3.46 | 2.5 | 3.264 | 3.271 | 3.46 | ********* | 3.259 | 0.057 | 3.46 | ********* | 3.26 | 3.26 | 164 | 30 | 3000 | 10 | 500 | 0 | 30 | 0 | 100 | 90.09 | 1.75 | PASS | DropOut H_164Vdc - 10ms
756 | 12.81 | 11.59 | 12.23 | 12.211 | 12.6 | 11.4 | 12.052 | 12.044 | 3.46 | 2.5 | 3.264 | 3.271 | 3.46 | ********* | 3.259 | 0.06 | 3.46 | ********* | 3.26 | 3.258 | 164 | 30 | 3000 | 10 | 500 | 0 | 30 | 0 | 100 | 90.09 | 1.75 | PASS | DropOut H_164Vdc - 10ms
758 | 12.81 | 11.59 | 12.23 | 12.209 | 12.6 | 11.4 | 12.052 | 12.044 | 3.46 | 2.5 | 3.264 | 3.272 | 3.46 | ********* | 3.257 | 0.058 | 3.46 | ********* | 3.259 | 3.258 | 164 | 30 | 3000 | 10 | 500 | 0 | 30 | 0 | 100 | 90.09 | 1.75 | PASS | DropOut H_164Vdc - 10ms
760 | 12.81 | 11.59 | 12.229 | 12.209 | 12.6 | 11.4 | 12.052 | 12.044 | 3.46 | 2.5 | 3.265 | 3.273 | 3.46 | ********* | 3.257 | 0.06 | 3.46 | ********* | 3.26 | 3.257 | 164 | 30 | 3000 | 10 | 500 | 0 | 30 | 0 | 100 | 90.09 | 1.75 | PASS | DropOut H_164Vdc - 10ms
762 | 12.81 | 11.59 | 12.229 | 12.209 | 12.6 | 11.4 | 12.052 | 12.044 | 3.46 | 2.5 | 3.265 | 3.271 | 3.46 | ********* | 3.259 | 0.056 | 3.46 | ********* | 3.26 | 3.259 | 164 | 30 | 3000 | 10 | 500 | 0 | 30 | 0 | 100 | 90.09 | 1.75 | PASS | DropOut H_164Vdc - 10ms
764 | 12.81 | 11.59 | 12.229 | 12.211 | 12.6 | 11.4 | 12.052 | 12.042 | 3.46 | 2.5 | 3.266 | 3.271 | 3.46 | ********* | 3.257 | 0.058 | 3.46 | ********* | 3.26 | 3.258 | 164 | 30 | 3000 | 10 | 500 | 0 | 30 | 0 | 100 | 90.09 | 1.75 | PASS | DropOut H_164Vdc - 10ms
766 | 12.81 | 11.59 | 12.228 | 12.209 | 12.6 | 11.4 | 12.05 | 12.042 | 3.46 | 2.5 | 3.265 | 3.271 | 3.46 | ********* | 3.257 | 0.058 | 3.46 | ********* | 3.26 | 3.259 | 164 | 30 | 3000 | 10 | 500 | 0 | 30 | 0 | 100 | 90.09 | 1.75 | PASS | DropOut H_164Vdc - 10ms
768 | 12.81 | 11.59 | 12.228 | 12.208 | 12.6 | 11.4 | 12.052 | 12.043 | 3.46 | 2.5 | 3.264 | 3.27 | 3.46 | ********* | 3.257 | 0.057 | 3.46 | ********* | 3.259 | 3.257 | 164 | 30 | 3000 | 10 | 500 | 0 | 30 | 0 | 100 | 90.09 | 1.75 | PASS | DropOut H_164Vdc - 10ms
770 | 12.81 | 11.59 | 12.229 | 12.208 | 12.6 | 11.4 | 12.051 | 12.043 | 3.46 | 2.5 | 3.265 | 3.271 | 3.46 | ********* | 3.257 | 0.056 | 3.46 | ********* | 3.26 | 3.258 | 164 | 30 | 3000 | 10 | 500 | 0 | 30 | 0 | 100 | 90.09 | 1.75 | PASS | DropOut H_164Vdc - 10ms
772 | 12.81 | 11.59 | 12.228 | 12.209 | 12.6 | 11.4 | 12.052 | 12.044 | 3.46 | 2.5 | 3.264 | 3.271 | 3.46 | ********* | 3.259 | 0.061 | 3.46 | ********* | 3.259 | 3.258 | 164 | 30 | 3000 | 10 | 500 | 0 | 30 | 0 | 100 | 90.09 | 1.75 | PASS | DropOut H_164Vdc - 10ms
782 | 12.81 | 11.59 | 12.221 | 12.2 | 12.6 | 11.4 | 12.051 | 12.04 | 3.46 | 2.5 | 3.263 | 3.27 | 3.46 | ********* | 3.257 | 0.057 | 3.46 | ********* | 3.26 | 3.258 | 200 | 30 | 3000 | 10 | 500 | 0 | 30 | 0 | 100 | 101.57 | 1.75 | PASS | DropOut H_200Vdc - 10ms
784 | 12.81 | 11.59 | 12.221 | 12.203 | 12.6 | 11.4 | 12.049 | 12.044 | 3.46 | 2.5 | 3.263 | 3.269 | 3.46 | ********* | 3.257 | 0.057 | 3.46 | ********* | 3.26 | 3.259 | 200 | 30 | 3000 | 10 | 500 | 0 | 30 | 0 | 100 | 101.57 | 1.75 | PASS | DropOut H_200Vdc - 10ms
786 | 12.81 | 11.59 | 12.221 | 12.204 | 12.6 | 11.4 | 12.049 | 12.042 | 3.46 | 2.5 | 3.263 | 3.27 | 3.46 | ********* | 3.256 | 0.057 | 3.46 | ********* | 3.26 | 3.259 | 200 | 30 | 3000 | 10 | 500 | 0 | 30 | 0 | 100 | 101.57 | 1.75 | PASS | DropOut H_200Vdc - 10ms
788 | 12.81 | 11.59 | 12.221 | 12.203 | 12.6 | 11.4 | 12.049 | 12.043 | 3.46 | 2.5 | 3.263 | 3.27 | 3.46 | ********* | 3.257 | 0.057 | 3.46 | ********* | 3.26 | 3.26 | 200 | 30 | 3000 | 10 | 500 | 0 | 30 | 0 | 100 | 101.57 | 1.75 | PASS | DropOut H_200Vdc - 10ms
790 | 12.81 | 11.59 | 12.221 | 12.202 | 12.6 | 11.4 | 12.05 | 12.044 | 3.46 | 2.5 | 3.263 | 3.27 | 3.46 | ********* | 3.256 | 0.055 | 3.46 | ********* | 3.26 | 3.26 | 200 | 30 | 3000 | 10 | 500 | 0 | 30 | 0 | 100 | 101.57 | 1.75 | PASS | DropOut H_200Vdc - 10ms
792 | 12.81 | 11.59 | 12.221 | 12.203 | 12.6 | 11.4 | 12.05 | 12.043 | 3.46 | 2.5 | 3.263 | 3.269 | 3.46 | ********* | 3.256 | 0.056 | 3.46 | ********* | 3.262 | 3.258 | 200 | 30 | 3000 | 10 | 500 | 0 | 30 | 0 | 100 | 101.57 | 1.75 | PASS | DropOut H_200Vdc - 10ms
794 | 12.81 | 11.59 | 12.221 | 12.202 | 12.6 | 11.4 | 12.05 | 12.044 | 3.46 | 2.5 | 3.263 | 3.27 | 3.46 | ********* | 3.257 | 0.058 | 3.46 | ********* | 3.26 | 3.26 | 200 | 30 | 3000 | 10 | 500 | 0 | 30 | 0 | 100 | 101.57 | 1.75 | PASS | DropOut H_200Vdc - 10ms
796 | 12.81 | 11.59 | 12.221 | 12.202 | 12.6 | 11.4 | 12.051 | 12.044 | 3.46 | 2.5 | 3.263 | 3.27 | 3.46 | ********* | 3.257 | 0.058 | 3.46 | ********* | 3.26 | 3.259 | 200 | 30 | 3000 | 10 | 500 | 0 | 30 | 0 | 100 | 101.57 | 1.75 | PASS | DropOut H_200Vdc - 10ms
798 | 12.81 | 11.59 | 12.223 | 12.201 | 12.6 | 11.4 | 12.05 | 12.044 | 3.46 | 2.5 | 3.263 | 3.27 | 3.46 | ********* | 3.257 | 0.057 | 3.46 | ********* | 3.262 | 3.26 | 200 | 30 | 3000 | 10 | 500 | 0 | 30 | 0 | 100 | 101.57 | 1.75 | PASS | DropOut H_200Vdc - 10ms
800 | 12.81 | 11.59 | 12.221 | 12.203 | 12.6 | 11.4 | 12.05 | 12.044 | 3.46 | 2.5 | 3.263 | 3.27 | 3.46 | ********* | 3.257 | 0.057 | 3.46 | ********* | 3.26 | 3.26 | 200 | 30 | 3000 | 10 | 500 | 0 | 30 | 0 | 100 | 101.57 | 1.75 | PASS | DropOut H_200Vdc - 10ms
805 | 12.81 | 11.59 | 12.215 | 12.196 | 12.6 | 11.4 | 12.049 | 12.04 | 3.46 | 2.5 | 3.261 | 3.268 | 3.46 | ********* | 3.254 | 0.055 | 3.46 | ********* | 3.262 | 3.26 | 220 | 30 | 3000 | 10 | 500 | 0 | 30 | 0 | 100 | 113.05 | 1.75 | PASS | DropOut H_220Vdc - 10ms
807 | 12.81 | 11.59 | 12.215 | 12.196 | 12.6 | 11.4 | 12.049 | 12.04 | 3.46 | 2.5 | 3.262 | 3.268 | 3.46 | ********* | 3.254 | 0.055 | 3.46 | ********* | 3.262 | 3.261 | 220 | 30 | 3000 | 10 | 500 | 0 | 30 | 0 | 100 | 113.05 | 1.75 | PASS | DropOut H_220Vdc - 10ms
809 | 12.81 | 11.59 | 12.215 | 12.194 | 12.6 | 11.4 | 12.049 | 12.042 | 3.46 | 2.5 | 3.261 | 3.266 | 3.46 | ********* | 3.254 | 0.053 | 3.46 | ********* | 3.26 | 3.258 | 220 | 30 | 3000 | 10 | 500 | 0 | 30 | 0 | 100 | 113.05 | 1.75 | PASS | DropOut H_220Vdc - 10ms
811 | 12.81 | 11.59 | 12.215 | 12.196 | 12.6 | 11.4 | 12.049 | 12.042 | 3.46 | 2.5 | 3.261 | 3.268 | 3.46 | ********* | 3.255 | 0.056 | 3.46 | ********* | 3.26 | 3.259 | 220 | 30 | 3000 | 10 | 500 | 0 | 30 | 0 | 100 | 113.05 | 1.75 | PASS | DropOut H_220Vdc - 10ms
813 | 12.81 | 11.59 | 12.215 | 12.194 | 12.6 | 11.4 | 12.049 | 12.04 | 3.46 | 2.5 | 3.262 | 3.268 | 3.46 | ********* | 3.255 | 0.056 | 3.46 | ********* | 3.26 | 3.258 | 220 | 30 | 3000 | 10 | 500 | 0 | 30 | 0 | 100 | 113.05 | 1.75 | PASS | DropOut H_220Vdc - 10ms
815 | 12.81 | 11.59 | 12.215 | 12.196 | 12.6 | 11.4 | 12.049 | 12.042 | 3.46 | 2.5 | 3.261 | 3.268 | 3.46 | ********* | 3.255 | 0.055 | 3.46 | ********* | 3.26 | 3.26 | 220 | 30 | 3000 | 10 | 500 | 0 | 30 | 0 | 100 | 113.05 | 1.75 | PASS | DropOut H_220Vdc - 10ms
817 | 12.81 | 11.59 | 12.215 | 12.194 | 12.6 | 11.4 | 12.049 | 12.042 | 3.46 | 2.5 | 3.262 | 3.268 | 3.46 | ********* | 3.254 | 0.056 | 3.46 | ********* | 3.26 | 3.26 | 220 | 30 | 3000 | 10 | 500 | 0 | 30 | 0 | 100 | 113.05 | 1.75 | PASS | DropOut H_220Vdc - 10ms
819 | 12.81 | 11.59 | 12.214 | 12.194 | 12.6 | 11.4 | 12.049 | 12.041 | 3.46 | 2.5 | 3.261 | 3.27 | 3.46 | ********* | 3.253 | 0.052 | 3.46 | ********* | 3.262 | 3.26 | 220 | 30 | 3000 | 10 | 500 | 0 | 30 | 0 | 100 | 113.05 | 1.75 | PASS | DropOut H_220Vdc - 10ms
821 | 12.81 | 11.59 | 12.214 | 12.194 | 12.6 | 11.4 | 12.049 | 12.042 | 3.46 | 2.5 | 3.26 | 3.27 | 3.46 | ********* | 3.253 | 0.055 | 3.46 | ********* | 3.26 | 3.258 | 220 | 30 | 3000 | 10 | 500 | 0 | 30 | 0 | 100 | 113.05 | 1.75 | PASS | DropOut H_220Vdc - 10ms
823 | 12.81 | 11.59 | 12.214 | 12.196 | 12.6 | 11.4 | 12.05 | 12.041 | 3.46 | 2.5 | 3.261 | 3.268 | 3.46 | ********* | 3.256 | 0.057 | 3.46 | ********* | 3.26 | 3.26 | 220 | 30 | 3000 | 10 | 500 | 0 | 30 | 0 | 100 | 113.05 | 1.75 | PASS | DropOut H_220Vdc - 10ms
828 | 12.81 | 11.59 | 12.213 | 12.194 | 12.6 | 11.4 | 12.049 | 12.04 | 3.46 | 2.5 | 3.26 | 3.269 | 3.46 | ********* | 3.255 | 0.056 | 3.46 | ********* | 3.262 | 3.26 | 300 | 30 | 3000 | 10 | 500 | 0 | 30 | 0 | 100 | 113.05 | 1.75 | PASS | DropOut H_300Vdc - 10ms
830 | 12.81 | 11.59 | 12.214 | 12.194 | 12.6 | 11.4 | 12.049 | 12.04 | 3.46 | 2.5 | 3.261 | 3.268 | 3.46 | ********* | 3.255 | 0.055 | 3.46 | ********* | 3.262 | 3.26 | 300 | 30 | 3000 | 10 | 500 | 0 | 30 | 0 | 100 | 113.05 | 1.75 | PASS | DropOut H_300Vdc - 10ms
832 | 12.81 | 11.59 | 12.213 | 12.193 | 12.6 | 11.4 | 12.049 | 12.041 | 3.46 | 2.5 | 3.261 | 3.268 | 3.46 | ********* | 3.255 | 0.054 | 3.46 | ********* | 3.262 | 3.26 | 300 | 30 | 3000 | 10 | 500 | 0 | 30 | 0 | 100 | 113.05 | 1.75 | PASS | DropOut H_300Vdc - 10ms
834 | 12.81 | 11.59 | 12.214 | 12.194 | 12.6 | 11.4 | 12.047 | 12.04 | 3.46 | 2.5 | 3.263 | 3.27 | 3.46 | ********* | 3.256 | 0.055 | 3.46 | ********* | 3.262 | 3.26 | 300 | 30 | 3000 | 10 | 500 | 0 | 30 | 0 | 100 | 113.05 | 1.75 | PASS | DropOut H_300Vdc - 10ms
836 | 12.81 | 11.59 | 12.215 | 12.194 | 12.6 | 11.4 | 12.049 | 12.041 | 3.46 | 2.5 | 3.262 | 3.268 | 3.46 | ********* | 3.254 | 0.053 | 3.46 | ********* | 3.26 | 3.261 | 300 | 30 | 3000 | 10 | 500 | 0 | 30 | 0 | 100 | 113.05 | 1.75 | PASS | DropOut H_300Vdc - 10ms
838 | 12.81 | 11.59 | 12.215 | 12.194 | 12.6 | 11.4 | 12.049 | 12.041 | 3.46 | 2.5 | 3.26 | 3.27 | 3.46 | ********* | 3.256 | 0.055 | 3.46 | ********* | 3.262 | 3.261 | 300 | 30 | 3000 | 10 | 500 | 0 | 30 | 0 | 100 | 113.05 | 1.75 | PASS | DropOut H_300Vdc - 10ms
840 | 12.81 | 11.59 | 12.214 | 12.193 | 12.6 | 11.4 | 12.049 | 12.04 | 3.46 | 2.5 | 3.26 | 3.269 | 3.46 | ********* | 3.254 | 0.056 | 3.46 | ********* | 3.26 | 3.26 | 300 | 30 | 3000 | 10 | 500 | 0 | 30 | 0 | 100 | 113.05 | 1.75 | PASS | DropOut H_300Vdc - 10ms
842 | 12.81 | 11.59 | 12.213 | 12.194 | 12.6 | 11.4 | 12.049 | 12.042 | 3.46 | 2.5 | 3.261 | 3.268 | 3.46 | ********* | 3.255 | 0.053 | 3.46 | ********* | 3.262 | 3.26 | 300 | 30 | 3000 | 10 | 500 | 0 | 30 | 0 | 100 | 113.05 | 1.75 | PASS | DropOut H_300Vdc - 10ms
844 | 12.81 | 11.59 | 12.214 | 12.196 | 12.6 | 11.4 | 12.049 | 12.04 | 3.46 | 2.5 | 3.263 | 3.268 | 3.46 | ********* | 3.255 | 0.053 | 3.46 | ********* | 3.262 | 3.261 | 300 | 30 | 3000 | 10 | 500 | 0 | 30 | 0 | 100 | 113.05 | 1.75 | PASS | DropOut H_300Vdc - 10ms
846 | 12.81 | 11.59 | 12.215 | 12.194 | 12.6 | 11.4 | 12.049 | 12.04 | 3.46 | 2.5 | 3.261 | 3.268 | 3.46 | ********* | 3.254 | 0.056 | 3.46 | ********* | 3.26 | 3.259 | 300 | 30 | 3000 | 10 | 500 | 0 | 30 | 0 | 100 | 113.05 | 1.75 | PASS | DropOut H_300Vdc - 10ms

## Sag_Surge
AC Line Sag Surge 80611N-2_Multi_S5
SEQ | SPEC_Max | SPEC_Min | Value1_H | Value1_L | SPEC_Max | SPEC_Min | Value2_H | Value2_L | SPEC_Max | SPEC_Min | Value3_H | Value3_L | SPEC_Max | SPEC_Min | Value4_H | Value4_L | SPEC_Max | SPEC_Min | Value5_H | Value5_L | Vin | Fin | DelayTime(ms) | DropTime(ms) | DropRecoveryTime(ms) | DropVoltage | DropFrequency | Degree | DutyCycle | Main_Load(A) | Vsb_Load(A) | Result | Ext
559 | ********* | ********* | 12.206 | 0.014 | ********* | ********* | 12.053 | 0.11 | ********* | ********* | 3.266 | 0.068 | ********* | ********* | 3.268 | 0.056 | ********* | ********* | 3.259 | 0.11 | 90 | 47 | 1000 | 5000 | 1000 | 0 | 47 | 0 | 100 | 71.3 | 2.5 | PASS | 90V-5S
562 | ********* | ********* | 12.176 | 0.014 | ********* | ********* | 12.041 | 0.108 | ********* | ********* | 3.252 | 0.052 | ********* | ********* | 3.266 | 0.038 | ********* | ********* | 3.265 | 0.11 | 264 | 63 | 3000 | 5000 | 1000 | 0 | 63 | 0 | 100 | 161.5 | 2.5 | PASS | 264V-5S
565 | 12.81 | 11.59 | 12.239 | 12.216 | 12.6 | 11.4 | 12.037 | 12.024 | 3.46 | 2.5 | 3.268 | 3.273 | 3.46 | 2.5 | 3.262 | 3.263 | 3.46 | 2.5 | 3.26 | 3.255 | 115 | 60 | 3000 | 15000 | 1000 | 97.75 | 50 | 0 | 100 | 71.3 | 2.5 | PASS | 115V-->97.75V -15S
567 | 12.81 | 11.59 | 12.233 | 12.209 | 12.6 | 11.4 | 12.036 | 12.024 | 3.46 | 2.5 | 3.267 | 3.272 | 3.46 | 2.5 | 3.26 | 3.26 | 3.46 | 2.5 | 3.26 | 3.256 | 115 | 60 | 3000 | 15000 | 1000 | 132.25 | 50 | 0 | 100 | 79.5 | 2.5 | PASS | 115V-->132.25V -15S
672 | 12.81 | 11.59 | 12.237 | 12.216 | 12.6 | 11.4 | 12.036 | 12.025 | 3.46 | 2.5 | 3.267 | 3.275 | 3.46 | 2.5 | 3.26 | 3.263 | 3.46 | 2.5 | 3.259 | 3.257 | 115 | 60 | 3000 | 10 | 1000 | 80.5 | 50 | 0 | 100 | 71.3 | 2.5 | PASS | 115Vac -->80.5Vac - 0.5 cycle
674 | 12.81 | 11.59 | 12.232 | 12.211 | 12.6 | 11.4 | 12.036 | 12.024 | 3.46 | 2.5 | 3.265 | 3.275 | 3.46 | 2.5 | 3.259 | 3.262 | 3.46 | 2.5 | 3.259 | 3.258 | 115 | 60 | 1000 | 10 | 1000 | 149.5 | 50 | 0 | 100 | 79.5 | 2.5 | PASS | 115Vac -->149.5Vac - 0.5 cycle
677 | 12.81 | 11.59 | 12.179 | 12.16 | 12.6 | 11.4 | 12.025 | 12.016 | 3.46 | 2.5 | 3.254 | 3.262 | 3.46 | 2.5 | 3.247 | 3.248 | 3.46 | 2.5 | 3.264 | 3.263 | 220 | 50 | 3000 | 100 | 500 | 253 | 50 | 0 | 100 | 161.5 | 2.5 | PASS | 220Vac -->253Vac - 100ms Max
679 | 12.81 | 11.59 | 12.178 | 12.157 | 12.6 | 11.4 | 12.025 | 12.016 | 3.46 | 2.5 | 3.253 | 3.263 | 3.46 | 2.5 | 3.247 | 3.25 | 3.46 | 2.5 | 3.264 | 3.262 | 220 | 50 | 500 | 10 | 500 | 286 | 50 | 0 | 100 | 161.5 | 2.5 | PASS | 220Vac -->286Vac - 0.5 Cycle Max
681 | 12.81 | 11.59 | 12.281 | 12.26 | 12.6 | 11.4 | 12.165 | 12.158 | 3.46 | 2.5 | 3.278 | 3.287 | 3.46 | 2.5 | 3.272 | 3.276 | 3.46 | 2.5 | 3.255 | 3.253 | 220 | 50 | 1000 | 100 | 500 | 253 | 50 | 0 | 100 | 1 | 0.1 | PASS | 220Vac -->253Vac - 100ms Min
683 | 12.81 | 11.59 | 12.283 | 12.259 | 12.6 | 11.4 | 12.161 | 12.157 | 3.46 | 2.5 | 3.278 | 3.286 | 3.46 | 2.5 | 3.271 | 3.275 | 3.46 | 2.5 | 3.255 | 3.253 | 220 | 50 | 500 | 10 | 500 | 286 | 50 | 0 | 100 | 1 | 0.1 | PASS | 220Vac -->286Vac - 0.5 Cycle Min

## Accuracy
Input Output Accuracy Multi or Single_S3
SEQ | SPEC_Max | SPEC_Min | CH1_Value | SPEC_Max | SPEC_Min | CH2_Value | SPEC_Max | SPEC_Min | CH3_Value | SPEC_Max | SPEC_Min | CH4_Value | SPEC_Max | SPEC_Min | CH5_Value | SPEC_Max | SPEC_Min | CH6_Value | SPEC_Max | SPEC_Min | CH7_Value | Vin | Fin | Main_Load(A) | Vsb_Load(A) | Result | Ext
690 | 12.35 | 11.59 | 12.164 | 12.6 | 11.4 | 11.994 | 3.46 | 2.5 | 3.222 | 3.46 | 2.5 | 3.225 | 3.46 | 2.5 | 3.222 | 8.2 | 7.8 | 8.001 | 0.4 | ******* | -0.022 | 230 | 50 | 161.5 | 2.5 | PASS | 230Vac-50Hz-100%
692 | 12.35 | 11.59 | 12.175 | 12.6 | 11.4 | 12.003 | 3.46 | 2.5 | 3.225 | 3.46 | 2.5 | 3.229 | 3.46 | 2.5 | 3.22 | ******* | ******* | 7.193 | 0.4 | ******* | -0.02 | 230 | 50 | 145.35 | 2.25 | PASS | 230Vac-50Hz-90%
694 | 12.35 | 11.59 | 12.185 | 12.6 | 11.4 | 12.011 | 3.46 | 2.5 | 3.225 | 3.46 | 2.5 | 3.229 | 3.46 | 2.5 | 3.223 | ******* | ******* | 6.385 | 0.4 | ******* | -0.017 | 230 | 50 | 129.2 | 2 | PASS | 230Vac-50Hz-80%
696 | 12.35 | 11.59 | 12.194 | 12.6 | 11.4 | 12.02 | 3.46 | 2.5 | 3.233 | 3.46 | 2.5 | 3.228 | 3.46 | 2.5 | 3.226 | ******* | ******* | 5.582 | 0.4 | ******* | -0.015 | 230 | 50 | 113.05 | 1.75 | PASS | 230Vac-50Hz-70%
698 | 12.35 | 11.59 | 12.204 | 12.6 | 11.4 | 12.029 | 3.46 | 2.5 | 3.234 | 3.46 | 2.5 | 3.235 | 3.46 | 2.5 | 3.219 | ******* | ******* | 4.782 | 0.4 | ******* | -0.012 | 230 | 50 | 96.9 | 1.5 | PASS | 230Vac-50Hz-60%
700 | 12.35 | 11.59 | 12.213 | 12.6 | 11.4 | 12.039 | 3.46 | 2.5 | 3.235 | 3.46 | 2.5 | 3.237 | 3.46 | 2.5 | 3.217 | 4.2 | 3.8 | 3.999 | 0.4 | ******* | -0.01 | 230 | 50 | 80.75 | 1.25 | PASS | 230Vac-50Hz-50%
702 | 12.35 | 11.59 | 12.223 | 12.6 | 11.4 | 12.051 | 3.46 | 2.5 | 3.235 | 3.46 | 2.5 | 3.242 | 3.46 | 2.5 | 3.216 | ******* | ******* | 3.206 | 0.4 | ******* | -0.007 | 230 | 50 | 64.6 | 1 | PASS | 230Vac-50Hz-40%
704 | 12.35 | 11.59 | 12.233 | 12.6 | 11.4 | 12.064 | 3.46 | 2.5 | 3.238 | 3.46 | 2.5 | 3.244 | 3.46 | 2.5 | 3.215 | ******* | ******* | 2.405 | 0.4 | ******* | -0.005 | 230 | 50 | 48.45 | 0.75 | PASS | 230Vac-50Hz-30%
706 | 12.35 | 11.59 | 12.243 | 12.6 | 11.4 | 12.081 | 3.46 | 2.5 | 3.241 | 3.46 | 2.5 | 3.247 | 3.46 | 2.5 | 3.213 | 1.8 | 1.4 | 1.607 | 0.4 | ******* | -0.002 | 230 | 50 | 32.3 | 0.5 | PASS | 230Vac-50Hz-20%
708 | 12.35 | 11.59 | 12.253 | 12.6 | 11.4 | 12.107 | 3.46 | 2.5 | 3.242 | 3.46 | 2.5 | 3.249 | 3.46 | 2.5 | 3.214 | 1 | 0.6 | 0.81 | 0.4 | ******* | 0.001 | 230 | 50 | 16.15 | 0.25 | PASS | 230Vac-50Hz-10%
710 | 12.35 | 11.59 | 12.167 | 12.6 | 11.4 | 11.996 | 3.46 | 2.5 | 3.227 | 3.46 | 2.5 | 3.22 | 3.46 | 2.5 | 3.228 | 8.2 | 7.8 | 8.002 | 0.4 | ******* | -0.022 | 230 | 60 | 161.5 | 2.5 | PASS | 230Vac-60Hz-100%
711 | 12.35 | 11.59 | 12.176 | 12.6 | 11.4 | 12.003 | 3.46 | 2.5 | 3.227 | 3.46 | 2.5 | 3.228 | 3.46 | 2.5 | 3.22 | ******* | ******* | 7.194 | 0.4 | ******* | -0.019 | 230 | 60 | 145.35 | 2.25 | PASS | 230Vac-60Hz-90%
712 | 12.35 | 11.59 | 12.185 | 12.6 | 11.4 | 12.011 | 3.46 | 2.5 | 3.228 | 3.46 | 2.5 | 3.23 | 3.46 | 2.5 | 3.219 | ******* | ******* | 6.385 | 0.4 | ******* | -0.017 | 230 | 60 | 129.2 | 2 | PASS | 230Vac-60Hz-80%
713 | 12.35 | 11.59 | 12.195 | 12.6 | 11.4 | 12.02 | 3.46 | 2.5 | 3.228 | 3.46 | 2.5 | 3.232 | 3.46 | 2.5 | 3.222 | ******* | ******* | 5.582 | 0.4 | ******* | -0.015 | 230 | 60 | 113.05 | 1.75 | PASS | 230Vac-60Hz-70%
714 | 12.35 | 11.59 | 12.206 | 12.6 | 11.4 | 12.031 | 3.46 | 2.5 | 3.236 | 3.46 | 2.5 | 3.23 | 3.46 | 2.5 | 3.223 | ******* | ******* | 4.782 | 0.4 | ******* | -0.012 | 230 | 60 | 96.9 | 1.5 | PASS | 230Vac-60Hz-60%
715 | 12.35 | 11.59 | 12.213 | 12.6 | 11.4 | 12.04 | 3.46 | 2.5 | 3.234 | 3.46 | 2.5 | 3.237 | 3.46 | 2.5 | 3.221 | 4.2 | 3.8 | 4 | 0.4 | ******* | -0.01 | 230 | 60 | 80.75 | 1.25 | PASS | 230Vac-60Hz-50%
716 | 12.35 | 11.59 | 12.225 | 12.6 | 11.4 | 12.051 | 3.46 | 2.5 | 3.235 | 3.46 | 2.5 | 3.241 | 3.46 | 2.5 | 3.219 | ******* | ******* | 3.204 | 0.4 | ******* | -0.007 | 230 | 60 | 64.6 | 1 | PASS | 230Vac-60Hz-40%
717 | 12.35 | 11.59 | 12.233 | 12.6 | 11.4 | 12.065 | 3.46 | 2.5 | 3.24 | 3.46 | 2.5 | 3.24 | 3.46 | 2.5 | 3.22 | ******* | ******* | 2.405 | 0.4 | ******* | -0.005 | 230 | 60 | 48.45 | 0.75 | PASS | 230Vac-60Hz-30%
718 | 12.35 | 11.59 | 12.242 | 12.6 | 11.4 | 12.081 | 3.46 | 2.5 | 3.241 | 3.46 | 2.5 | 3.247 | 3.46 | 2.5 | 3.214 | 1.8 | 1.4 | 1.606 | 0.4 | ******* | -0.002 | 230 | 60 | 32.3 | 0.5 | PASS | 230Vac-60Hz-20%
719 | 12.35 | 11.59 | 12.252 | 12.6 | 11.4 | 12.107 | 3.46 | 2.5 | 3.247 | 3.46 | 2.5 | 3.246 | 3.46 | 2.5 | 3.218 | 1 | 0.6 | 0.81 | 0.4 | ******* | 0 | 230 | 60 | 16.15 | 0.25 | PASS | 230Vac-60Hz-10%
720 | 12.35 | 11.59 | 12.166 | 12.6 | 11.4 | 11.994 | 3.46 | 2.5 | 3.222 | 3.46 | 2.5 | 3.226 | 3.46 | 2.5 | 3.22 | 8.2 | 7.8 | 8.003 | 0.4 | ******* | -0.022 | 240 | 60 | 161.5 | 2.5 | PASS | 240Vac-60Hz-100%
721 | 12.35 | 11.59 | 12.175 | 12.6 | 11.4 | 12.002 | 3.46 | 2.5 | 3.226 | 3.46 | 2.5 | 3.228 | 3.46 | 2.5 | 3.219 | ******* | ******* | 7.19 | 0.4 | ******* | -0.02 | 240 | 60 | 145.35 | 2.25 | PASS | 240Vac-60Hz-90%
722 | 12.35 | 11.59 | 12.185 | 12.6 | 11.4 | 12.01 | 3.46 | 2.5 | 3.231 | 3.46 | 2.5 | 3.226 | 3.46 | 2.5 | 3.22 | ******* | ******* | 6.388 | 0.4 | ******* | -0.017 | 240 | 60 | 129.2 | 2 | PASS | 240Vac-60Hz-80%
723 | 12.35 | 11.59 | 12.194 | 12.6 | 11.4 | 12.02 | 3.46 | 2.5 | 3.233 | 3.46 | 2.5 | 3.227 | 3.46 | 2.5 | 3.225 | ******* | ******* | 5.581 | 0.4 | ******* | -0.015 | 240 | 60 | 113.05 | 1.75 | PASS | 240Vac-60Hz-70%
724 | 12.35 | 11.59 | 12.205 | 12.6 | 11.4 | 12.029 | 3.46 | 2.5 | 3.232 | 3.46 | 2.5 | 3.237 | 3.46 | 2.5 | 3.221 | ******* | ******* | 4.783 | 0.4 | ******* | -0.012 | 240 | 60 | 96.9 | 1.5 | PASS | 240Vac-60Hz-60%
725 | 12.35 | 11.59 | 12.214 | 12.6 | 11.4 | 12.04 | 3.46 | 2.5 | 3.239 | 3.46 | 2.5 | 3.233 | 3.46 | 2.5 | 3.217 | 4.2 | 3.8 | 4 | 0.4 | ******* | -0.01 | 240 | 60 | 80.75 | 1.25 | PASS | 240Vac-60Hz-50%
726 | 12.35 | 11.59 | 12.224 | 12.6 | 11.4 | 12.051 | 3.46 | 2.5 | 3.24 | 3.46 | 2.5 | 3.236 | 3.46 | 2.5 | 3.223 | ******* | ******* | 3.206 | 0.4 | ******* | -0.007 | 240 | 60 | 64.6 | 1 | PASS | 240Vac-60Hz-40%
727 | 12.35 | 11.59 | 12.233 | 12.6 | 11.4 | 12.065 | 3.46 | 2.5 | 3.242 | 3.46 | 2.5 | 3.238 | 3.46 | 2.5 | 3.222 | ******* | ******* | 2.406 | 0.4 | ******* | -0.004 | 240 | 60 | 48.45 | 0.75 | PASS | 240Vac-60Hz-30%
728 | 12.35 | 11.59 | 12.243 | 12.6 | 11.4 | 12.082 | 3.46 | 2.5 | 3.247 | 3.46 | 2.5 | 3.24 | 3.46 | 2.5 | 3.22 | 1.8 | 1.4 | 1.606 | 0.4 | ******* | -0.002 | 240 | 60 | 32.3 | 0.5 | PASS | 240Vac-60Hz-20%
729 | 12.35 | 11.59 | 12.252 | 12.6 | 11.4 | 12.108 | 3.46 | 2.5 | 3.242 | 3.46 | 2.5 | 3.249 | 3.46 | 2.5 | 3.214 | 1 | 0.6 | 0.811 | 0.4 | ******* | 0 | 240 | 60 | 16.15 | 0.25 | PASS | 240Vac-60Hz-10%
730 | 12.35 | 11.59 | 12.215 | 12.6 | 11.4 | 12.005 | 3.46 | 2.5 | 3.238 | 3.46 | 2.5 | 3.233 | 3.46 | 2.5 | 3.219 | ******* | ******* | 3.94 | 0.4 | ******* | -0.01 | 100 | 60 | 79.5 | 2.5 | PASS | 100Vac-60Hz-100%
732 | 12.35 | 11.59 | 12.219 | 12.6 | 11.4 | 12.011 | 3.46 | 2.5 | 3.24 | 3.46 | 2.5 | 3.235 | 3.46 | 2.5 | 3.219 | ******* | ******* | 3.544 | 0.4 | ******* | -0.009 | 100 | 60 | 71.55 | 2.25 | PASS | 100Vac-60Hz-90%
734 | 12.35 | 11.59 | 12.224 | 12.6 | 11.4 | 12.018 | 3.46 | 2.5 | 3.238 | 3.46 | 2.5 | 3.241 | 3.46 | 2.5 | 3.215 | ******* | ******* | 3.156 | 0.4 | ******* | -0.008 | 100 | 60 | 63.6 | 2 | PASS | 100Vac-60Hz-80%
736 | 12.35 | 11.59 | 12.229 | 12.6 | 11.4 | 12.027 | 3.46 | 2.5 | 3.236 | 3.46 | 2.5 | 3.241 | 3.46 | 2.5 | 3.217 | ******* | ******* | 2.759 | 0.4 | ******* | -0.006 | 100 | 60 | 55.65 | 1.75 | PASS | 100Vac-60Hz-70%
738 | 12.35 | 11.59 | 12.235 | 12.6 | 11.4 | 12.034 | 3.46 | 2.5 | 3.243 | 3.46 | 2.5 | 3.237 | 3.46 | 2.5 | 3.221 | ******* | ******* | 2.367 | 0.4 | ******* | -0.005 | 100 | 60 | 47.7 | 1.5 | PASS | 100Vac-60Hz-60%
740 | 12.35 | 11.59 | 12.239 | 12.6 | 11.4 | 12.043 | 3.46 | 2.5 | 3.245 | 3.46 | 2.5 | 3.238 | 3.46 | 2.5 | 3.221 | ******* | ******* | 1.973 | 0.4 | ******* | -0.004 | 100 | 60 | 39.75 | 1.25 | PASS | 100Vac-60Hz-50%
742 | 12.35 | 11.59 | 12.242 | 12.6 | 11.4 | 12.054 | 3.46 | 2.5 | 3.245 | 3.46 | 2.5 | 3.244 | 3.46 | 2.5 | 3.214 | ******* | ******* | 1.582 | 0.4 | ******* | -0.002 | 100 | 60 | 31.8 | 1 | PASS | 100Vac-60Hz-40%
744 | 12.35 | 11.59 | 12.247 | 12.6 | 11.4 | 12.068 | 3.46 | 2.5 | 3.243 | 3.46 | 2.5 | 3.247 | 3.46 | 2.5 | 3.213 | ******* | ******* | 1.19 | 0.4 | ******* | -0.001 | 100 | 60 | 23.85 | 0.75 | PASS | 100Vac-60Hz-30%
746 | 12.35 | 11.59 | 12.25 | 12.6 | 11.4 | 12.082 | 3.46 | 2.5 | 3.242 | 3.46 | 2.5 | 3.247 | 3.46 | 2.5 | 3.219 | ******* | ******* | 0.797 | 0.4 | ******* | 0 | 100 | 60 | 15.9 | 0.5 | PASS | 100Vac-60Hz-20%
748 | 12.35 | 11.59 | 12.256 | 12.6 | 11.4 | 12.105 | 3.46 | 2.5 | 3.249 | 3.46 | 2.5 | 3.243 | 3.46 | 2.5 | 3.22 | ******* | ******* | 0.407 | 0.4 | ******* | 0.002 | 100 | 60 | 7.95 | 0.25 | PASS | 100Vac-60Hz-10%
775 | 12.35 | 11.59 | 12.165 | 12.6 | 11.4 | 11.996 | 3.46 | 2.5 | 3.222 | 3.46 | 2.5 | 3.222 | 3.46 | 2.5 | 3.226 | 8.2 | 7.8 | 8.003 | 0.4 | ******* | -0.022 | 240 | 30 | 161.5 | 2.5 | PASS | 240Vdc-100%
776 | 12.35 | 11.59 | 12.213 | 12.6 | 11.4 | 12.04 | 3.46 | 2.5 | 3.238 | 3.46 | 2.5 | 3.235 | 3.46 | 2.5 | 3.22 | 4.2 | 3.8 | 4 | 0.4 | ******* | -0.01 | 240 | 30 | 80.75 | 1.25 | PASS | 240Vdc-50%
777 | 12.35 | 11.59 | 12.243 | 12.6 | 11.4 | 12.079 | 3.46 | 2.5 | 3.245 | 3.46 | 2.5 | 3.24 | 3.46 | 2.5 | 3.221 | 1.8 | 1.4 | 1.606 | 0.4 | ******* | -0.002 | 240 | 30 | 32.3 | 0.5 | FAIL | 240Vdc-20%
778 | 12.35 | 11.59 | 12.251 | 12.6 | 11.4 | 12.105 | 3.46 | 2.5 | 3.243 | 3.46 | 2.5 | 3.246 | 3.46 | 2.5 | 3.217 | 1 | 0.6 | 0.809 | 0.4 | ******* | 0 | 240 | 30 | 16.15 | 0.25 | PASS | 240Vdc-10%
---------------------------------------
Accuracy_Ripple_Main
SEQ | Vin | Fin | Main_Load(A) | Vsb_Load(A) | SPEC_Max | SPEC_Min | Value | Result | Ext
690 | 230 | 50 | 161.5 | 2.5 | 120 | 0 | 15.43 | PASS | 230Vac-50Hz-100%
692 | 230 | 50 | 145.35 | 2.25 | 120 | 0 | 14.72 | PASS | 230Vac-50Hz-90%
694 | 230 | 50 | 129.2 | 2 | 120 | 0 | 14.26 | PASS | 230Vac-50Hz-80%
696 | 230 | 50 | 113.05 | 1.75 | 120 | 0 | 12.57 | PASS | 230Vac-50Hz-70%
698 | 230 | 50 | 96.9 | 1.5 | 120 | 0 | 12.58 | PASS | 230Vac-50Hz-60%
700 | 230 | 50 | 80.75 | 1.25 | 120 | 0 | 9.22 | PASS | 230Vac-50Hz-50%
702 | 230 | 50 | 64.6 | 1 | 120 | 0 | 8.9 | PASS | 230Vac-50Hz-40%
704 | 230 | 50 | 48.45 | 0.75 | 120 | 0 | 8.32 | PASS | 230Vac-50Hz-30%
706 | 230 | 50 | 32.3 | 0.5 | 120 | 0 | 8.47 | PASS | 230Vac-50Hz-20%
708 | 230 | 50 | 16.15 | 0.25 | 120 | 0 | 23.08 | PASS | 230Vac-50Hz-10%
710 | 230 | 60 | 161.5 | 2.5 | 120 | 0 | 15.02 | PASS | 230Vac-60Hz-100%
711 | 230 | 60 | 145.35 | 2.25 | 120 | 0 | 14.29 | PASS | 230Vac-60Hz-90%
712 | 230 | 60 | 129.2 | 2 | 120 | 0 | 13.02 | PASS | 230Vac-60Hz-80%
713 | 230 | 60 | 113.05 | 1.75 | 120 | 0 | 13.57 | PASS | 230Vac-60Hz-70%
714 | 230 | 60 | 96.9 | 1.5 | 120 | 0 | 12.53 | PASS | 230Vac-60Hz-60%
715 | 230 | 60 | 80.75 | 1.25 | 120 | 0 | 10.17 | PASS | 230Vac-60Hz-50%
716 | 230 | 60 | 64.6 | 1 | 120 | 0 | 8.81 | PASS | 230Vac-60Hz-40%
717 | 230 | 60 | 48.45 | 0.75 | 120 | 0 | 8.41 | PASS | 230Vac-60Hz-30%
718 | 230 | 60 | 32.3 | 0.5 | 120 | 0 | 8.25 | PASS | 230Vac-60Hz-20%
719 | 230 | 60 | 16.15 | 0.25 | 120 | 0 | 21.51 | PASS | 230Vac-60Hz-10%
720 | 240 | 60 | 161.5 | 2.5 | 120 | 0 | 15.05 | PASS | 240Vac-60Hz-100%
721 | 240 | 60 | 145.35 | 2.25 | 120 | 0 | 14.41 | PASS | 240Vac-60Hz-90%
722 | 240 | 60 | 129.2 | 2 | 120 | 0 | 13.28 | PASS | 240Vac-60Hz-80%
723 | 240 | 60 | 113.05 | 1.75 | 120 | 0 | 13.17 | PASS | 240Vac-60Hz-70%
724 | 240 | 60 | 96.9 | 1.5 | 120 | 0 | 12.06 | PASS | 240Vac-60Hz-60%
725 | 240 | 60 | 80.75 | 1.25 | 120 | 0 | 9.25 | PASS | 240Vac-60Hz-50%
726 | 240 | 60 | 64.6 | 1 | 120 | 0 | 8.85 | PASS | 240Vac-60Hz-40%
727 | 240 | 60 | 48.45 | 0.75 | 120 | 0 | 8.37 | PASS | 240Vac-60Hz-30%
728 | 240 | 60 | 32.3 | 0.5 | 120 | 0 | 7.58 | PASS | 240Vac-60Hz-20%
729 | 240 | 60 | 16.15 | 0.25 | 120 | 0 | 23.6 | PASS | 240Vac-60Hz-10%
730 | 100 | 60 | 79.5 | 2.5 | 120 | 0 | 12.13 | PASS | 100Vac-60Hz-100%
732 | 100 | 60 | 71.55 | 2.25 | 120 | 0 | 11.95 | PASS | 100Vac-60Hz-90%
734 | 100 | 60 | 63.6 | 2 | 120 | 0 | 12.33 | PASS | 100Vac-60Hz-80%
736 | 100 | 60 | 55.65 | 1.75 | 120 | 0 | 11.48 | PASS | 100Vac-60Hz-70%
738 | 100 | 60 | 47.7 | 1.5 | 120 | 0 | 11.31 | PASS | 100Vac-60Hz-60%
740 | 100 | 60 | 39.75 | 1.25 | 120 | 0 | 10.94 | PASS | 100Vac-60Hz-50%
742 | 100 | 60 | 31.8 | 1 | 120 | 0 | 9.82 | PASS | 100Vac-60Hz-40%
744 | 100 | 60 | 23.85 | 0.75 | 120 | 0 | 10.05 | PASS | 100Vac-60Hz-30%
746 | 100 | 60 | 15.9 | 0.5 | 120 | 0 | 18.72 | PASS | 100Vac-60Hz-20%
748 | 100 | 60 | 7.95 | 0.25 | 120 | 0 | 9.81 | PASS | 100Vac-60Hz-10%
775 | 240 | 30 | 161.5 | 2.5 | 120 | 0 | 14.75 | PASS | 240Vdc-100%
776 | 240 | 30 | 80.75 | 1.25 | 120 | 0 | 9.2 | PASS | 240Vdc-50%
777 | 240 | 30 | 32.3 | 0.5 | 120 | 0 | 8.7 | FAIL | 240Vdc-20%
778 | 240 | 30 | 16.15 | 0.25 | 120 | 0 | 30.75 | PASS | 240Vdc-10%
---------------------------------------
Accuracy_Ripple_CH2
SEQ | Vin | Fin | Main_Load(A) | Vsb_Load(A) | SPEC_Max | SPEC_Min | Value | Result | Ext
690 | 230 | 50 | 161.5 | 2.5 | 120 | 0 | 16.05 | PASS | 230Vac-50Hz-100%
692 | 230 | 50 | 145.35 | 2.25 | 120 | 0 | 13.96 | PASS | 230Vac-50Hz-90%
694 | 230 | 50 | 129.2 | 2 | 120 | 0 | 13.19 | PASS | 230Vac-50Hz-80%
696 | 230 | 50 | 113.05 | 1.75 | 120 | 0 | 11.45 | PASS | 230Vac-50Hz-70%
698 | 230 | 50 | 96.9 | 1.5 | 120 | 0 | 8.69 | PASS | 230Vac-50Hz-60%
700 | 230 | 50 | 80.75 | 1.25 | 120 | 0 | 6.81 | PASS | 230Vac-50Hz-50%
702 | 230 | 50 | 64.6 | 1 | 120 | 0 | 5.53 | PASS | 230Vac-50Hz-40%
704 | 230 | 50 | 48.45 | 0.75 | 120 | 0 | 4.34 | PASS | 230Vac-50Hz-30%
706 | 230 | 50 | 32.3 | 0.5 | 120 | 0 | 3.57 | PASS | 230Vac-50Hz-20%
708 | 230 | 50 | 16.15 | 0.25 | 120 | 0 | 2.98 | PASS | 230Vac-50Hz-10%
710 | 230 | 60 | 161.5 | 2.5 | 120 | 0 | 15.15 | PASS | 230Vac-60Hz-100%
711 | 230 | 60 | 145.35 | 2.25 | 120 | 0 | 14.23 | PASS | 230Vac-60Hz-90%
712 | 230 | 60 | 129.2 | 2 | 120 | 0 | 13.2 | PASS | 230Vac-60Hz-80%
713 | 230 | 60 | 113.05 | 1.75 | 120 | 0 | 11.63 | PASS | 230Vac-60Hz-70%
714 | 230 | 60 | 96.9 | 1.5 | 120 | 0 | 8.59 | PASS | 230Vac-60Hz-60%
715 | 230 | 60 | 80.75 | 1.25 | 120 | 0 | 6.66 | PASS | 230Vac-60Hz-50%
716 | 230 | 60 | 64.6 | 1 | 120 | 0 | 5.7 | PASS | 230Vac-60Hz-40%
717 | 230 | 60 | 48.45 | 0.75 | 120 | 0 | 4.54 | PASS | 230Vac-60Hz-30%
718 | 230 | 60 | 32.3 | 0.5 | 120 | 0 | 3.86 | PASS | 230Vac-60Hz-20%
719 | 230 | 60 | 16.15 | 0.25 | 120 | 0 | 3.13 | PASS | 230Vac-60Hz-10%
720 | 240 | 60 | 161.5 | 2.5 | 120 | 0 | 15.43 | PASS | 240Vac-60Hz-100%
721 | 240 | 60 | 145.35 | 2.25 | 120 | 0 | 14.35 | PASS | 240Vac-60Hz-90%
722 | 240 | 60 | 129.2 | 2 | 120 | 0 | 13.29 | PASS | 240Vac-60Hz-80%
723 | 240 | 60 | 113.05 | 1.75 | 120 | 0 | 11.52 | PASS | 240Vac-60Hz-70%
724 | 240 | 60 | 96.9 | 1.5 | 120 | 0 | 8.58 | PASS | 240Vac-60Hz-60%
725 | 240 | 60 | 80.75 | 1.25 | 120 | 0 | 6.82 | PASS | 240Vac-60Hz-50%
726 | 240 | 60 | 64.6 | 1 | 120 | 0 | 5.34 | PASS | 240Vac-60Hz-40%
727 | 240 | 60 | 48.45 | 0.75 | 120 | 0 | 4.36 | PASS | 240Vac-60Hz-30%
728 | 240 | 60 | 32.3 | 0.5 | 120 | 0 | 3.73 | PASS | 240Vac-60Hz-20%
729 | 240 | 60 | 16.15 | 0.25 | 120 | 0 | 3.12 | PASS | 240Vac-60Hz-10%
730 | 100 | 60 | 79.5 | 2.5 | 120 | 0 | 13.65 | PASS | 100Vac-60Hz-100%
732 | 100 | 60 | 71.55 | 2.25 | 120 | 0 | 12.9 | PASS | 100Vac-60Hz-90%
734 | 100 | 60 | 63.6 | 2 | 120 | 0 | 12.31 | PASS | 100Vac-60Hz-80%
736 | 100 | 60 | 55.65 | 1.75 | 120 | 0 | 11.74 | PASS | 100Vac-60Hz-70%
738 | 100 | 60 | 47.7 | 1.5 | 120 | 0 | 9.96 | PASS | 100Vac-60Hz-60%
740 | 100 | 60 | 39.75 | 1.25 | 120 | 0 | 7.08 | PASS | 100Vac-60Hz-50%
742 | 100 | 60 | 31.8 | 1 | 120 | 0 | 5.37 | PASS | 100Vac-60Hz-40%
744 | 100 | 60 | 23.85 | 0.75 | 120 | 0 | 4.66 | PASS | 100Vac-60Hz-30%
746 | 100 | 60 | 15.9 | 0.5 | 120 | 0 | 3.92 | PASS | 100Vac-60Hz-20%
748 | 100 | 60 | 7.95 | 0.25 | 120 | 0 | 3.01 | PASS | 100Vac-60Hz-10%
775 | 240 | 30 | 161.5 | 2.5 | 120 | 0 | 15.88 | PASS | 240Vdc-100%
776 | 240 | 30 | 80.75 | 1.25 | 120 | 0 | 10.63 | PASS | 240Vdc-50%
777 | 240 | 30 | 32.3 | 0.5 | 120 | 0 | 5.85 | FAIL | 240Vdc-20%
778 | 240 | 30 | 16.15 | 0.25 | 120 | 0 | 4.35 | PASS | 240Vdc-10%
---------------------------------------
PF
SEQ | Vin | Fin | Main_Load(A) | Vsb_Load(A) | SPEC_Max | SPEC_Min | Value | Result | Ext
690 | 230 | 50 | 161.5 | 2.5 | 1 | 0.99 | 0.9984 | PASS | 230Vac-50Hz-100%
692 | 230 | 50 | 145.35 | 2.25 | 1 | 0.98 | 0.9984 | PASS | 230Vac-50Hz-90%
694 | 230 | 50 | 129.2 | 2 | 1 | 0.98 | 0.9987 | PASS | 230Vac-50Hz-80%
696 | 230 | 50 | 113.05 | 1.75 | 1 | 0.98 | 0.9987 | PASS | 230Vac-50Hz-70%
698 | 230 | 50 | 96.9 | 1.5 | 1 | 0.98 | 0.9986 | PASS | 230Vac-50Hz-60%
700 | 230 | 50 | 80.75 | 1.25 | 1 | 0.98 | 0.9977 | PASS | 230Vac-50Hz-50%
702 | 230 | 50 | 64.6 | 1 | 1 | 0.96 | 0.9967 | PASS | 230Vac-50Hz-40%
704 | 230 | 50 | 48.45 | 0.75 | 1 | 0.96 | 0.9947 | PASS | 230Vac-50Hz-30%
706 | 230 | 50 | 32.3 | 0.5 | 1 | 0.96 | 0.9927 | PASS | 230Vac-50Hz-20%
708 | 230 | 50 | 16.15 | 0.25 | 1 | 0.9 | 0.9835 | PASS | 230Vac-50Hz-10%
710 | 230 | 60 | 161.5 | 2.5 | 1 | 0.99 | 0.9982 | PASS | 230Vac-60Hz-100%
711 | 230 | 60 | 145.35 | 2.25 | 1 | 0.98 | 0.9983 | PASS | 230Vac-60Hz-90%
712 | 230 | 60 | 129.2 | 2 | 1 | 0.98 | 0.9986 | PASS | 230Vac-60Hz-80%
713 | 230 | 60 | 113.05 | 1.75 | 1 | 0.98 | 0.9986 | PASS | 230Vac-60Hz-70%
714 | 230 | 60 | 96.9 | 1.5 | 1 | 0.98 | 0.9985 | PASS | 230Vac-60Hz-60%
715 | 230 | 60 | 80.75 | 1.25 | 1 | 0.98 | 0.9973 | PASS | 230Vac-60Hz-50%
716 | 230 | 60 | 64.6 | 1 | 1 | 0.96 | 0.9961 | PASS | 230Vac-60Hz-40%
717 | 230 | 60 | 48.45 | 0.75 | 1 | 0.96 | 0.9934 | PASS | 230Vac-60Hz-30%
718 | 230 | 60 | 32.3 | 0.5 | 1 | 0.96 | 0.9909 | PASS | 230Vac-60Hz-20%
719 | 230 | 60 | 16.15 | 0.25 | 1 | 0.9 | 0.9782 | PASS | 230Vac-60Hz-10%
720 | 240 | 60 | 161.5 | 2.5 | 1 | ******** | 0.9976 | PASS | 240Vac-60Hz-100%
721 | 240 | 60 | 145.35 | 2.25 | 1 | ******** | 0.9983 | PASS | 240Vac-60Hz-90%
722 | 240 | 60 | 129.2 | 2 | 1 | ******** | 0.9985 | PASS | 240Vac-60Hz-80%
723 | 240 | 60 | 113.05 | 1.75 | 1 | ******** | 0.9984 | PASS | 240Vac-60Hz-70%
724 | 240 | 60 | 96.9 | 1.5 | 1 | ******** | 0.9982 | PASS | 240Vac-60Hz-60%
725 | 240 | 60 | 80.75 | 1.25 | 1 | ******** | 0.9968 | PASS | 240Vac-60Hz-50%
726 | 240 | 60 | 64.6 | 1 | 1 | ******** | 0.9952 | PASS | 240Vac-60Hz-40%
727 | 240 | 60 | 48.45 | 0.75 | 1 | ******** | 0.9925 | PASS | 240Vac-60Hz-30%
728 | 240 | 60 | 32.3 | 0.5 | 1 | ******** | 0.9891 | PASS | 240Vac-60Hz-20%
729 | 240 | 60 | 16.15 | 0.25 | 1 | ******** | 0.973 | PASS | 240Vac-60Hz-10%
730 | 100 | 60 | 79.5 | 2.5 | 1 | ******** | 0.9994 | PASS | 100Vac-60Hz-100%
732 | 100 | 60 | 71.55 | 2.25 | 1 | ******** | 0.9995 | PASS | 100Vac-60Hz-90%
734 | 100 | 60 | 63.6 | 2 | 1 | ******** | 0.9995 | PASS | 100Vac-60Hz-80%
736 | 100 | 60 | 55.65 | 1.75 | 1 | ******** | 0.9995 | PASS | 100Vac-60Hz-70%
738 | 100 | 60 | 47.7 | 1.5 | 1 | ******** | 0.9995 | PASS | 100Vac-60Hz-60%
740 | 100 | 60 | 39.75 | 1.25 | 1 | ******** | 0.9995 | PASS | 100Vac-60Hz-50%
742 | 100 | 60 | 31.8 | 1 | 1 | ******** | 0.9995 | PASS | 100Vac-60Hz-40%
744 | 100 | 60 | 23.85 | 0.75 | 1 | ******** | 0.9993 | PASS | 100Vac-60Hz-30%
746 | 100 | 60 | 15.9 | 0.5 | 1 | ******** | 0.9986 | PASS | 100Vac-60Hz-20%
748 | 100 | 60 | 7.95 | 0.25 | 1 | ******** | 0.9939 | PASS | 100Vac-60Hz-10%
775 | 240 | 30 | 161.5 | 2.5 | 1 | ******** | 1 | PASS | 240Vdc-100%
776 | 240 | 30 | 80.75 | 1.25 | 1 | ******** | 1 | PASS | 240Vdc-50%
777 | 240 | 30 | 32.3 | 0.5 | 1 | ******** | 1 | FAIL | 240Vdc-20%
778 | 240 | 30 | 16.15 | 0.25 | 1 | ******** | 1 | PASS | 240Vdc-10%
---------------------------------------
THDi
SEQ | Vin | Fin | Main_Load(A) | Vsb_Load(A) | SPEC_Max | SPEC_Min | Value | Result | Ext
690 | 230 | 50 | 161.5 | 2.5 | 5 | * | 2.435 | PASS | 230Vac-50Hz-100%
692 | 230 | 50 | 145.35 | 2.25 | 8 | * | 2.459 | PASS | 230Vac-50Hz-90%
694 | 230 | 50 | 129.2 | 2 | 8 | * | 2.441 | PASS | 230Vac-50Hz-80%
696 | 230 | 50 | 113.05 | 1.75 | 8 | * | 2.428 | PASS | 230Vac-50Hz-70%
698 | 230 | 50 | 96.9 | 1.5 | 8 | * | 2.412 | PASS | 230Vac-50Hz-60%
700 | 230 | 50 | 80.75 | 1.25 | 8 | * | 2.771 | PASS | 230Vac-50Hz-50%
702 | 230 | 50 | 64.6 | 1 | 10 | * | 3.131 | PASS | 230Vac-50Hz-40%
704 | 230 | 50 | 48.45 | 0.75 | 10 | * | 3.572 | PASS | 230Vac-50Hz-30%
706 | 230 | 50 | 32.3 | 0.5 | 10 | * | 5.896 | PASS | 230Vac-50Hz-20%
708 | 230 | 50 | 16.15 | 0.25 | 20 | * | 7.37 | PASS | 230Vac-50Hz-10%
710 | 230 | 60 | 161.5 | 2.5 | 5 | * | 2.346 | PASS | 230Vac-60Hz-100%
711 | 230 | 60 | 145.35 | 2.25 | 8 | * | 2.208 | PASS | 230Vac-60Hz-90%
712 | 230 | 60 | 129.2 | 2 | 8 | * | 2.307 | PASS | 230Vac-60Hz-80%
713 | 230 | 60 | 113.05 | 1.75 | 8 | * | 2.114 | PASS | 230Vac-60Hz-70%
714 | 230 | 60 | 96.9 | 1.5 | 8 | * | 2.319 | PASS | 230Vac-60Hz-60%
715 | 230 | 60 | 80.75 | 1.25 | 8 | * | 2.485 | PASS | 230Vac-60Hz-50%
716 | 230 | 60 | 64.6 | 1 | 10 | * | 2.957 | PASS | 230Vac-60Hz-40%
717 | 230 | 60 | 48.45 | 0.75 | 10 | * | 3.484 | PASS | 230Vac-60Hz-30%
718 | 230 | 60 | 32.3 | 0.5 | 10 | * | 6.324 | PASS | 230Vac-60Hz-20%
719 | 230 | 60 | 16.15 | 0.25 | 20 | * | 8.065 | PASS | 230Vac-60Hz-10%
720 | 240 | 60 | 161.5 | 2.5 | ******** | * | 2.332 | PASS | 240Vac-60Hz-100%
721 | 240 | 60 | 145.35 | 2.25 | ******** | * | 2.195 | PASS | 240Vac-60Hz-90%
722 | 240 | 60 | 129.2 | 2 | ******** | * | 2.203 | PASS | 240Vac-60Hz-80%
723 | 240 | 60 | 113.05 | 1.75 | ******** | * | 2.153 | PASS | 240Vac-60Hz-70%
724 | 240 | 60 | 96.9 | 1.5 | ******** | * | 2.278 | PASS | 240Vac-60Hz-60%
725 | 240 | 60 | 80.75 | 1.25 | ******** | * | 2.663 | PASS | 240Vac-60Hz-50%
726 | 240 | 60 | 64.6 | 1 | ******** | * | 2.993 | PASS | 240Vac-60Hz-40%
727 | 240 | 60 | 48.45 | 0.75 | ******** | * | 3.428 | PASS | 240Vac-60Hz-30%
728 | 240 | 60 | 32.3 | 0.5 | ******** | * | 6.779 | PASS | 240Vac-60Hz-20%
729 | 240 | 60 | 16.15 | 0.25 | ******** | * | 8.82 | PASS | 240Vac-60Hz-10%
730 | 100 | 60 | 79.5 | 2.5 | ******** | * | 2.868 | PASS | 100Vac-60Hz-100%
732 | 100 | 60 | 71.55 | 2.25 | ******** | * | 2.742 | PASS | 100Vac-60Hz-90%
734 | 100 | 60 | 63.6 | 2 | ******** | * | 2.715 | PASS | 100Vac-60Hz-80%
736 | 100 | 60 | 55.65 | 1.75 | ******** | * | 2.875 | PASS | 100Vac-60Hz-70%
738 | 100 | 60 | 47.7 | 1.5 | ******** | * | 2.935 | PASS | 100Vac-60Hz-60%
740 | 100 | 60 | 39.75 | 1.25 | ******** | * | 2.762 | PASS | 100Vac-60Hz-50%
742 | 100 | 60 | 31.8 | 1 | ******** | * | 2.962 | PASS | 100Vac-60Hz-40%
744 | 100 | 60 | 23.85 | 0.75 | ******** | * | 3.335 | PASS | 100Vac-60Hz-30%
746 | 100 | 60 | 15.9 | 0.5 | ******** | * | 4.234 | PASS | 100Vac-60Hz-20%
748 | 100 | 60 | 7.95 | 0.25 | ******** | * | 5.919 | PASS | 100Vac-60Hz-10%
775 | 240 | 30 | 161.5 | 2.5 | ******** | * | 479.557 | PASS | 240Vdc-100%
776 | 240 | 30 | 80.75 | 1.25 | ******** | * | 1068.507 | PASS | 240Vdc-50%
777 | 240 | 30 | 32.3 | 0.5 | ******** | * | 776.902 | FAIL | 240Vdc-20%
778 | 240 | 30 | 16.15 | 0.25 | ******** | * | 2013.432 | PASS | 240Vdc-10%
---------------------------------------
EFF
SEQ | Vin | Fin | Main_Load(A) | Vsb_Load(A) | SPEC_Max | SPEC_Min | Value | Result | Ext
690 | 230 | 50 | 161.5 | 2.5 | 99 | 89 | 90.39 | PASS | 230Vac-50Hz-100%
692 | 230 | 50 | 145.35 | 2.25 | 99 | ******** | 90.771 | PASS | 230Vac-50Hz-90%
694 | 230 | 50 | 129.2 | 2 | 99 | ******** | 91.146 | PASS | 230Vac-50Hz-80%
696 | 230 | 50 | 113.05 | 1.75 | 99 | ******** | 91.49 | PASS | 230Vac-50Hz-70%
698 | 230 | 50 | 96.9 | 1.5 | 99 | ******** | 92.309 | PASS | 230Vac-50Hz-60%
700 | 230 | 50 | 80.75 | 1.25 | 99 | 92 | 93.239 | PASS | 230Vac-50Hz-50%
702 | 230 | 50 | 64.6 | 1 | 99 | ******** | 93.568 | PASS | 230Vac-50Hz-40%
704 | 230 | 50 | 48.45 | 0.75 | 99 | ******** | 93.552 | PASS | 230Vac-50Hz-30%
706 | 230 | 50 | 32.3 | 0.5 | 99 | 91 | 92.984 | PASS | 230Vac-50Hz-20%
708 | 230 | 50 | 16.15 | 0.25 | 99 | 88 | 90.891 | PASS | 230Vac-50Hz-10%
710 | 230 | 60 | 161.5 | 2.5 | 99 | 89 | 90.379 | PASS | 230Vac-60Hz-100%
711 | 230 | 60 | 145.35 | 2.25 | 99 | ******** | 90.79 | PASS | 230Vac-60Hz-90%
712 | 230 | 60 | 129.2 | 2 | 99 | ******** | 91.155 | PASS | 230Vac-60Hz-80%
713 | 230 | 60 | 113.05 | 1.75 | 99 | ******** | 91.557 | PASS | 230Vac-60Hz-70%
714 | 230 | 60 | 96.9 | 1.5 | 99 | ******** | 92.304 | PASS | 230Vac-60Hz-60%
715 | 230 | 60 | 80.75 | 1.25 | 99 | 92 | 93.245 | PASS | 230Vac-60Hz-50%
716 | 230 | 60 | 64.6 | 1 | 99 | ******** | 93.556 | PASS | 230Vac-60Hz-40%
717 | 230 | 60 | 48.45 | 0.75 | 99 | ******** | 93.548 | PASS | 230Vac-60Hz-30%
718 | 230 | 60 | 32.3 | 0.5 | 99 | 91 | 92.989 | PASS | 230Vac-60Hz-20%
719 | 230 | 60 | 16.15 | 0.25 | 99 | 88 | 90.878 | PASS | 230Vac-60Hz-10%
720 | 240 | 60 | 161.5 | 2.5 | ******** | ******** | 90.553 | PASS | 240Vac-60Hz-100%
721 | 240 | 60 | 145.35 | 2.25 | ******** | ******** | 90.929 | PASS | 240Vac-60Hz-90%
722 | 240 | 60 | 129.2 | 2 | ******** | ******** | 91.294 | PASS | 240Vac-60Hz-80%
723 | 240 | 60 | 113.05 | 1.75 | ******** | ******** | 91.633 | PASS | 240Vac-60Hz-70%
724 | 240 | 60 | 96.9 | 1.5 | ******** | ******** | 92.414 | PASS | 240Vac-60Hz-60%
725 | 240 | 60 | 80.75 | 1.25 | ******** | ******** | 93.342 | PASS | 240Vac-60Hz-50%
726 | 240 | 60 | 64.6 | 1 | ******** | ******** | 93.608 | PASS | 240Vac-60Hz-40%
727 | 240 | 60 | 48.45 | 0.75 | ******** | ******** | 93.612 | PASS | 240Vac-60Hz-30%
728 | 240 | 60 | 32.3 | 0.5 | ******** | ******** | 93.037 | PASS | 240Vac-60Hz-20%
729 | 240 | 60 | 16.15 | 0.25 | ******** | ******** | 90.923 | PASS | 240Vac-60Hz-10%
730 | 100 | 60 | 79.5 | 2.5 | ******** | ******** | 87.161 | PASS | 100Vac-60Hz-100%
732 | 100 | 60 | 71.55 | 2.25 | ******** | ******** | 87.468 | PASS | 100Vac-60Hz-90%
734 | 100 | 60 | 63.6 | 2 | ******** | ******** | 87.717 | PASS | 100Vac-60Hz-80%
736 | 100 | 60 | 55.65 | 1.75 | ******** | ******** | 87.81 | PASS | 100Vac-60Hz-70%
738 | 100 | 60 | 47.7 | 1.5 | ******** | ******** | 87.74 | PASS | 100Vac-60Hz-60%
740 | 100 | 60 | 39.75 | 1.25 | ******** | ******** | 88.733 | PASS | 100Vac-60Hz-50%
742 | 100 | 60 | 31.8 | 1 | ******** | ******** | 88.872 | PASS | 100Vac-60Hz-40%
744 | 100 | 60 | 23.85 | 0.75 | ******** | ******** | 89.326 | PASS | 100Vac-60Hz-30%
746 | 100 | 60 | 15.9 | 0.5 | ******** | ******** | 87.413 | PASS | 100Vac-60Hz-20%
748 | 100 | 60 | 7.95 | 0.25 | ******** | ******** | 84.42 | PASS | 100Vac-60Hz-10%
775 | 240 | 30 | 161.5 | 2.5 | 99 | 89 | 90.555 | PASS | 240Vdc-100%
776 | 240 | 30 | 80.75 | 1.25 | 99 | 92 | 92.271 | PASS | 240Vdc-50%
777 | 240 | 30 | 32.3 | 0.5 | 99 | 91 | 90.916 | FAIL | 240Vdc-20%
778 | 240 | 30 | 16.15 | 0.25 | 99 | 88 | 88.662 | PASS | 240Vdc-10%
---------------------------------------------
Accuracy_Vin
SEQ | Read_SPEC_Max | Read_SPEC_Min | Read_Value | MCU_Value | VS_SPEC_Max | VS_SPEC_Min | VS_MCU | Vin | Fin | Main_Load(A) | Vsb_Load(A) | Result | Ext
690 | ******** | ******** | 229.5 | 228.75 | 2 | * | 0.327 | 230 | 50 | 161.5 | 2.5 | PASS | 230Vac-50Hz-100%
692 | ******** | ******** | 229.537 | 228.75 | 2 | * | 0.343 | 230 | 50 | 145.35 | 2.25 | PASS | 230Vac-50Hz-90%
694 | ******** | ******** | 229.618 | 229 | 2 | * | 0.269 | 230 | 50 | 129.2 | 2 | PASS | 230Vac-50Hz-80%
696 | ******** | ******** | 229.721 | 229.25 | 2 | * | 0.205 | 230 | 50 | 113.05 | 1.75 | PASS | 230Vac-50Hz-70%
698 | ******** | ******** | 229.775 | 229.5 | 2 | * | 0.12 | 230 | 50 | 96.9 | 1.5 | PASS | 230Vac-50Hz-60%
700 | ******** | ******** | 229.865 | 229.5 | 2 | * | 0.159 | 230 | 50 | 80.75 | 1.25 | PASS | 230Vac-50Hz-50%
702 | ******** | ******** | 229.934 | 229.75 | 2 | * | 0.08 | 230 | 50 | 64.6 | 1 | PASS | 230Vac-50Hz-40%
704 | ******** | ******** | 230.006 | 229.75 | 2 | * | 0.112 | 230 | 50 | 48.45 | 0.75 | PASS | 230Vac-50Hz-30%
706 | ******** | ******** | 230.129 | 230 | 2 | * | 0.056 | 230 | 50 | 32.3 | 0.5 | PASS | 230Vac-50Hz-20%
708 | ******** | ******** | 230.222 | 230.25 | 5 | * | 0.012 | 230 | 50 | 16.15 | 0.25 | PASS | 230Vac-50Hz-10%
710 | ******** | ******** | 229.448 | 228.75 | 2 | * | 0.304 | 230 | 60 | 161.5 | 2.5 | PASS | 230Vac-60Hz-100%
711 | ******** | ******** | 229.543 | 229 | 2 | * | 0.236 | 230 | 60 | 145.35 | 2.25 | PASS | 230Vac-60Hz-90%
712 | ******** | ******** | 229.636 | 229 | 2 | * | 0.277 | 230 | 60 | 129.2 | 2 | PASS | 230Vac-60Hz-80%
713 | ******** | ******** | 229.733 | 229.25 | 2 | * | 0.21 | 230 | 60 | 113.05 | 1.75 | PASS | 230Vac-60Hz-70%
714 | ******** | ******** | 229.808 | 229.5 | 2 | * | 0.134 | 230 | 60 | 96.9 | 1.5 | PASS | 230Vac-60Hz-60%
715 | ******** | ******** | 229.88 | 229.75 | 2 | * | 0.056 | 230 | 60 | 80.75 | 1.25 | PASS | 230Vac-60Hz-50%
716 | ******** | ******** | 229.966 | 229.75 | 2 | * | 0.094 | 230 | 60 | 64.6 | 1 | PASS | 230Vac-60Hz-40%
717 | ******** | ******** | 230.05 | 230 | 2 | * | 0.022 | 230 | 60 | 48.45 | 0.75 | PASS | 230Vac-60Hz-30%
718 | ******** | ******** | 230.132 | 230 | 2 | * | 0.058 | 230 | 60 | 32.3 | 0.5 | PASS | 230Vac-60Hz-20%
719 | ******** | ******** | 230.242 | 230.25 | 5 | * | 0.004 | 230 | 60 | 16.15 | 0.25 | PASS | 230Vac-60Hz-10%
720 | ******** | ******** | 239.459 | 238.75 | 2 | * | 0.296 | 240 | 60 | 161.5 | 2.5 | PASS | 240Vac-60Hz-100%
721 | ******** | ******** | 239.545 | 239 | 2 | * | 0.228 | 240 | 60 | 145.35 | 2.25 | PASS | 240Vac-60Hz-90%
722 | ******** | ******** | 239.636 | 239 | 2 | * | 0.265 | 240 | 60 | 129.2 | 2 | PASS | 240Vac-60Hz-80%
723 | ******** | ******** | 239.715 | 239.25 | 2 | * | 0.194 | 240 | 60 | 113.05 | 1.75 | PASS | 240Vac-60Hz-70%
724 | ******** | ******** | 239.784 | 239.5 | 2 | * | 0.118 | 240 | 60 | 96.9 | 1.5 | PASS | 240Vac-60Hz-60%
725 | ******** | ******** | 239.9 | 239.75 | 2 | * | 0.062 | 240 | 60 | 80.75 | 1.25 | PASS | 240Vac-60Hz-50%
726 | ******** | ******** | 240.011 | 240 | 2 | * | 0.004 | 240 | 60 | 64.6 | 1 | PASS | 240Vac-60Hz-40%
727 | ******** | ******** | 240.089 | 240 | 2 | * | 0.037 | 240 | 60 | 48.45 | 0.75 | PASS | 240Vac-60Hz-30%
728 | ******** | ******** | 240.166 | 240.25 | 2 | * | 0.035 | 240 | 60 | 32.3 | 0.5 | PASS | 240Vac-60Hz-20%
729 | ******** | ******** | 240.246 | 240.25 | 5 | * | 0.002 | 240 | 60 | 16.15 | 0.25 | PASS | 240Vac-60Hz-10%
730 | ******** | ******** | 99.152 | 98 | 2 | * | 1.162 | 100 | 60 | 79.5 | 2.5 | PASS | 100Vac-60Hz-100%
732 | ******** | ******** | 99.27 | 98.25 | 2 | * | 1.027 | 100 | 60 | 71.55 | 2.25 | PASS | 100Vac-60Hz-90%
734 | ******** | ******** | 99.395 | 98.375 | 2 | * | 1.026 | 100 | 60 | 63.6 | 2 | PASS | 100Vac-60Hz-80%
736 | ******** | ******** | 99.48 | 98.5 | 2 | * | 0.985 | 100 | 60 | 55.65 | 1.75 | PASS | 100Vac-60Hz-70%
738 | ******** | ******** | 99.584 | 98.75 | 2 | * | 0.837 | 100 | 60 | 47.7 | 1.5 | PASS | 100Vac-60Hz-60%
740 | ******** | ******** | 99.663 | 99.125 | 2 | * | 0.54 | 100 | 60 | 39.75 | 1.25 | PASS | 100Vac-60Hz-50%
742 | ******** | ******** | 99.751 | 99.25 | 2 | * | 0.502 | 100 | 60 | 31.8 | 1 | PASS | 100Vac-60Hz-40%
744 | ******** | ******** | 99.854 | 99.375 | 2 | * | 0.479 | 100 | 60 | 23.85 | 0.75 | PASS | 100Vac-60Hz-30%
746 | ******** | ******** | 99.972 | 99.625 | 2 | * | 0.348 | 100 | 60 | 15.9 | 0.5 | PASS | 100Vac-60Hz-20%
748 | ******** | ******** | 100.063 | 99.75 | 5 | * | 0.312 | 100 | 60 | 7.95 | 0.25 | PASS | 100Vac-60Hz-10%
775 | ******** | ******** | 239.587 | 240 | ******* | * | 0.172 | 240 | 30 | 161.5 | 2.5 | PASS | 240Vdc-100%
776 | ******** | ******** | 239.982 | 240.5 | ******* | * | 0.216 | 240 | 30 | 80.75 | 1.25 | PASS | 240Vdc-50%
777 | ******** | ******** | 240.194 | 240.5 | ******* | * | 0.127 | 240 | 30 | 32.3 | 0.5 | FAIL | 240Vdc-20%
778 | ******** | ******** | 240.264 | 240.75 | ******* | * | 0.202 | 240 | 30 | 16.15 | 0.25 | PASS | 240Vdc-10%
---------------------------------------------
Accuracy_Iin
SEQ | Read_SPEC_Max | Read_SPEC_Min | Read_Value | MCU_Value | VS_SPEC_Max | VS_SPEC_Min | VS_MCU | Vin | Fin | Main_Load(A) | Vsb_Load(A) | Result | Ext
690 | 10 | ******** | 9.63 | 9.656 | 2 | * | 0.276 | 230 | 50 | 161.5 | 2.5 | PASS | 230Vac-50Hz-100%
692 | ******** | ******** | 8.636 | 8.672 | 2 | * | 0.412 | 230 | 50 | 145.35 | 2.25 | PASS | 230Vac-50Hz-90%
694 | ******** | ******** | 7.646 | 7.68 | 2 | * | 0.434 | 230 | 50 | 129.2 | 2 | PASS | 230Vac-50Hz-80%
696 | ******** | ******** | 6.668 | 6.688 | 2 | * | 0.299 | 230 | 50 | 113.05 | 1.75 | PASS | 230Vac-50Hz-70%
698 | ******** | ******** | 5.668 | 5.695 | 2 | * | 0.477 | 230 | 50 | 96.9 | 1.5 | PASS | 230Vac-50Hz-60%
700 | ******** | ******** | 4.682 | 4.695 | 2 | * | 0.278 | 230 | 50 | 80.75 | 1.25 | PASS | 230Vac-50Hz-50%
702 | ******** | ******** | 3.738 | 3.75 | 2 | * | 0.312 | 230 | 50 | 64.6 | 1 | PASS | 230Vac-50Hz-40%
704 | ******** | ******** | 2.811 | 2.812 | 2 | * | 0.038 | 230 | 50 | 48.45 | 0.75 | PASS | 230Vac-50Hz-30%
706 | ******** | ******** | 1.89 | 1.887 | 2 | * | 0.167 | 230 | 50 | 32.3 | 0.5 | PASS | 230Vac-50Hz-20%
708 | ******** | ******** | 0.976 | 0.988 | 5 | * | 1.236 | 230 | 50 | 16.15 | 0.25 | PASS | 230Vac-50Hz-10%
710 | 10 | ******** | 9.637 | 9.656 | 2 | * | 0.201 | 230 | 60 | 161.5 | 2.5 | PASS | 230Vac-60Hz-100%
711 | ******** | ******** | 8.636 | 8.656 | 2 | * | 0.231 | 230 | 60 | 145.35 | 2.25 | PASS | 230Vac-60Hz-90%
712 | ******** | ******** | 7.646 | 7.664 | 2 | * | 0.242 | 230 | 60 | 129.2 | 2 | PASS | 230Vac-60Hz-80%
713 | ******** | ******** | 6.663 | 6.68 | 2 | * | 0.246 | 230 | 60 | 113.05 | 1.75 | PASS | 230Vac-60Hz-70%
714 | ******** | ******** | 5.669 | 5.688 | 2 | * | 0.319 | 230 | 60 | 96.9 | 1.5 | PASS | 230Vac-60Hz-60%
715 | ******** | ******** | 4.684 | 4.688 | 2 | * | 0.082 | 230 | 60 | 80.75 | 1.25 | PASS | 230Vac-60Hz-50%
716 | ******** | ******** | 3.741 | 3.742 | 2 | * | 0.027 | 230 | 60 | 64.6 | 1 | PASS | 230Vac-60Hz-40%
717 | ******** | ******** | 2.815 | 2.812 | 2 | * | 0.074 | 230 | 60 | 48.45 | 0.75 | PASS | 230Vac-60Hz-30%
718 | ******** | ******** | 1.893 | 1.885 | 2 | * | 0.444 | 230 | 60 | 32.3 | 0.5 | PASS | 230Vac-60Hz-20%
719 | ******** | ******** | 0.981 | 0.989 | 5 | * | 0.798 | 230 | 60 | 16.15 | 0.25 | PASS | 230Vac-60Hz-10%
720 | ******** | ******** | 9.221 | 9.234 | 2 | * | 0.144 | 240 | 60 | 161.5 | 2.5 | PASS | 240Vac-60Hz-100%
721 | ******** | ******** | 8.263 | 8.281 | 2 | * | 0.226 | 240 | 60 | 145.35 | 2.25 | PASS | 240Vac-60Hz-90%
722 | ******** | ******** | 7.317 | 7.336 | 2 | * | 0.264 | 240 | 60 | 129.2 | 2 | PASS | 240Vac-60Hz-80%
723 | ******** | ******** | 6.382 | 6.391 | 2 | * | 0.143 | 240 | 60 | 113.05 | 1.75 | PASS | 240Vac-60Hz-70%
724 | ******** | ******** | 5.428 | 5.445 | 2 | * | 0.31 | 240 | 60 | 96.9 | 1.5 | PASS | 240Vac-60Hz-60%
725 | ******** | ******** | 4.486 | 4.484 | 2 | * | 0.04 | 240 | 60 | 80.75 | 1.25 | PASS | 240Vac-60Hz-50%
726 | ******** | ******** | 3.586 | 3.582 | 2 | * | 0.099 | 240 | 60 | 64.6 | 1 | PASS | 240Vac-60Hz-40%
727 | ******** | ******** | 2.697 | 2.691 | 2 | * | 0.223 | 240 | 60 | 48.45 | 0.75 | PASS | 240Vac-60Hz-30%
728 | ******** | ******** | 1.816 | 1.807 | 2 | * | 0.54 | 240 | 60 | 32.3 | 0.5 | PASS | 240Vac-60Hz-20%
729 | ******** | ******** | 0.945 | 0.949 | 5 | * | 0.44 | 240 | 60 | 16.15 | 0.25 | PASS | 240Vac-60Hz-10%
730 | 13 | ******** | 11.591 | 11.625 | 2 | * | 0.294 | 100 | 60 | 79.5 | 2.5 | PASS | 100Vac-60Hz-100%
732 | ******** | ******** | 10.386 | 10.406 | 2 | * | 0.199 | 100 | 60 | 71.55 | 2.25 | PASS | 100Vac-60Hz-90%
734 | ******** | ******** | 9.197 | 9.219 | 2 | * | 0.237 | 100 | 60 | 63.6 | 2 | PASS | 100Vac-60Hz-80%
736 | ******** | ******** | 8.035 | 8.062 | 2 | * | 0.339 | 100 | 60 | 55.65 | 1.75 | PASS | 100Vac-60Hz-70%
738 | ******** | ******** | 6.889 | 6.883 | 2 | * | 0.095 | 100 | 60 | 47.7 | 1.5 | PASS | 100Vac-60Hz-60%
740 | ******** | ******** | 5.674 | 5.688 | 2 | * | 0.244 | 100 | 60 | 39.75 | 1.25 | PASS | 100Vac-60Hz-50%
742 | ******** | ******** | 4.53 | 4.547 | 2 | * | 0.384 | 100 | 60 | 31.8 | 1 | PASS | 100Vac-60Hz-40%
744 | ******** | ******** | 3.378 | 3.402 | 2 | * | 0.705 | 100 | 60 | 23.85 | 0.75 | PASS | 100Vac-60Hz-30%
746 | ******** | ******** | 2.301 | 2.316 | 2 | * | 0.668 | 100 | 60 | 15.9 | 0.5 | PASS | 100Vac-60Hz-20%
748 | ******** | ******** | 1.196 | 1.221 | 5 | * | 2.046 | 100 | 60 | 7.95 | 0.25 | PASS | 100Vac-60Hz-10%
775 | 9.3 | ******** | 9.193 | 9.203 | ******* | * | 0.106 | 240 | 30 | 161.5 | 2.5 | PASS | 240Vdc-100%
776 | ******** | ******** | 4.522 | 4.523 | ******* | * | 0.037 | 240 | 30 | 80.75 | 1.25 | PASS | 240Vdc-50%
777 | ******** | ******** | 1.838 | 1.826 | ******* | * | 0.666 | 240 | 30 | 32.3 | 0.5 | FAIL | 240Vdc-20%
778 | ******** | ******** | 0.943 | 0.936 | ******* | * | 0.781 | 240 | 30 | 16.15 | 0.25 | PASS | 240Vdc-10%
---------------------------------------------
Accuracy_Pin
SEQ | Read_SPEC_Max | Read_SPEC_Min | Read_Value | MCU_Value | VS_SPEC_Max | VS_SPEC_Min | VS_MCU | Vin | Fin | Main_Load(A) | Vsb_Load(A) | Result | Ext
690 | ******** | ******** | 2206.435 | 2216 | 2 | * | 0.434 | 230 | 50 | 161.5 | 2.5 | PASS | 230Vac-50Hz-100%
692 | ******** | ******** | 1979.258 | 1988 | 2 | * | 0.442 | 230 | 50 | 145.35 | 2.25 | PASS | 230Vac-50Hz-90%
694 | ******** | ******** | 1753.486 | 1758 | 2 | * | 0.257 | 230 | 50 | 129.2 | 2 | PASS | 230Vac-50Hz-80%
696 | ******** | ******** | 1529.726 | 1532 | 2 | * | 0.149 | 230 | 50 | 113.05 | 1.75 | PASS | 230Vac-50Hz-70%
698 | ******** | ******** | 1300.585 | 1306 | 2 | * | 0.416 | 230 | 50 | 96.9 | 1.5 | PASS | 230Vac-50Hz-60%
700 | ******** | ******** | 1073.79 | 1076 | 2 | * | 0.206 | 230 | 50 | 80.75 | 1.25 | PASS | 230Vac-50Hz-50%
702 | ******** | ******** | 856.738 | 860 | 2 | * | 0.381 | 230 | 50 | 64.6 | 1 | PASS | 230Vac-50Hz-40%
704 | ******** | ******** | 643.2 | 646 | 2 | * | 0.435 | 230 | 50 | 48.45 | 0.75 | PASS | 230Vac-50Hz-30%
706 | ******** | ******** | 431.754 | 431.5 | 2 | * | 0.059 | 230 | 50 | 32.3 | 0.5 | PASS | 230Vac-50Hz-20%
708 | ******** | ******** | 221.028 | 219.5 | 5 | * | 0.691 | 230 | 50 | 16.15 | 0.25 | PASS | 230Vac-50Hz-10%
710 | ******** | ******** | 2207.257 | 2204 | 2 | * | 0.148 | 230 | 60 | 161.5 | 2.5 | PASS | 230Vac-60Hz-100%
711 | ******** | ******** | 1979.085 | 1978 | 2 | * | 0.055 | 230 | 60 | 145.35 | 2.25 | PASS | 230Vac-60Hz-90%
712 | ******** | ******** | 1753.301 | 1752 | 2 | * | 0.074 | 230 | 60 | 129.2 | 2 | PASS | 230Vac-60Hz-80%
713 | ******** | ******** | 1528.702 | 1526 | 2 | * | 0.177 | 230 | 60 | 113.05 | 1.75 | PASS | 230Vac-60Hz-70%
714 | ******** | ******** | 1300.903 | 1300 | 2 | * | 0.069 | 230 | 60 | 96.9 | 1.5 | PASS | 230Vac-60Hz-60%
715 | ******** | ******** | 1073.793 | 1072 | 2 | * | 0.167 | 230 | 60 | 80.75 | 1.25 | PASS | 230Vac-60Hz-50%
716 | ******** | ******** | 856.949 | 857 | 2 | * | 0.006 | 230 | 60 | 64.6 | 1 | PASS | 230Vac-60Hz-40%
717 | ******** | ******** | 643.191 | 644 | 2 | * | 0.126 | 230 | 60 | 48.45 | 0.75 | PASS | 230Vac-60Hz-30%
718 | ******** | ******** | 431.702 | 430.5 | 2 | * | 0.278 | 230 | 60 | 32.3 | 0.5 | PASS | 230Vac-60Hz-20%
719 | ******** | ******** | 221.029 | 219 | 5 | * | 0.918 | 230 | 60 | 16.15 | 0.25 | PASS | 230Vac-60Hz-10%
720 | ******** | ******** | 2202.868 | 2204 | 2 | * | 0.051 | 240 | 60 | 161.5 | 2.5 | PASS | 240Vac-60Hz-100%
721 | ******** | ******** | 1975.824 | 1976 | 2 | * | 0.009 | 240 | 60 | 145.35 | 2.25 | PASS | 240Vac-60Hz-90%
722 | ******** | ******** | 1750.63 | 1750 | 2 | * | 0.036 | 240 | 60 | 129.2 | 2 | PASS | 240Vac-60Hz-80%
723 | ******** | ******** | 1527.349 | 1524 | 2 | * | 0.219 | 240 | 60 | 113.05 | 1.75 | PASS | 240Vac-60Hz-70%
724 | ******** | ******** | 1299.273 | 1300 | 2 | * | 0.056 | 240 | 60 | 96.9 | 1.5 | PASS | 240Vac-60Hz-60%
725 | ******** | ******** | 1072.732 | 1072 | 2 | * | 0.068 | 240 | 60 | 80.75 | 1.25 | PASS | 240Vac-60Hz-50%
726 | ******** | ******** | 856.423 | 857 | 2 | * | 0.067 | 240 | 60 | 64.6 | 1 | PASS | 240Vac-60Hz-40%
727 | ******** | ******** | 642.793 | 643 | 2 | * | 0.032 | 240 | 60 | 48.45 | 0.75 | PASS | 240Vac-60Hz-30%
728 | ******** | ******** | 431.509 | 430.5 | 2 | * | 0.234 | 240 | 60 | 32.3 | 0.5 | PASS | 240Vac-60Hz-20%
729 | ******** | ******** | 220.92 | 219 | 5 | * | 0.869 | 240 | 60 | 16.15 | 0.25 | PASS | 240Vac-60Hz-10%
730 | ******** | ******** | 1148.522 | 1140 | 2 | * | 0.742 | 100 | 60 | 79.5 | 2.5 | PASS | 100Vac-60Hz-100%
732 | ******** | ******** | 1030.424 | 1023 | 2 | * | 0.72 | 100 | 60 | 71.55 | 2.25 | PASS | 100Vac-60Hz-90%
734 | ******** | ******** | 913.658 | 907 | 2 | * | 0.729 | 100 | 60 | 63.6 | 2 | PASS | 100Vac-60Hz-80%
736 | ******** | ******** | 798.954 | 794 | 2 | * | 0.62 | 100 | 60 | 55.65 | 1.75 | PASS | 100Vac-60Hz-70%
738 | ******** | ******** | 685.691 | 680 | 2 | * | 0.83 | 100 | 60 | 47.7 | 1.5 | PASS | 100Vac-60Hz-60%
740 | ******** | ******** | 565.187 | 563 | 2 | * | 0.387 | 100 | 60 | 39.75 | 1.25 | PASS | 100Vac-60Hz-50%
742 | ******** | ******** | 451.582 | 451 | 2 | * | 0.129 | 100 | 60 | 31.8 | 1 | PASS | 100Vac-60Hz-40%
744 | ******** | ******** | 337.108 | 338 | 2 | * | 0.265 | 100 | 60 | 23.85 | 0.75 | PASS | 100Vac-60Hz-30%
746 | ******** | ******** | 229.707 | 230.25 | 2 | * | 0.236 | 100 | 60 | 15.9 | 0.5 | PASS | 100Vac-60Hz-20%
748 | ******** | ******** | 118.972 | 121.25 | 5 | * | 1.915 | 100 | 60 | 7.95 | 0.25 | PASS | 100Vac-60Hz-10%
775 | ******** | ******** | 2202.574 | 2208 | ******* | * | 0.246 | 240 | 30 | 161.5 | 2.5 | PASS | 240Vdc-100%
776 | ******** | ******** | 1085.123 | 1086 | ******* | * | 0.081 | 240 | 30 | 80.75 | 1.25 | PASS | 240Vdc-50%
777 | ******** | ******** | 441.572 | 439.5 | ******* | * | 0.469 | 240 | 30 | 32.3 | 0.5 | FAIL | 240Vdc-20%
778 | ******** | ******** | 226.543 | 224.75 | ******* | * | 0.791 | 240 | 30 | 16.15 | 0.25 | PASS | 240Vdc-10%
---------------------------------------------
Accuracy_Vout
SEQ | Read_SPEC_Max | Read_SPEC_Min | Read_Value | MCU_Value | VS_SPEC_Max | VS_SPEC_Min | VS_MCU | Vin | Fin | Main_Load(A) | Vsb_Load(A) | Result | Ext
690 | 12.35 | 11.59 | 12.164 | 12.201 | 2 | * | 0.307 | 230 | 50 | 161.5 | 2.5 | PASS | 230Vac-50Hz-100%
692 | 12.35 | 11.59 | 12.175 | 12.207 | 2 | * | 0.264 | 230 | 50 | 145.35 | 2.25 | PASS | 230Vac-50Hz-90%
694 | 12.35 | 11.59 | 12.185 | 12.213 | 2 | * | 0.232 | 230 | 50 | 129.2 | 2 | PASS | 230Vac-50Hz-80%
696 | 12.35 | 11.59 | 12.194 | 12.217 | 2 | * | 0.185 | 230 | 50 | 113.05 | 1.75 | PASS | 230Vac-50Hz-70%
698 | 12.35 | 11.59 | 12.204 | 12.223 | 2 | * | 0.154 | 230 | 50 | 96.9 | 1.5 | PASS | 230Vac-50Hz-60%
700 | 12.35 | 11.59 | 12.213 | 12.227 | 2 | * | 0.114 | 230 | 50 | 80.75 | 1.25 | PASS | 230Vac-50Hz-50%
702 | 12.35 | 11.59 | 12.223 | 12.232 | 2 | * | 0.077 | 230 | 50 | 64.6 | 1 | PASS | 230Vac-50Hz-40%
704 | 12.35 | 11.59 | 12.233 | 12.236 | 2 | * | 0.024 | 230 | 50 | 48.45 | 0.75 | PASS | 230Vac-50Hz-30%
706 | 12.35 | 11.59 | 12.243 | 12.242 | 2 | * | 0.007 | 230 | 50 | 32.3 | 0.5 | PASS | 230Vac-50Hz-20%
708 | 12.35 | 11.59 | 12.253 | 12.248 | 5 | * | 0.044 | 230 | 50 | 16.15 | 0.25 | PASS | 230Vac-50Hz-10%
710 | 12.35 | 11.59 | 12.167 | 12.201 | 2 | * | 0.282 | 230 | 60 | 161.5 | 2.5 | PASS | 230Vac-60Hz-100%
711 | 12.35 | 11.59 | 12.176 | 12.207 | 2 | * | 0.251 | 230 | 60 | 145.35 | 2.25 | PASS | 230Vac-60Hz-90%
712 | 12.35 | 11.59 | 12.185 | 12.213 | 2 | * | 0.232 | 230 | 60 | 129.2 | 2 | PASS | 230Vac-60Hz-80%
713 | 12.35 | 11.59 | 12.195 | 12.217 | 2 | * | 0.179 | 230 | 60 | 113.05 | 1.75 | PASS | 230Vac-60Hz-70%
714 | 12.35 | 11.59 | 12.206 | 12.223 | 2 | * | 0.136 | 230 | 60 | 96.9 | 1.5 | PASS | 230Vac-60Hz-60%
715 | 12.35 | 11.59 | 12.213 | 12.227 | 2 | * | 0.108 | 230 | 60 | 80.75 | 1.25 | PASS | 230Vac-60Hz-50%
716 | 12.35 | 11.59 | 12.225 | 12.232 | 2 | * | 0.064 | 230 | 60 | 64.6 | 1 | PASS | 230Vac-60Hz-40%
717 | 12.35 | 11.59 | 12.233 | 12.236 | 2 | * | 0.03 | 230 | 60 | 48.45 | 0.75 | PASS | 230Vac-60Hz-30%
718 | 12.35 | 11.59 | 12.242 | 12.242 | 2 | * | 0.001 | 230 | 60 | 32.3 | 0.5 | PASS | 230Vac-60Hz-20%
719 | 12.35 | 11.59 | 12.252 | 12.248 | 5 | * | 0.032 | 230 | 60 | 16.15 | 0.25 | PASS | 230Vac-60Hz-10%
720 | 12.35 | 11.59 | 12.166 | 12.201 | 2 | * | 0.289 | 240 | 60 | 161.5 | 2.5 | PASS | 240Vac-60Hz-100%
721 | 12.35 | 11.59 | 12.175 | 12.207 | 2 | * | 0.264 | 240 | 60 | 145.35 | 2.25 | PASS | 240Vac-60Hz-90%
722 | 12.35 | 11.59 | 12.185 | 12.213 | 2 | * | 0.232 | 240 | 60 | 129.2 | 2 | PASS | 240Vac-60Hz-80%
723 | 12.35 | 11.59 | 12.194 | 12.217 | 2 | * | 0.185 | 240 | 60 | 113.05 | 1.75 | PASS | 240Vac-60Hz-70%
724 | 12.35 | 11.59 | 12.205 | 12.223 | 2 | * | 0.142 | 240 | 60 | 96.9 | 1.5 | PASS | 240Vac-60Hz-60%
725 | 12.35 | 11.59 | 12.214 | 12.227 | 2 | * | 0.102 | 240 | 60 | 80.75 | 1.25 | PASS | 240Vac-60Hz-50%
726 | 12.35 | 11.59 | 12.224 | 12.232 | 2 | * | 0.071 | 240 | 60 | 64.6 | 1 | PASS | 240Vac-60Hz-40%
727 | 12.35 | 11.59 | 12.233 | 12.236 | 2 | * | 0.024 | 240 | 60 | 48.45 | 0.75 | PASS | 240Vac-60Hz-30%
728 | 12.35 | 11.59 | 12.243 | 12.242 | 2 | * | 0.007 | 240 | 60 | 32.3 | 0.5 | PASS | 240Vac-60Hz-20%
729 | 12.35 | 11.59 | 12.252 | 12.248 | 5 | * | 0.032 | 240 | 60 | 16.15 | 0.25 | PASS | 240Vac-60Hz-10%
730 | 12.35 | 11.59 | 12.215 | 12.228 | 2 | * | 0.111 | 100 | 60 | 79.5 | 2.5 | PASS | 100Vac-60Hz-100%
732 | 12.35 | 11.59 | 12.219 | 12.23 | 2 | * | 0.091 | 100 | 60 | 71.55 | 2.25 | PASS | 100Vac-60Hz-90%
734 | 12.35 | 11.59 | 12.224 | 12.232 | 2 | * | 0.071 | 100 | 60 | 63.6 | 2 | PASS | 100Vac-60Hz-80%
736 | 12.35 | 11.59 | 12.229 | 12.234 | 2 | * | 0.044 | 100 | 60 | 55.65 | 1.75 | PASS | 100Vac-60Hz-70%
738 | 12.35 | 11.59 | 12.235 | 12.238 | 2 | * | 0.028 | 100 | 60 | 47.7 | 1.5 | PASS | 100Vac-60Hz-60%
740 | 12.35 | 11.59 | 12.239 | 12.24 | 2 | * | 0.013 | 100 | 60 | 39.75 | 1.25 | PASS | 100Vac-60Hz-50%
742 | 12.35 | 11.59 | 12.242 | 12.242 | 2 | * | 0.001 | 100 | 60 | 31.8 | 1 | PASS | 100Vac-60Hz-40%
744 | 12.35 | 11.59 | 12.247 | 12.244 | 2 | * | 0.027 | 100 | 60 | 23.85 | 0.75 | PASS | 100Vac-60Hz-30%
746 | 12.35 | 11.59 | 12.25 | 12.248 | 2 | * | 0.02 | 100 | 60 | 15.9 | 0.5 | PASS | 100Vac-60Hz-20%
748 | 12.35 | 11.59 | 12.256 | 12.25 | 5 | * | 0.052 | 100 | 60 | 7.95 | 0.25 | PASS | 100Vac-60Hz-10%
775 | 12.35 | 11.59 | 12.165 | 12.201 | ******* | * | 0.301 | 240 | 30 | 161.5 | 2.5 | PASS | 240Vdc-100%
776 | 12.35 | 11.59 | 12.213 | 12.227 | ******* | * | 0.108 | 240 | 30 | 80.75 | 1.25 | PASS | 240Vdc-50%
777 | 12.35 | 11.59 | 12.243 | 12.242 | ******* | * | 0.007 | 240 | 30 | 32.3 | 0.5 | FAIL | 240Vdc-20%
778 | 12.35 | 11.59 | 12.251 | 12.248 | ******* | * | 0.026 | 240 | 30 | 16.15 | 0.25 | PASS | 240Vdc-10%
---------------------------------------------
Accuracy_Iout
SEQ | Read_SPEC_Max | Read_SPEC_Min | Read_Value | MCU_Value | VS_SPEC_Max | VS_SPEC_Min | VS_MCU | Vin | Fin | Main_Load(A) | Vsb_Load(A) | Result | Ext
690 | ******* | ******* | 161.497 | 161.25 | 2 | * | 0.153 | 230 | 50 | 161.5 | 2.5 | PASS | 230Vac-50Hz-100%
692 | ******* | ******* | 145.347 | 145.25 | 2 | * | 0.067 | 230 | 50 | 145.35 | 2.25 | PASS | 230Vac-50Hz-90%
694 | ******* | ******* | 129.197 | 129 | 2 | * | 0.152 | 230 | 50 | 129.2 | 2 | PASS | 230Vac-50Hz-80%
696 | ******* | ******* | 113.047 | 113 | 2 | * | 0.042 | 230 | 50 | 113.05 | 1.75 | PASS | 230Vac-50Hz-70%
698 | ******* | ******* | 96.898 | 96.75 | 2 | * | 0.152 | 230 | 50 | 96.9 | 1.5 | PASS | 230Vac-50Hz-60%
700 | ******* | ******* | 80.748 | 80.625 | 2 | * | 0.152 | 230 | 50 | 80.75 | 1.25 | PASS | 230Vac-50Hz-50%
702 | ******* | ******* | 64.598 | 64.625 | 2 | * | 0.042 | 230 | 50 | 64.6 | 1 | PASS | 230Vac-50Hz-40%
704 | ******* | ******* | 48.448 | 48.5 | 2 | * | 0.108 | 230 | 50 | 48.45 | 0.75 | PASS | 230Vac-50Hz-30%
706 | ******* | ******* | 32.298 | 32.375 | 2 | * | 0.239 | 230 | 50 | 32.3 | 0.5 | PASS | 230Vac-50Hz-20%
708 | ******* | ******* | 16.148 | 16.281 | 5 | * | 0.826 | 230 | 50 | 16.15 | 0.25 | PASS | 230Vac-50Hz-10%
710 | ******* | ******* | 161.497 | 161.25 | 2 | * | 0.153 | 230 | 60 | 161.5 | 2.5 | PASS | 230Vac-60Hz-100%
711 | ******* | ******* | 145.347 | 145.25 | 2 | * | 0.067 | 230 | 60 | 145.35 | 2.25 | PASS | 230Vac-60Hz-90%
712 | ******* | ******* | 129.197 | 129 | 2 | * | 0.152 | 230 | 60 | 129.2 | 2 | PASS | 230Vac-60Hz-80%
713 | ******* | ******* | 113.047 | 113 | 2 | * | 0.042 | 230 | 60 | 113.05 | 1.75 | PASS | 230Vac-60Hz-70%
714 | ******* | ******* | 96.898 | 96.75 | 2 | * | 0.152 | 230 | 60 | 96.9 | 1.5 | PASS | 230Vac-60Hz-60%
715 | ******* | ******* | 80.748 | 80.625 | 2 | * | 0.152 | 230 | 60 | 80.75 | 1.25 | PASS | 230Vac-60Hz-50%
716 | ******* | ******* | 64.598 | 64.625 | 2 | * | 0.042 | 230 | 60 | 64.6 | 1 | PASS | 230Vac-60Hz-40%
717 | ******* | ******* | 48.448 | 48.5 | 2 | * | 0.108 | 230 | 60 | 48.45 | 0.75 | PASS | 230Vac-60Hz-30%
718 | ******* | ******* | 32.298 | 32.375 | 2 | * | 0.24 | 230 | 60 | 32.3 | 0.5 | PASS | 230Vac-60Hz-20%
719 | ******* | ******* | 16.148 | 16.281 | 5 | * | 0.828 | 230 | 60 | 16.15 | 0.25 | PASS | 230Vac-60Hz-10%
720 | ******* | ******* | 161.497 | 161.25 | 2 | * | 0.153 | 240 | 60 | 161.5 | 2.5 | PASS | 240Vac-60Hz-100%
721 | ******* | ******* | 145.347 | 145.25 | 2 | * | 0.067 | 240 | 60 | 145.35 | 2.25 | PASS | 240Vac-60Hz-90%
722 | ******* | ******* | 129.197 | 129 | 2 | * | 0.152 | 240 | 60 | 129.2 | 2 | PASS | 240Vac-60Hz-80%
723 | ******* | ******* | 113.047 | 113 | 2 | * | 0.042 | 240 | 60 | 113.05 | 1.75 | PASS | 240Vac-60Hz-70%
724 | ******* | ******* | 96.897 | 96.75 | 2 | * | 0.152 | 240 | 60 | 96.9 | 1.5 | PASS | 240Vac-60Hz-60%
725 | ******* | ******* | 80.748 | 80.625 | 2 | * | 0.152 | 240 | 60 | 80.75 | 1.25 | PASS | 240Vac-60Hz-50%
726 | ******* | ******* | 64.598 | 64.625 | 2 | * | 0.042 | 240 | 60 | 64.6 | 1 | PASS | 240Vac-60Hz-40%
727 | ******* | ******* | 48.448 | 48.5 | 2 | * | 0.108 | 240 | 60 | 48.45 | 0.75 | PASS | 240Vac-60Hz-30%
728 | ******* | ******* | 32.298 | 32.375 | 2 | * | 0.239 | 240 | 60 | 32.3 | 0.5 | PASS | 240Vac-60Hz-20%
729 | ******* | ******* | 16.148 | 16.281 | 5 | * | 0.828 | 240 | 60 | 16.15 | 0.25 | PASS | 240Vac-60Hz-10%
730 | ******* | ******* | 79.498 | 79.375 | 2 | * | 0.154 | 100 | 60 | 79.5 | 2.5 | PASS | 100Vac-60Hz-100%
732 | ******* | ******* | 71.548 | 71.5 | 2 | * | 0.067 | 100 | 60 | 71.55 | 2.25 | PASS | 100Vac-60Hz-90%
734 | ******* | ******* | 63.598 | 63.625 | 2 | * | 0.043 | 100 | 60 | 63.6 | 2 | PASS | 100Vac-60Hz-80%
736 | ******* | ******* | 55.648 | 55.688 | 2 | * | 0.071 | 100 | 60 | 55.65 | 1.75 | PASS | 100Vac-60Hz-70%
738 | ******* | ******* | 47.698 | 47.75 | 2 | * | 0.11 | 100 | 60 | 47.7 | 1.5 | PASS | 100Vac-60Hz-60%
740 | ******* | ******* | 39.748 | 39.812 | 2 | * | 0.163 | 100 | 60 | 39.75 | 1.25 | PASS | 100Vac-60Hz-50%
742 | ******* | ******* | 31.798 | 31.875 | 2 | * | 0.243 | 100 | 60 | 31.8 | 1 | PASS | 100Vac-60Hz-40%
744 | ******* | ******* | 23.848 | 23.969 | 2 | * | 0.508 | 100 | 60 | 23.85 | 0.75 | PASS | 100Vac-60Hz-30%
746 | ******* | ******* | 15.898 | 16.031 | 2 | * | 0.841 | 100 | 60 | 15.9 | 0.5 | PASS | 100Vac-60Hz-20%
748 | ******* | ******* | 7.948 | 8.141 | 5 | * | 2.428 | 100 | 60 | 7.95 | 0.25 | PASS | 100Vac-60Hz-10%
775 | ******* | ******* | 161.497 | 161.25 | ******* | * | 0.153 | 240 | 30 | 161.5 | 2.5 | PASS | 240Vdc-100%
776 | ******* | ******* | 80.748 | 80.625 | ******* | * | 0.152 | 240 | 30 | 80.75 | 1.25 | PASS | 240Vdc-50%
777 | ******* | ******* | 32.298 | 32.312 | ******* | * | 0.046 | 240 | 30 | 32.3 | 0.5 | FAIL | 240Vdc-20%
778 | ******* | ******* | 16.148 | 16.25 | ******* | * | 0.633 | 240 | 30 | 16.15 | 0.25 | PASS | 240Vdc-10%
---------------------------------------------
Accuracy_Pout
SEQ | Read_SPEC_Max | Read_SPEC_Min | Read_Value | MCU_Value | VS_SPEC_Max | VS_SPEC_Min | VS_MCU | Vin | Fin | Main_Load(A) | Vsb_Load(A) | Result | Ext
690 | ******** | ******** | 1994.408 | 1968 | 2 | * | 0.182 | 230 | 50 | 161.5 | 2.5 | PASS | 230Vac-50Hz-100%
692 | ******** | ******** | 1796.598 | 1772 | 2 | * | 0.136 | 230 | 50 | 145.35 | 2.25 | PASS | 230Vac-50Hz-90%
694 | ******** | ******** | 1598.23 | 1576 | 2 | * | 0.114 | 230 | 50 | 129.2 | 2 | PASS | 230Vac-50Hz-80%
696 | ******** | ******** | 1399.55 | 1380 | 2 | * | 0.108 | 230 | 50 | 113.05 | 1.75 | PASS | 230Vac-50Hz-70%
698 | ******** | ******** | 1200.562 | 1182 | 2 | * | 0.044 | 230 | 50 | 96.9 | 1.5 | PASS | 230Vac-50Hz-60%
700 | ******** | ******** | 1001.195 | 987 | 2 | * | 0.086 | 230 | 50 | 80.75 | 1.25 | PASS | 230Vac-50Hz-50%
702 | ******** | ******** | 801.632 | 791 | 2 | * | 0.18 | 230 | 50 | 64.6 | 1 | PASS | 230Vac-50Hz-40%
704 | ******** | ******** | 601.728 | 593 | 2 | * | 0.054 | 230 | 50 | 48.45 | 0.75 | PASS | 230Vac-50Hz-30%
706 | ******** | ******** | 401.464 | 396 | 2 | * | 0.146 | 230 | 50 | 32.3 | 0.5 | PASS | 230Vac-50Hz-20%
708 | ******** | ******** | 200.894 | 199.25 | 5 | * | 0.699 | 230 | 50 | 16.15 | 0.25 | PASS | 230Vac-50Hz-10%
710 | ******** | ******** | 1994.889 | 1968 | 2 | * | 0.158 | 230 | 60 | 161.5 | 2.5 | PASS | 230Vac-60Hz-100%
711 | ******** | ******** | 1796.813 | 1772 | 2 | * | 0.124 | 230 | 60 | 145.35 | 2.25 | PASS | 230Vac-60Hz-90%
712 | ******** | ******** | 1598.228 | 1576 | 2 | * | 0.114 | 230 | 60 | 129.2 | 2 | PASS | 230Vac-60Hz-80%
713 | ******** | ******** | 1399.634 | 1380 | 2 | * | 0.102 | 230 | 60 | 113.05 | 1.75 | PASS | 230Vac-60Hz-70%
714 | ******** | ******** | 1200.781 | 1182 | 2 | * | 0.062 | 230 | 60 | 96.9 | 1.5 | PASS | 230Vac-60Hz-60%
715 | ******** | ******** | 1001.254 | 987 | 2 | * | 0.081 | 230 | 60 | 80.75 | 1.25 | PASS | 230Vac-60Hz-50%
716 | ******** | ******** | 801.728 | 791 | 2 | * | 0.168 | 230 | 60 | 64.6 | 1 | PASS | 230Vac-60Hz-40%
717 | ******** | ******** | 601.692 | 593 | 2 | * | 0.06 | 230 | 60 | 48.45 | 0.75 | PASS | 230Vac-60Hz-30%
718 | ******** | ******** | 401.437 | 396 | 2 | * | 0.153 | 230 | 60 | 32.3 | 0.5 | PASS | 230Vac-60Hz-20%
719 | ******** | ******** | 200.866 | 199.25 | 5 | * | 0.713 | 230 | 60 | 16.15 | 0.25 | PASS | 230Vac-60Hz-10%
720 | ******** | ******** | 1994.766 | 1968 | 2 | * | 0.164 | 240 | 60 | 161.5 | 2.5 | PASS | 240Vac-60Hz-100%
721 | ******** | ******** | 1796.593 | 1772 | 2 | * | 0.136 | 240 | 60 | 145.35 | 2.25 | PASS | 240Vac-60Hz-90%
722 | ******** | ******** | 1598.227 | 1576 | 2 | * | 0.114 | 240 | 60 | 129.2 | 2 | PASS | 240Vac-60Hz-80%
723 | ******** | ******** | 1399.549 | 1380 | 2 | * | 0.108 | 240 | 60 | 113.05 | 1.75 | PASS | 240Vac-60Hz-70%
724 | ******** | ******** | 1200.704 | 1182 | 2 | * | 0.056 | 240 | 60 | 96.9 | 1.5 | PASS | 240Vac-60Hz-60%
725 | ******** | ******** | 1001.315 | 987 | 2 | * | 0.074 | 240 | 60 | 80.75 | 1.25 | PASS | 240Vac-60Hz-50%
726 | ******** | ******** | 801.679 | 791 | 2 | * | 0.174 | 240 | 60 | 64.6 | 1 | PASS | 240Vac-60Hz-40%
727 | ******** | ******** | 601.728 | 593 | 2 | * | 0.054 | 240 | 60 | 48.45 | 0.75 | PASS | 240Vac-60Hz-30%
728 | ******** | ******** | 401.463 | 396 | 2 | * | 0.146 | 240 | 60 | 32.3 | 0.5 | PASS | 240Vac-60Hz-20%
729 | ******** | ******** | 200.867 | 199.25 | 5 | * | 0.713 | 240 | 60 | 16.15 | 0.25 | PASS | 240Vac-60Hz-10%
730 | ******** | ******** | 1001.066 | 971 | 2 | * | 0.006 | 100 | 60 | 79.5 | 2.5 | PASS | 100Vac-60Hz-100%
732 | ******** | ******** | 901.291 | 874 | 2 | * | 0.031 | 100 | 60 | 71.55 | 2.25 | PASS | 100Vac-60Hz-90%
734 | ******** | ******** | 801.438 | 778 | 2 | * | 0.077 | 100 | 60 | 63.6 | 2 | PASS | 100Vac-60Hz-80%
736 | ******** | ******** | 701.561 | 681 | 2 | * | 0.071 | 100 | 60 | 55.65 | 1.75 | PASS | 100Vac-60Hz-70%
738 | ******** | ******** | 601.627 | 584 | 2 | * | 0.073 | 100 | 60 | 47.7 | 1.5 | PASS | 100Vac-60Hz-60%
740 | ******** | ******** | 501.508 | 487 | 2 | * | 0.112 | 100 | 60 | 39.75 | 1.25 | PASS | 100Vac-60Hz-50%
742 | ******** | ******** | 401.331 | 390 | 2 | * | 0.186 | 100 | 60 | 31.8 | 1 | PASS | 100Vac-60Hz-40%
744 | ******** | ******** | 301.124 | 293.5 | 2 | * | 0.489 | 100 | 60 | 23.85 | 0.75 | PASS | 100Vac-60Hz-30%
746 | ******** | ******** | 200.794 | 196.25 | 2 | * | 0.769 | 100 | 60 | 15.9 | 0.5 | PASS | 100Vac-60Hz-20%
748 | ******** | ******** | 100.436 | 99.625 | 5 | * | 2.275 | 100 | 60 | 7.95 | 0.25 | PASS | 100Vac-60Hz-10%
775 | ******** | ******** | 1994.531 | 1968 | ******* | * | 0.176 | 240 | 30 | 161.5 | 2.5 | PASS | 240Vdc-100%
776 | ******** | ******** | 1001.253 | 987 | ******* | * | 0.081 | 240 | 30 | 80.75 | 1.25 | PASS | 240Vdc-50%
777 | ******** | ******** | 401.462 | 396 | ******* | * | 0.146 | 240 | 30 | 32.3 | 0.5 | FAIL | 240Vdc-20%
778 | ******** | ******** | 200.856 | 199.25 | ******* | * | 0.718 | 240 | 30 | 16.15 | 0.25 | PASS | 240Vdc-10%

## I2C
I2C Read Status
SEQ | Word SPEC | Word_Page_00 | Word SPEC_Page1 | Word_Page_01 | Byte SPEC | Status_Byte_P00 | Status_Byte_P01 | VOUT SPEC | Status_VOUT_P00 | Status_VOUT_P01 | Iout SPEC | Status_IOUT_P00 | Status_IOUT_P01 | Input SPEC | Status_INPUT_P00 | Status_INPUT_P01 | Temperature SPEC | Status_TEM_P00 | Status_TEM_P01 | CML SPEC | Status_CML_P00 | Status_CML_P01 | FAN SPEC | Status_FANS_P00 | Status_FANS_P01 | Result | Ext
11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 264V_63Hz_HH
148 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 90V_47Hz_LL
151 | 16392 | 16392 | 16392 | 16392 | 64 | 64 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | StandBy
162 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 90V_47Hz_No Load
176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 90V_47Hz_HH
179 | 25224 | 25224 | 25224 | 25224 | 98 | 98 | 98 | 192 | 192 | 192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 128 | 128 | 128 | 0 | 0 | 0 | PASS | 90V_47Hz_HH_I2C_OVP
195 | 20584 | 20584 | 20584 | 20584 | 80 | 80 | 80 | 0 | 0 | 0 | 163 | 163 | 163 | 7 | 7 | 7 | 0 | 0 | 0 | 128 | 128 | 128 | 0 | 0 | 0 | PASS | 90V-OCP2
199 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 90V-OCP2_Recover Check
204 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 100V_60Hz_HH
234 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 180V_47Hz_HH
264 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 200V_50Hz_HH
294 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 220V_50Hz_HH
296 | 16392 | 16392 | 16392 | 16392 | 64 | 64 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | StandBy
329 | 16392 | 16392 | 16392 | 16392 | 64 | 64 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | StandBy
352 | 25224 | 25224 | 25224 | 25224 | 98 | 98 | 98 | 192 | 192 | 192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 128 | 128 | 128 | 0 | 0 | 0 | PASS | 12V_OV
359 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 264V_63Hz_HH
361 | 16392 | 16392 | 16392 | 16392 | 64 | 64 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | StandBy
394 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 164VDC_LL
396 | 16392 | 16392 | 16392 | 16392 | 64 | 64 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | StandBy
410 | 25224 | 25224 | 25224 | 25224 | 98 | 98 | 98 | 192 | 192 | 192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 128 | 128 | 128 | 0 | 0 | 0 | PASS | 12V_OV
427 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 164VDC_HH
429 | 16392 | 16392 | 16392 | 16392 | 64 | 64 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | StandBy
448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 200Vdc_HH
467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 220VDC_HH
469 | 16392 | 16392 | 16392 | 16392 | 64 | 64 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | StandBy
487 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 300VDC_LL
489 | 16392 | 16392 | 16392 | 16392 | 64 | 64 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | StandBy
502 | 25224 | 25224 | 25224 | 25224 | 98 | 98 | 98 | 192 | 192 | 192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 128 | 128 | 128 | 0 | 0 | 0 | PASS | 12V_OV
520 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 300VDC_HH
522 | 16392 | 16392 | 16392 | 16392 | 64 | 64 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | StandBy
554 | 18472 | 18472 | 18472 | 18472 | 72 | 72 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 56 | 56 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | Vin_UV
566 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | PASS
568 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | PASS
573 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 90Vac -->0Vac - 10ms-0
575 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 90Vac -->0Vac - 10ms-45
577 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 90Vac -->0Vac - 10ms-90
579 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 90Vac -->0Vac - 10ms-135
581 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 90Vac -->0Vac - 10ms-225
583 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 90Vac -->0Vac - 10ms-270
585 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 90Vac -->0Vac - 10ms-315
590 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 100Vac -->0Vac - 10ms-0
592 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 100Vac -->0Vac - 10ms-45
594 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 100Vac -->0Vac - 10ms-90
596 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 100Vac -->0Vac - 10ms-135
598 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 100Vac -->0Vac - 10ms-225
600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 100Vac -->0Vac - 10ms-270
602 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 100Vac -->0Vac - 10ms-315
607 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 180Vac -->0Vac - 10ms-0
609 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 180Vac -->0Vac - 10ms-45
611 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 180Vac -->0Vac - 10ms-90
613 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 180Vac -->0Vac - 10ms-135
615 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 180Vac -->0Vac - 10ms-225
617 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 180Vac -->0Vac - 10ms-270
619 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 180Vac -->0Vac - 10ms-315
624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 200Vac -->0Vac - 10ms-0
626 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 200Vac -->0Vac - 10ms-45
628 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 200Vac -->0Vac - 10ms-90
630 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 200Vac -->0Vac - 10ms-135
632 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 200Vac -->0Vac - 10ms-225
634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 200Vac -->0Vac - 10ms-270
636 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 200Vac -->0Vac - 10ms-315
641 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 220Vac -->0Vac - 10ms-0
643 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 220Vac -->0Vac - 10ms-45
645 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 220Vac -->0Vac - 10ms-90
647 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 220Vac -->0Vac - 10ms-135
649 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 220Vac -->0Vac - 10ms-225
651 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 220Vac -->0Vac - 10ms-270
653 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 220Vac -->0Vac - 10ms-315
658 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 264Vac -->0Vac - 10ms-0
660 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 264Vac -->0Vac - 10ms-45
662 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 264Vac -->0Vac - 10ms-90
664 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 264Vac -->0Vac - 10ms-135
666 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 264Vac -->0Vac - 10ms-225
668 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 264Vac -->0Vac - 10ms-270
670 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 264Vac -->0Vac - 10ms-315
673 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 115Vac -->80.5Vac - 0.5 cycle
675 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 115Vac -->149.5Vac - 0.5 cycle
678 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 220Vac -->253Vac - 100ms Max
680 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 220Vac -->286Vac - 0.5 Cycle Max
682 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 220Vac -->253Vac - 100ms Min
684 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 220Vac -->286Vac - 0.5 Cycle Min
755 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | DropOut H_164Vdc - 10ms
757 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | DropOut H_164Vdc - 10ms
759 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | DropOut H_164Vdc - 10ms
761 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | DropOut H_164Vdc - 10ms
763 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | DropOut H_164Vdc - 10ms
765 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | DropOut H_164Vdc - 10ms
767 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | DropOut H_164Vdc - 10ms
769 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | DropOut H_164Vdc - 10ms
771 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | DropOut H_164Vdc - 10ms
773 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | DropOut H_164Vdc - 10ms
783 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | DropOut H_200Vdc - 10ms
785 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | DropOut H_200Vdc - 10ms
787 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | DropOut H_200Vdc - 10ms
789 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | DropOut H_200Vdc - 10ms
791 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | DropOut H_200Vdc - 10ms
793 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | DropOut H_200Vdc - 10ms
795 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | DropOut H_200Vdc - 10ms
797 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | DropOut H_200Vdc - 10ms
799 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | DropOut H_200Vdc - 10ms
801 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | DropOut H_200Vdc - 10ms
806 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | DropOut H_220Vdc - 10ms
808 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | DropOut H_220Vdc - 10ms
810 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | DropOut H_220Vdc - 10ms
812 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | DropOut H_220Vdc - 10ms
814 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | DropOut H_220Vdc - 10ms
816 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | DropOut H_220Vdc - 10ms
818 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | DropOut H_220Vdc - 10ms
820 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | DropOut H_220Vdc - 10ms
822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | DropOut H_220Vdc - 10ms
824 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | DropOut H_220Vdc - 10ms
829 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | DropOut H_300Vdc - 10ms
831 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | DropOut H_300Vdc - 10ms
833 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | DropOut H_300Vdc - 10ms
835 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | DropOut H_300Vdc - 10ms
837 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | DropOut H_300Vdc - 10ms
839 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | DropOut H_300Vdc - 10ms
841 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | DropOut H_300Vdc - 10ms
843 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | DropOut H_300Vdc - 10ms
845 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | DropOut H_300Vdc - 10ms
847 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | DropOut H_300Vdc - 10ms

## E14
Dynamic
SEQ | SPEC_Max | SPEC_Min | VpkHigh_1 | VpkLow_1 | SPEC_Max | SPEC_Min | VpkHigh_2 | VpkLow_2 | SPEC_Max | SPEC_Min | VpkHigh_3 | VpkLow_3 | SPEC_Max | SPEC_Min | VpkHigh_4 | VpkLow_4 | SPEC_Max | SPEC_Min | VpkHigh_5 | VpkLow_5 | Vin | Fin | Main_L1(A) | Main_L2(A) | Vsb_L1(A) | Vsb_L2(A) | Duration1(ms) | Duration2(ms) | Result | Ext | Ext_V | Ext_L1a | Ext_L1b | Ext_L2a | Ext_L2b | Ext_Hz | Ext_HzSum | Ext_percent
228 | 12.81 | 11.59 | 12.274 | 12.261 | 12.6 | 11.4 | 12.025 | 12.007 | [8 empty] | 3.46 | 2.5 | 3.249 | 3.253 | 110 | 60 | 1 | 1 | 2.75 | 3.65 | 100 | 50.2 | PASS | 110V-OCP_12Vsb_LH_Delay time 50ms | 註解無法分析
229 | 12.81 | 11.59 | 12.228 | 12.214 | 12.6 | 11.4 | 12.022 | 11.998 | [8 empty] | 3.46 | 2.5 | 3.253 | 3.259 | 110 | 60 | 79.5 | 79.5 | 2.75 | 3.65 | 100 | 50.2 | PASS | 110V-OCP_12Vsb_HH_Delay time 50ms | 註解無法分析
258 | 12.81 | 11.59 | 12.271 | 12.259 | 12.6 | 11.4 | 12.028 | 12.007 | [8 empty] | 3.46 | 2.5 | 3.249 | 3.255 | 180 | 47 | 1 | 1 | 2.75 | 3.65 | 100 | 50.2 | PASS | 180V-OCP_12Vsb_LH_Delay time 50ms | 註解無法分析
259 | 12.81 | 11.59 | 12.191 | 12.178 | 12.6 | 11.4 | 12.017 | 11.991 | [8 empty] | 3.46 | 2.5 | 3.259 | 3.264 | 180 | 47 | 128.7 | 128.7 | 2.75 | 3.65 | 100 | 50.2 | PASS | 180V-OCP_12Vsb_HH_Delay time 50ms | 註解無法分析
288 | 12.81 | 11.59 | 12.274 | 12.265 | 12.6 | 11.4 | 12.027 | 12.011 | [8 empty] | 3.46 | 2.5 | 3.251 | 3.256 | 200 | 50 | 1 | 1 | 2.75 | 3.65 | 100 | 50.2 | PASS | 200V-OCP_12Vsb_LH_Delay time 50ms | 註解無法分析
289 | 12.81 | 11.59 | 12.182 | 12.172 | 12.6 | 11.4 | 12.017 | 11.992 | [8 empty] | 3.46 | 2.5 | 3.257 | 3.262 | 200 | 50 | 145.1 | 145.1 | 2.75 | 3.65 | 100 | 50.2 | PASS | 200V-OCP_12Vsb_HH_Delay time 50ms | 註解無法分析
319 | 12.81 | 11.59 | 12.273 | 12.259 | 12.6 | 11.4 | 12.026 | 12.008 | [8 empty] | 3.46 | 2.5 | 3.251 | 3.256 | 220 | 50 | 1 | 1 | 2.75 | 3.65 | 100 | 50.2 | PASS | 220V-OCP_12Vsb_LH_Delay time 50ms | 註解無法分析
320 | 12.81 | 11.59 | 12.179 | 12.165 | 12.6 | 11.4 | 12.014 | 11.991 | [8 empty] | 3.46 | 2.5 | 3.259 | 3.268 | 220 | 50 | 161.5 | 161.5 | 2.75 | 3.65 | 100 | 50.2 | PASS | 220V-OCP_12Vsb_HH_Delay time 50ms | 註解無法分析
321 | ******** | ******** | 無值 | 無值 | ******** | ******** | 無值 | 無值 | [8 empty] | ******** | ******** | 無值 | 無值 | 220 | 50 | 161.5 | 209.95 | 2.5 | 2.5 | 500 | 5 | PASS | 220V-Fast OCW_SMBAlert | 註解無法分析
323 | 12.81 | 11.59 | 12.217 | 12.089 | 12.6 | 11.4 | 12.016 | 12.008 | [8 empty] | 3.46 | ******** | 3.25 | 0.086 | 220 | 50 | 161.5 | 209.95 | 2.5 | 2.5 | 200 | 30 | PASS | 220V-Fast OCW | 註解無法分析
384 | 12.81 | 11.59 | 12.274 | 12.26 | 12.6 | 11.4 | 12.027 | 12.011 | [8 empty] | 3.46 | 2.5 | 3.251 | 3.253 | 264 | 63 | 1 | 1 | 2.75 | 3.65 | 100 | 50.2 | PASS | 264V-OCP_12Vsb_LH_Delay time 50ms | 註解無法分析
385 | 12.81 | 11.59 | 12.178 | 12.169 | 12.6 | 11.4 | 12.01 | 11.985 | [8 empty] | 3.46 | 2.5 | 3.262 | 3.266 | 264 | 63 | 161.5 | 161.5 | 2.75 | 3.65 | 100 | 50.2 | PASS | 264V-OCP_12Vsb_HH_Delay time 50ms | 註解無法分析
386 | ******** | ******** | 無值 | 無值 | ******** | ******** | 無值 | 無值 | [8 empty] | ******** | ******** | 無值 | 無值 | 264 | 63 | 161.5 | 209.95 | 2.5 | 2.5 | 500 | 5 | PASS | 264V-Fast OCW_SMBAlert | 註解無法分析
388 | 12.81 | 11.59 | 12.221 | 12.091 | 12.6 | 11.4 | 12.014 | 12.011 | [8 empty] | 3.46 | ******** | 3.249 | 0.085 | 264 | 63 | 161.5 | 209.95 | 2.5 | 2.5 | 200 | 30 | PASS | 264V-Fast OCW | 註解無法分析